{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":62,"n_cols":8,"rows_kept":62,"merged":[[0,0,0,7],[1,0,1,7],[2,1,2,3],[3,1,3,3],[5,1,5,3],[7,1,7,3],[9,1,9,3],[11,1,11,3],[13,1,13,3],[15,1,15,3],[17,1,17,3],[19,1,19,3],[21,1,21,3],[23,1,23,3],[25,1,25,3],[27,1,27,3],[29,1,29,3],[55,0,55,6],[58,0,58,6],[61,0,61,6]],"flags":["formulas_cached_only"]}
["SCHEDULE OF COST - RAISED ACCESS FLOOR - DATA CENTRE AT SENTECH’S NASREC FACILITY"]
["Having examined the Request for Quotation documentation pack for the Works required and inspected site conditions, I/we hereby submit the Schedule of Cost to construct/supply/fabricate, deliver, install and remedy any defects to the said Works"]
["ITEM","DESCRIPTION",null,null,"MEASURING UNIT","RATE","QUANTITY","PRICE"]
[1,"OVERHEADS, CONTRACTURAL REQUIREMENTS, PUBLIC LIABILITY INSURANCE, SHOP DRAWINGS, SITE ESTABLISHMENT, DIS-ESTABLISHMENT, PLANT AND EQUIPMENT, ACCOMODATION, CLEANING OF SITE ON COMPLETION, WATER, ETC",null,null,"SUM",null,1,"R"]
[]
[2,"PROVISION FOR OHS REQUIREMENTS (OHS FILE, ETC)",null,null,"SUM",null,1,"R"]
[]
[3,"SUPPLY AND INSTALLATION OF TEMPORARY FLOOR AND WALL SHEETING/PROTECTION TO THE CONSTRUCTION AREA AND ACCESS AREA AND ITS REMOVAL ON COMPLETION",null,null,"SUM",null,1,"R"]
[]
[4,"REMOVAL OF EXISTING PORCELAIN FLOOR TILES, EXCLUDING THE ENTRANCE STAIRWELL AND THE PASSAGE STAIRWELL AREAS (IF REQUIRED)",null,null,"M²",null,90,"R"]
[]
[5,"SUPPLY AND PLACE SELF LEVELLING SCREED TO FLOOR, IF REQUIRED, IN PREPARATION TO RECEIVE RAISED ACCESS FLOOR SYSTEM (ALL WORKS IN ACCORDANCE TO MANUFACTURERS DETAIL AND SPECIFICATION)",null,null,"M²",null,90,"R"]
[]
[6,"NOTES FOR THE RAISED ACCESS FLOOR AND ACCESSORIES TO BE READ IN CONJUNCTION WITH AND INCLUDED IN THE ITEMS BELOW:\n•PROPRIETARY MODULAR, STATIC DISSIPATIVE SYSTEM MANUFACTURED UNDER AN ACCREDITED ISO MANAGEMENT SYSTEM\n•600x600 MODULAR AND INTERCHANGEABLE, STRUCTURALLY RIGID (FULL HARD STEEL TOP SHEET WELDED TO DOMED STEEL BOTTOM SECTION ENCAPSULATING A LIGHTWEIGHT CEMENTITIOUS CORE), FIRE RESISTANT (60min) FLOOR PANELS WITH A \"HEAVY DUTY\" FLOOR DESIGNATION\n•ANTI-STATIC, FACTORY BONDED HIGH PRESSURE LAMINATE FINISH TO FLOOR PANELS. STOCK COLOUR                                                                                                                                                                                                •ALL CUT-OUTS IN FLOOR PANELS TO HAVE THE REQUIRED MOLDING TO MITIGATE AIR LEAKAGE   \n•CORROSION RESISTANT STEEL UNDERSTRUCTURE SYSTEM\n•PEDESTAL WITH BOLT-ON STRINGER SYSTEM WITH A \"HEAVY DUTY FLOOR\" DESIGNATION\n•FACTORY ASSEMBLED HEAD AND STEEL BASE PEDESTALS, ADJUSTABLE (+-25mm) WITH ANTI-ROTATION AND VIBRATION PROOF LOCKNUT SYSTEM                                                                                                  •PEDESTAL ANCHORING SYSTEM COMPATIBLE WITH THE ANCHORING SUBSTRATE\n•RIGID SYSTEM WITH NO LOSS OF LATERAL STABILITY OR INTEGRITY WHEN PANELS ARE REMOVED, FROM THE FULLY LOADED SYSTEM, IN ORDER TO WORK UNDER THE ACCESS FLOOR                                            •THE INSTALLATION OF THE RAISED ACCESS FLOOR SHALL BE CONDUCTED IN ACCORDANCE WITH THE MANUFACTURERS DETAIL AND SPECIFICATION                                                                                                       •THE FINISHED RAISED ACCESS FLOOR SURFACE SHALL BE FREE OF EXPOSED METAL EDGES, STURDY, RIGID AND FREE OF VIBRATION, ROCKING PANELS AND NOISE                                                                                               •PROPRIETARY SEALING TAPE OR SIMILAR TO BE UTILIZED FOR SEALING GAPS AND OPENINGS, ROOM PERIMETER, FLOOR OPENINGS, AROUND COLUMNS, AROUND CCU UNITS, FLOOR/FACIA JUNCTIONS AND WALL/FACIA JUNCTIONS (100kPa VOID PRESSURIZATION)                                                                                                                                             •STEPS TO BE CONSTRUCTED FROM THE SAME MATERIALS, STRUCTURAL STRENGTH AND CONSTRUCTION AS THE FLOOR PANELS\n•COVER OPEN JOINTS WITH FLUSH [ALUMINUM] OR [STAINLESS STEEL] COVER PLATES/TRIM\n•STEP AND STAIRWELL FACIA CONSTRUCTION AND FINISHES TO MATCH FLOOR PANELS\n•STEP AND FACIA CONSTRUCTION TO INCLUDE ALL CORNER PIECES, TRIM, STAIR NOSING, REINFORCING AND FIXING ANGLES, AS REQUIRED"]
[]
["6.1","DESIGN, SUPPLY AND INSTALLATION OF A PROPRIETARY RAISED ACCESS FLOOR TO THE DATA CENTRE",null,null,"M²",null,82,"R"]
[]
["6.2","DESIGN, SUPPLY AND INSTALL PROPRIETRY STEPS TO ENTRANCE AREA (NORTH)",null,null,"M²",null,"1.5","R"]
[]
["6.3","DESIGN, SUPPLY AND INSTALL PROPRIETARY STEPS TO PASSAGE AREA (SOUTH)",null,null,"M²",null,"1.2","R"]
[]
[7,"NOTES FOR THE STAINLESS STEEL HANDRAIL AND HORIZONTAL TUBE BALLUSTRADE SYSTEM TO BE READ IN CONJUNCTION WITH AND INCLUDED IN THE ITEMS BELOW:                                                                                                                                                         •MINIMUM Ø50mm WALL MOUNTED HANDRAIL INCLUDING ALL ENDCAPS, BRACKETS, FLANGES, PLATES AND ANCHORING MATERIAL \n•FLOOR MOUNTED BALUSTRADE - MINIMUM Ø50mm TOP RAIL, MINIMUM Ø50mm MAIN POSTS, MINIMUM Ø38mm INTERMEDIATE POSTS, MINIMUM Ø38mm INTERMEDIATE RAIL INCLUDING ALL ENDCAPS, BRACKETS, FLANGES, PLATES AND ANCHORING MATERIAL                                                                                                                                                                                                                                                                               •FLOOR MOUNTED HANDRAIL - MINIMUM Ø50mm TOP RAIL, MINIMUM Ø50mm MAIN POSTS, MINIMUM Ø38mm INTERMEDIATE POSTS, MINIMUM Ø38mm INTERMEDIATE RAIL INCLUDING ALL ENDCAPS, BRACKETS, FLANGES, PLATES AND ANCHORING MATERIAL"]
[]
["7.1","SUPPLY AND INSTALLATION OF WALL MOUNTED HANDRAIL TO PASSAGE STAIRWAY",null,null,"No",null,1,"R"]
[]
["7.2","SUPPLY AND INSTALLATION OF FLOOR MOUNTED HANDRAIL TO PASSAGE AND ENTRANCE STAIRWAY",null,null,"No",null,3,"R"]
[]
["7.3","SUPPLY AND INSTALLATION OF FLOOR MOUNTED BALUSTRADE TO PASSAGE AND ENTRANCE STAIRWAY",null,null,"No",null,3,"R"]
[]
[8,"SUPPLY AND INSTALL DOUBLE SUCTION CUP LIFTER WITH WALL MOUNTED PANEL LIFTING BRACKET INCLUDING ALL BRACKETS, FLANGES, PLATES AND ANCHORING MATERIAL",null,null,"No",null,2,"R"]
[]
[]
[]
[]
["SUB-TOTAL 1",{"$nulls":6},"R"]
[]
[]
[]
["10% CONTINGENCY",{"$nulls":6},"R"]
[]
[]
[]
["SUB-TOTAL 2",{"$nulls":6},"R"]
[]
[]
[]
["VAT AT 15%",{"$nulls":6},"R"]
[]
[]
[]
["TOTAL TO BE CARRIED FORWARD TO  QUOTATION DOCUMENT",{"$nulls":6},"R"]
[]
[]
[]
[]
["Signature                                          :______________________________"]
[]
[]
["Duly authorised to sign on behalf of :______________________________"]
[]
[]
["Date                                                  :______________________________"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}