SCHEDULE A:

| Item No | Description | Eskom’s minimum requirements | Equipment guarantees and particular |
| --- | --- | --- | --- |
| 2.0 | Manufacturer/ Supplier | Specify |  |
| 2.1 | Drawing No. | Specify |  |
| 2.2 | Maximum System Voltage (Um) | 145 kV |  |
| 2.4 | Phase Conductor | N/A |  |
| 2.6 | Span Length: Wind Weight | N/A m N/A m |  |
| 2.7 | Altitude | 1800m |  |
| 2.8 | Required Life Expectancy | ≥ 30 years |  |
| 3.0 | Technical Details |  |  |
| 3.2 | Core material Cover Thickness | ≥3mm |  |
| 3.3 | Shed material | Silicone based |  |
| 3.4 | Shed profile | Flat, No Under-ribs |  |
| 3.6 | Operating Temperature |  |  |
| (a) | - Minimum | -5ºC |  |
| (b) | - Maximum | 50ºC |  |
| (c) | - Maximum Diurnal Variation | 30ºC |  |
| 3.10 | Combined Load Curves offered, showing Horizontal, Vertical and Longitudinal combined loadability | Y/N |  |
| 3.11 | Strength Requirements |  |  |
|  | - CBL | kN |  |
|  | - SCL | kN |  |
|  | - MDCL | 5.3 kN |  |
| 3.12 | Minimum horizontal distance between conductor and pole, mm | 1300 mm |  |
|  | Horizontal Inclination for Installation | 12 - 15 Deg. |  |
| 3.13 | Live End Fitting | Drop Eye |  |
|  | Dead End Fitting | Gain base PCD to be confirmed |  |
| 3.15 | Minimum Specific Creepage Distance | 20 mm/kV |  |
| 3.16 | Shed Spacing to Projection Ratio | ≥ 1 |  |
| 3.17 | LIWV (at specified altitude) | 650 kV |  |
| 3.19 | 60 sec Power Frequency Withstand (at specified altitude) | 275 kV |  |
| 3.18 | Corona Rings |  |  |
| (a) | Corona ring arc rating | 50k A @ 100 ms |  |
| (b) | Live End Corona Ring Diameter | m |  |
| (c) | Dead End Corona Ring Diameter | m |  |
| 3.19 | FRP Rod Diameter | mm |  |
| 3.20 | Diameter over sheath | mm |  |
| 3.21 | Dry Arcing Distance (between rings as applicable) | mm |  |
| 3.22 | Hot dip galvanizing of ferrous fittings | Y/N |  |
| 3.23 | Live and dead end electric field limits | ≤ 0.42 kV/mm |  |
| 4.0 | Comments & Deviations |  |  |