Annexure 1: Bid Specification:

RFB 3290-2026: APPOINTMENT OF A SERVICE PROVIDER FOR THE REPLACEMENT OF THE EXISTING UNINTERRUPTABLE POWER SUPPLY (UPS) SYSTEM AT THE PIETERMARITZBURG DATA CENTRE WITH ONE (1) YEAR INSTALLATION AND THIRTY-SIX (36) MONTHS MAINTENANCE AND SERVICE PLAN.

TECHNICAL, PRICING AND PREFERENCE POINTS REQUIREMENTS

Contents

1.	Introduction	4

1.1	Purpose	4

1.2	Background	4

2.	Scope of Bid	4

2.1	Scope of Work	4

2.1.1	Supply, Installation and Commissioning of 2 UPS (280kVA -300 kVA)	4

2.1.2	Replacement of Distribution Electrical Panels for UPS Systems as per SLD annex F	5

2.1.3	Supply and installation of Battery Isolator panel Bank	6

2.1.4	UPS System Cabling	6

2.1.5	Commissioning and handover	6

2.1.6	Provision of temporary supply during installation	7

2.1.7	Maintain and service the entire UPS system for a period of 36 months	7

2.1.8	UPS batteries Maintenance	8

2.2	Delivery address	8

2.3	Customer Infrastructure and environment requirements	9

3.	Requirements	9

3.1	Product / Service / Solution Requirements	9

4.	Bid Evaluation Stages	9

4.1	Mandatory Administrative Responsiveness (Stage 1)	10

4.1.1	Attendance of briefing session	10

4.1.2	Registered Supplier	10

4.2	Technical returnable documents	10

4.2.1	Instruction and evaluation criteria	10

4.2.2	Technical mandatory requirements (Stage 2)	10

4.3	Special Conditions of Contract Verification (Stage 3)	12

4.3.1	Special Conditions of Contract	12

4.3.1.1 Contracting Conditions	12

4.3.1.2 Delivery Address	13

4.3.1.3 Certification, Expertise and Qualification	13

4.3.1.4 Regulatory, Quality and Standards	13

4.3.1.5 Security screening and security clearance requirements	13

4.3.1.6 Confidentiality and non -disclosure conditions	14

4.3.1.7 Guarantee and warranties	15

4.3.1.8 Intellectual Property Rights	16

4.3.1.9 Counter Conditions	17

4.3.1.10 Fronting	17

4.3.1.11 Business Continuity and Disaster Recovery Plans	17

4.3.1.12 Supplier Due Diligence	17

4.3.1.13 Preference Goal Requirements conditions	18

4.3.2	Declaration of compliance and acceptance SCC	18

4.4	Price and Preference Points Evaluation (Stage 4)	18

4.4.1	Costing and Preference Evaluation	18

4.4.2	Costing and Pricing Conditions	19

4.4.3	Bid Pricing Schedule	19

4.4.4	Declaration of Acceptance	19

4.5	Preference Requirements	20

Annex A: Bidder Substantiating Evidence	25

5.	Technical Mandatory Requirement Evidence	25

5.1	Bidder Certification / Affiliation Requirements	25

5.2	Bidders Experience and Capabilities	25

5.3	CIDB Registration Requirements	26

5.4	Special Condition of Contract Verification	26

Annex B: CIDB Registration Requirement	28

Annex C: Technical Specifications	29

Annex D: UPS and Battery Maintenance Requirements	31

Annex E: Contract Data (UPS)	35

Part 1: Contract Data Provided by the Employer	35

1.	General	35

2.	Time and Possession	35

3.	Contract Price and Payment	36

4.	Quality, Materials and Standards	36

Annex F: Single line diagrams (SLDS)	38

# Introduction

## Purpose

The purpose of this Request for Bid (RFB) is to invite Suppliers (hereinafter referred to as “bidders”) to submit bids for the appointment of a service provide for the replacement of the existing Uninterruptable Power Supply (UPS) system at the Pietermaritzburg Data Centre with 1 year installation and thirty-six (36) Months maintenance and service plan.

## Background

The State Information Technology Agency provides Data Centre services to all departments of the South African Government. These services include the housing of client equipment as well as the hosting of departmental unique business systems that enables key business processes and optimizes service delivery to the citizens of the country. In addition, the SITA Pietermaritzburg Oracle Cloud is housed in the Data Centre, and the Pietermaritzburg Switching Centre uses the same electrical infrastructure.

# Scope of Bid

## Scope of Work

The scope of work for the bidders is as follow:

Replacement of 2 UPS modules (Platinum Plus 280 KVA Module UPS 1 and 2, each rack with 7 x 40kVA Modules). The systems must be fully supported by a local technical team based in South Africa with available spare parts and service capabilities.

- Supply, Installation and Commissioning of 2 x UPS (280kVA -300 kVA).

- Replace the existing UPS electrical panels to support 2 x 280kVA-300kVA UPS’s.

- UPS system Cabling.

- Maintain and service the entire UPS system for a period of 36 months.

- Maintenance of the existing UPS batteries for a period of 36 months.

- Floor resurfacing and painting _Resurfacing the damaged floor after installation, restoring the floor’s surface to its original or improved condition.

### Supply, Installation and Commissioning of 2 UPS (280kVA -300 kVA)

Scope of Work for UPS Replacement entails the following activities:

- Existing System Assessment

  - Inspection: Conduct a thorough inspection of the existing UPS system to document its current state, including capacity, configuration, and any issues.

  - Load Analysis: Perform a load analysis to determine the current and future power requirements.

  - Environmental Conditions: Review the environmental conditions (temperature, humidity, airflow) to ensure they meet the new UPS requirements.

- Provision of New UPS

  - Replacement of 2 UPS modules (Platinum Plus 280 KVA Module UPS 1 and 2) with new modules – as per technical specifications in Annex C.

- Pre-Installation Activities

  - Site Preparation: Prepare the site for the installation, including any necessary electrical or structural modifications.

  - Shutdown Planning: Develop a detailed shutdown plan to minimize disruption, including backup power arrangements during the replacement process.

  - Safety Measures: Implement safety protocols to protect personnel and equipment during the installation.

- Decommissioning of Existing UPS

  - Shutdown: Safely shut down and disconnect the existing UPS system.

  - Removal: Remove the old UPS and associated equipment.

  - Safely isolate and de-energize the existing panels.

  - Disconnect and remove old distribution panels.

  - Dispose of removed equipment in accordance with environmental regulations.

- Installation of New UPS

  - Delivery and Placement: Receive the new UPS and position it in the designated area.

  - Electrical Connections: Connect the new UPS to the new electrical infrastructure Distribution board and cabling.

  - Cooling and Ventilation: Verify that cooling and ventilation systems are adequate for the new UPS.

- System Integration and Testing

  - System Configuration: Configure the new UPS system, including setting parameters, alarms, and notifications.

  - Load Testing: Perform load testing to verify that the new UPS can handle the required load and provide the necessary backup time.

  - Redundancy Check: Verify redundancy to ensure failover systems function correctly.

### Replacement of Distribution Electrical Panels for UPS Systems as per SLD Annex F

- The panel shall be suitable for integration with newly installed UPS and existing battery systems.

- These panels must comply with IEC 61439 standards

- The new UPS installation shall provide two independent power feeds (A and B) to all critical loads. Under normal operating conditions, the A and B power paths shall be electrically separated to maintain redundancy and eliminate single points of failure. A bus coupler shall be provided between the A and B distribution buses to allow emergency load transfer and operational flexibility in the event of a UPS failure, maintenance activity, or abnormal operating condition. The bus coupler shall normally remain open and shall only be closed under controlled operating conditions to maintain continuity of supply to critical loads. Appropriate interlocking and protection schemes shall be provided to prevent unsafe parallel operation and ensure system integrity.

- The existing parallel UPS configuration shall not be replicated unless specifically approved by the client.

- Panel to include space for maintenance bypass if not provided separately

- Supply and install new distribution panels compatible with 280 kVA-300kVA, UPS x 2 systems and include the following features:

  - Incoming MCCBs rated for UPS output

  - Outgoing MCCBs/MCBs for various loads

  - Surge protection devices (SPDs)

  - Proper cable termination and labelling

  - Internal schematic drawing mounted inside the door

  - Internal lighting

  - Phase indication lamps

  - Bus coupler

- Bus Coupler Requirements

  - The bus coupler should be rated for the full load capacity of the UPS distribution system.

  - The bus coupler circuit breaker shall have the same fault level rating as the associated distribution boards.

  - Mechanical and electrical interlocks shall be provided to prevent unintended parallel of independent UPS sources.

  - The bus coupler should be integrated into the monitoring system and provide open/close status indications and alarms.

  - The bus coupler arrangement shall permit maintenance on either UPS system while maintaining supply to critical loads, subject to load capacity limitations.

  - The Contractor shall demonstrate bus coupler operation during Site Acceptance Testing (SAT) and Integrated System Testing.

- Manufacturing and Supply

  - Fabricate and factory-test panels prior to delivery.

  - Submit shop drawings and GA (general arrangement) diagrams for approval before fabrication.

- Installation and Termination

  - Install new distribution panels in the existing or modified positions.

  - Connect all incoming and outgoing feeders.

  - Ensure proper earthing, bonding, and termination practices.

### Supply and installation of Battery Isolator panel Bank

  - DC Isolator Type: Load-break DC Circuit Breaker

  - Rated Voltage: Minimum 500 VDC (preferably 600 VDC)

  - Rated Current: 315 A DC minimum

  - Breaking Capacity: As per calculated DC fault level

  - Lockable OFF position

  - Auxiliary contacts for monitoring

Each battery bank shall be connected to the UPS through a dedicated load-break DC battery isolator rated for a minimum of 432 VDC and 315 A continuous current. The isolator shall be capable of safely disconnecting the battery bank under load conditions and shall be fitted with auxiliary contacts for status monitoring. Each battery bank shall be individually protected against over-discharge, with battery disconnect initiated at a minimum cell voltage of 1.65 V per cell. The battery isolation panel shall permit independent operation, isolation, and parallel operation of the battery banks as required.

### UPS System Cabling

The scope of works covers the supply, installation, testing, and commissioning of all cabling associated with the Uninterruptible Power Supply (UPS) system to ensure safe, reliable, and compliant operation. The contractor shall provide all labour, materials, tools, and equipment necessary to complete the cabling works in accordance with the project drawings, SANS standards, and the UPS manufacturer’s requirements. This includes, but is not limited to, input power cabling, output power cabling, bypass cabling, battery cabling, control and communication cabling, proper termination, earthing and bonding, cable management, and full system integration to the critical load distribution network.

### Commissioning and handover

    - Document all test results and submit commissioning report.

  - Provide as-built drawings

  - Provide panel schedule and wiring diagrams

  - Submit test certificates

    - Commissioning and Handover

  - Final Testing: Conduct a final round of testing to ensure the new UPS is fully operational and meets performance specifications.

  - Training: Provide training for on-site personnel on the operation and maintenance of the new UPS system.

  - Documentation: Deliver all relevant documentation, including user manuals, warranty information, and maintenance schedules.

  - Handover: Formally hand over the system to the Organization.

    - Post-Installation Support

  - Monitoring: Monitor the new UPS system for a specified period after installation to ensure stable operation.

  - Support: Provide post-installation support for any issues that arise during the initial operation phase.

  - Maintenance Agreement: Establish a maintenance agreement for regular inspections, battery replacements, and firmware updates.

    - Project Close-Out

  - Review: Conduct a project close-out meeting to review the installation, address any outstanding issues, and confirm project completion.

### Provision of temporary supply during installation

The UPS replacement shall be executed in a phased manner. At all times, at least one existing UPS system shall remain operational to support the critical load. The contractor shall plan and execute all changeover activities to ensure no interruption to the data centre load. Temporary supply arrangements shall only be required during controlled transfer and commissioning stages

### Maintain and service the entire UPS system for a period of 36 months

The service provider shall maintain and service the entire UPS system, including the newly installed distribution panels, for a period of 36 months from the date of commissioning. This includes:

      - Preventive Maintenance

- Conduct quarterly inspections and maintenance of:

  - UPS units (both 280 kVA systems)

  - Associated distribution panels

  - Circuit breakers, connections, and cable terminations

  - Battery banks and monitoring systems

  - Ventilation and cooling within UPS rooms

- Perform load tests as required

- Clean panels and UPS equipment internally and externally

- Tighten all terminations and check for heat-related stress

- Corrective Maintenance

- Provide 24/7 fault reporting and technical support.

- Respond to system faults within agreed SLA.

- Replace any faulty components (parts & labor inclusive or excluded based on the contract).

- Submit incident reports detailing root cause and corrective action.

- Reporting and Record Keeping

- Maintain a full maintenance logbook for each visit and service

- Submit quarterly maintenance reports including findings, actions taken, and recommendations

- Provide annual performance summaries

- Spare Parts and Consumables

- Ensure availability of critical spare parts

- Maintain an inventory list with lead times for replacement components

- Warranty Compliance

- Ensure all maintenance activities are in line with the OEM warranty conditions to avoid invalidation

- Work closely with the UPS manufacturer (if needed) during warranty claim

### UPS batteries Maintenance

- The system comprises two (2) battery banks and four (4) stands. The two (2) battery strings and interlinking busbars consist of two hundred and sixteen (216) cells of 2V each, rated at 250Ah at the one (1) hour discharge rate per battery cell.

- The interlink busbars are rated as a minimum at the battery cell’s C1 amp per hour rating.

- The battery cell type is chloride flooded lead acid batteries. The minimum discharge voltage set point is 1.65V per cell. The battery string consists of a battery bank made up of discrete, replaceable batteries. These batteries are long design life batteries, with twelve (12) year design float life at 25℃. The battery casing is flaming retardant and of the transparent type for ease of battery condition inspection and assessment during maintenance. The battery has facilities to easily insert a hydrometer for testing and determining the charge condition.

- The system has two (2) isolation panels, which comprises of load rated DC breakers for over current protection and isolating the battery strings from the UPS units for maintenance purposes. These isolation panels are capable of isolating the one (1) bank (plus a future battery bank) as well as allowing the banks to feed the UPS individually or in parallel. Each battery bank is protected however, to ensure that each of the battery banks do not fall below the allowed 1.65V per cell.

- The battery system circuit breakers are installed inside a metal clad, wall mounting and floor standing enclosure, which is electric orange in colour.  The service provider must provide evidence of the service done and a report(s), which both the service provider and the designated SITA person must sign.

- A service should entail checking water levels, acid leaks and the specific gravity (SG) readings. In a flooded lead-acid battery, the (SG) reading, also known as the electrolyte density, indicates the state of charge.     Specific gravity measures the relative density of the battery's electrolyte (sulfuric acid and water mixture) compared to water. A fully charged battery will typically have a SG reading between 1.265 and 1.280. Lower readings indicate a discharged or partially charged battery. A fully charged battery has a higher concentration of sulfuric acid, making the electrolyte denser (higher SG). As the battery discharges, the sulfuric acid is consumed, and the electrolyte becomes less dense (lower SG). A hydrometer is used to measure SG. The hydrometer should be checked for accuracy and cleanliness before use.

## Delivery address

The goods or services must be supplied or provided at the following physical address:

| No | Site Name | Physical Address |
| --- | --- | --- |
| 1 | SITA Pietermaritzburg Data Centre | Natalia Building, 333 Jabu Ndlovu Street, Pietermaritzburg. |

## Customer Infrastructure and environment requirements

The existing system

- There are two (2) UPS modules. These are ‘Platinum Plus’ 520KVA Modules (named UPS-A and UPS-B), but the actual rating is 280kVA and not 520 kVA. Each rack has seven (7) 40KVA Modules. Each UPS rack has a capacity of 280kW. The Input Voltage and Frequency characteristics is 400V ac, 3 phase, 50 Hertz and the Output Voltage and Frequency characteristics must be 400V ac, 3 phase, 50 Hertz.

- Each cabinet has six (6) active UPS modules. For now, the two (2) cabinets run in parallel and operate as one (1) system, for example if there five (5) working modules in UPS-A and four (4) in UPS-B, then there is a total of nine (9) 40kVA modules, which gives 360kVA of power. This is then fine for the load as the two (2) cabinets are in parallel so essential they operate as one (1) system. Two (2) modules are kept in the Storeroom as a backup for each rack.

- The specified temperature range is 0 to 40℃, with relative humidity of 5%-95%. The rated load capacity should be reduced by 12％ per 5℃. The maximum temperature cannot be higher than 50℃.

- The UPS equipment has a remote NetAgent facility that allows remote access to check the UPS and also send alerts when the UPS switches to battery power or if there are errors/warnings. The NetAgent facility sends daily eMails to the DC-Facilities team.

- The service provider must provide evidence of the service done and a report(s), which both the service provider and the designated SITA person must sign. This document must be saved on the SITA file server under the relevant financial year.

# Requirements

## Product / Service / Solution Requirements

The Bidder will provide these services: replacement of the existing 2 x 280kVA UPS system, testing, commissioning, and integrating the new UPS system to the electrical network.

# Bid Evaluation Stages

The bid evaluation process consists of four stages, according to the nature of the bid. A bidder must qualify for each stage to be eligible to proceed to the next stage of the evaluation. The stages are:

Table 1: Bid Evaluation Stages

| Stage | Description | Applicable for this bid YES/NO |
| --- | --- | --- |
| Stage 1 | Mandatory Administrative Responsiveness | YES |
| Stage 2 | Technical Mandatory Responsiveness | YES |
| Stage 3 | Special Conditions of Contract verification | YES |
| Stage 4 | Price and Preference Points Evaluation | YES |

## Mandatory Administrative Responsiveness (Stage 1)

### Attendance of briefing session

- A Compulsory physical briefing session will be held. The bidder must sign the briefing session attendance register using the same information (bidder company name, bidder representative person name and contact details) as submitted in the bidder’s response document. Any bidder who fails to attend the compulsory briefing session will be disqualified.

- In the case of joint ventures or consortiums the bidder must demonstrate that at least one of the parties to the bid response attended the briefing session.

### Registered Supplier

- Only responses from bidders who are registered as a Supplier on National Treasury’s Central Supplier Database (CSD) in terms of National Treasury’s Instruction Note 4A of 2016/17 will be considered for award on this RFB.

## Technical returnable documents

### Instruction and evaluation criteria

- The bidder must comply with ALL the requirements as per the Technical Mandatory Requirements below by providing substantiating evidence in the form of documentation or information, failing which it will be regarded as “NOT COMPLY”.

- The bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response.

- The bidder must comply with ALL the TECHNICAL MANDATORY REQUIREMENTS in order for the bid response to proceed to the next stage of the evaluation.

### Technical mandatory requirements (Stage 2)

Table 2: Technical Mandatory Requirements

| TECHNICAL MANDATORY REQUIREMENTS | Evidence of compliance (used to evaluate bid) | Evidence reference (to be completed by bidder) |
| --- | --- | --- |
| - Bidder Certification / Affiliation Requirements |  |  |
| - The Bidder must be registered at the Department of Labour as an Electrical contractor. | Attach to ANNEX A, a copy of a valid letter from the Department of Labour as evidence that the bidder is registered as an Electrical Contractor. The letter must clearly indicate: - The name of the registration authority (i.e. Department of Labour). - The name of the registered bidder; and - That the bidder is an Electrical contractor. - A minimum of one installation electrician (licensed with three-phase wireman) must be held by the contractor. - Letter must be in writing, dated, signed and on a letterhead of the entity that issued it. NOTE (1): SITA reserves the right to verify all information provided. | provide unique reference to locate substantiating evidence in the bid response –: see Annex A section 5.1 (a)> |
| - The bidder must be accredited with the Original Equipment Manufacturer (OEM) as a reseller to install, support and maintain the UPS system. | Attach to ANNEX A, a copy of valid documentation (letter) from OEM indicating that the bidder is an accredited reseller to install, support and maintain the UPS system. NOTE (1) The valid documentation (letter) clearly indicating the following information below: (a) The Regulator name (OEM); and (b) The Bidder’s name; and (c) The date it was issued; and (d) if applicable, the expiry date. NOTE (2): SITA reserves the right to verify information provided. | provide unique reference to locate substantiating evidence in the bid response –: see Annex A, section 5.1 (b)> |
| - Bidders Experience and Capabilities |  |  |
| The bidder must have installed, maintained and supported the UPS system to at least three (3) customers in the past ten (10) years from publication date of this bid. | Provide in ANNEX A, reference details and/or reference letters for three (3) customers to whom the UPS system was installed, maintained and supported in the past ten (10) years from publication date of this bid. NOTE (1): The Bidder must provide all of the following information when completing Table 6: - Company name; and - Contact person, telephone and/or e-mail address; and - Project scope of Work; and - Project start and End date. NOTE (2): The reference letters should be on a company letterhead and include all of the following information: - Company Name; and - Contact person, telephone and/or e-mail address; and - Project scope of Work; and - Project start and End date. NOTE (3): Failure to complete Table 6 fully and/or to submit reference letters as indicated above will result in disqualification. NOTE (4): SITA reserves the right to verify information provided. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A: section 5.2 |
| - CIDB Registration Requirements |  |  |
| The bidder must be registered with the Construction Industry Development Board (CIDB) and have a minimum rating of 5EB or higher. | The Bidder must complete and sign ANNEX B as evidence that the bidder is registered with the CIDB with a minimum rating of 5EB or higher. NOTE (1): SITA reserves the right to verify the information provided. | provide unique reference to locate substantiating evidence in the bid response – see Annex A: section 5.3 |
| - Special Conditions of Contract Verification |  |  |
| Bidder must accept ALL the Special Conditions of contract. | The Bidder must accept ALL the Special Conditions of Contract by completing and signing the declaration of Acceptance in the Declaration of Compliance and acceptance under the Special Conditions (Section 4.3.2). NOTE (1): Failure to accept ALL the Special Conditions of Contract will result in disqualification. | provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.4 |

## Special Conditions of Contract Verification (Stage 3)

- The successful supplier will be bound by Government Procurement: General Conditions of Contract (GCC) as well as this Special Conditions of Contract (SCC), which will form part of the signed contract with the successful Supplier. However, SITA reserves the right to include or waive the condition in the signed contract.

- SITA reserves the right to:

  - Negotiate the conditions; or

  - Automatically disqualify a bidder for not accepting these conditions; or

- If the bidder qualifies the proposal with own conditions and does not specifically withdraw such own conditions when called upon to do so, SITA will invoke the rights reserved in accordance with subsection 4.3. (b) above.

### Special Conditions of Contract

### 4.3.1.1 Contracting Conditions

- Formal Contract - The supplier must enter into a formal written contract (agreement) with SITA.

- Right to Audit - SITA reserves the right, before entering into a contract, to conduct or commission an external service provider to conduct a financial audit or probity to ascertain whether a qualifying bidder has the financial wherewithal or technical capability to provide the goods and services as required by this tender.

### 4.3.1.2 Delivery Address

The supplier must deliver the required products or services at as indicated in Section 2.2, Delivery Address: SITA Pietermaritzburg, Natalia Building, 333 Jabu Ndlovu Street, Pietermaritzburg.

### 4.3.1.3 Certification, Expertise and Qualification

- The Supplier represents that;

- it has the necessary expertise, skill, qualifications and ability to undertake the work required in terms of the Scope of Work or Service Definition;

- it is committed to provide the Products or Services; and

- it can perform all obligations detailed herein without any interruption to the Customer.

### 4.3.1.4 Regulatory, Quality and Standards

- Bidders must adhere to the provisions within the following minimum Standards and Acts during the full period of this contract. It is taken that the service provider is familiar and conversant with these Standards and Acts:

- Occupational Health and Safety Act, inclusive of the Regulations contained within this Act, with specific reference to the Lead Regulations, Environmental Regulations, Driven Machinery Regulations, Electrical Machinery Regulations

- IEC 61439-1: Low-voltage switchgear and control gear assemblies;

- SANS 10142-1 (South Africa): Wiring of premises – Low-voltage installations

- IEC 60364 Series: International electrical installation standard

- IEEE 446: Standby Power Systems for Industrial and Commercial Application

- SANS 10400: Application of the National Building Regulations in South Africa

- IEC 62040: Uninterruptible Power Systems (UPS) (UPS)

- IEC 61439: the compliance requirements for low-voltage electrical switchgear and control gear assemblies (Panels)

- Occupational Health and Safety Act

- Electrical Installation Regulations

- Environmental Conservation Act 1989 as amended;

- SITA’s Health and Safety Policy;

- SITA’s site access and security policy; and

- SITA’s Change Control Policy.

### 4.3.1.5 Security screening and security clearance requirements

(a)  	Company security screening: The supplier may be required to undergo a company security screening conducted by the State Security Agency (SSA). Should the SSA find the supplier not suitable after the conduct of the security screening, the business relationship will be terminated. The following documentation will be required for the company security screening process to be conducted:

(i)  	Copy of company registration documentation;

(ii)	 Copy(ies) of identity documentation of Director(s), Member(s) or Trustee(s);

(iii)	 Copy of valid tax clearance certificate.

(b)   Security suitability check for individuals: SITA may, at its own discretion and in line with its policies and procedures, require employees of the supplier to be subjected to a security suitability check before commencement of a project or delivering of a service. The security suitability check is conducted by SITA in order to ensure that individuals meet the minimum-security requirements and also to verify personal information. The supplier will be required to replace any employee(s) who is found to be not suitable after the conduct of the security screening. The following documentation will be required for the security suitability check:

(i)  Copy of identity document;

(ii) Copy(ies) of qualification(s) if SITA requires verification thereof;

(iii) Fingerprints – will be taken electronically;

(iv) Signed consent form for the conduct of background checks.

(c)  Security clearance: A security clearance, issued by either the SSA or Defence Intelligence (DI) is required if any employee of the supplier will have or may gain access to classified information throughout the duration of the project or in the process of delivering a service. The level of security clearance required – Confidential, Secret or Top Secret, will be determined at the sole discretion of SITA. The supplier will have to replace any employee who do not qualify for a security clearance or is found not suitable by the SSA or DI. The following documentation will be required for the security clearance process:

(i)  Completed Z204 or DD1057 security clearance application form;

(ii) Fingerprints;

(iii) Personal documentation of the applicant, including but not limited to, identity document, passport, marriage certificate (if applicable), divorce order (if applicable), qualifications, salary advice and bank statements.

### 4.3.1.6 Confidentiality and non -disclosure conditions

- The Supplier, including its management and staff, must before commencement of the Contract, sign a non-disclosure agreement regarding Confidential Information

- Confidential Information means any information or data, irrespective of the form or medium in which it may be stored, which is not in the public domain and which becomes available or accessible to a Party as a consequence of this Contract, including information or data which is prohibited from disclosure by virtue of:

  - the Promotion of Access to Information Act, 2000 (Act no. 2 of 2000);

  - being clearly marked "Confidential" and which is provided by one Party to another Party in terms of this Contract;

  - being information or data, which one Party provides to another Party or to which a Party has access because of Services provided in terms of this Contract and in which a Party would have a reasonable expectation of confidentiality;

  - being information provided by one Party to another Party in the course of contractual or other negotiations, which could reasonably be expected to prejudice the right of the non-disclosing Party;

  - being information, the disclosure of which could reasonably be expected to endanger a life or physical security of a person;

  - being technical, scientific, commercial, financial and market-related information, know-how and trade secrets of a Party;

  - being financial, commercial, scientific or technical information, other than trade secrets, of a Party, the disclosure of which would be likely to cause harm to the commercial or financial interests of a non-disclosing Party; and

  - being information supplied by a Party in confidence, the disclosure of which could reasonably be expected either to put the Party at a disadvantage in contractual or other negotiations or to prejudice the Party in commercial competition; or

  - information the disclosure of which would be likely to prejudice or impair the safety and security of a building, structure or system, including, but not limited to, a computer or communication system; a means of transport; or any other property; or a person; methods, systems, plans or procedures for the protection of an individual in accordance with a witness protection scheme; the safety of the public or any part of the public; or the security of property; information the disclosure of which could reasonably be expected to cause prejudice to the defence of the Republic; security of the Republic; or international relations of the Republic; or plans, designs, drawings, functional and technical requirements and specifications of a Party, but must not include information which has been made automatically available, in terms of the Promotion of Access to Information Act, 2000; and information which a Party has a statutory or common law duty to disclose or in respect of which there is no reasonable expectation of privacy or confidentiality;

- Notwithstanding the provisions of this Contract, no Party is entitled to disclose Confidential Information, except where required to do so in terms of a law, without the prior written consent of any other Party having an interest in the disclosure;

- Where a Party discloses Confidential Information which materially damages or could materially damage another Party, the disclosing Party must submit all facts related to the disclosure in writing to the other Party, who must submit information related to such actual or potential material damage to be resolved as a dispute.

- Parties may not, except to the extent that a Party is legally required to make a public statement, make any public statement or issue a press release which could affect another Party, without first submitting a written copy of the proposed public statement or press release to the other Party and obtaining the other Party's prior written approval for such public statement or press release, which consent must not unreasonably be withheld.

### 4.3.1.7 Guarantee and warranties

- The supplier confirms that:

  - The warranty of goods supplied under this contract remains valid for the duration of the contract after the goods were delivered, installed and commissioned with a sign off, including the clients signature

  - as at Commencement Date, it has the rights, title and interest in and to the Product or Services to deliver such Product or Services in terms of the Contract and that such rights are free from any encumbrances whatsoever.

  - the Product is in good working order, free from Defects in material and workmanship, and substantially conforms to the Specifications, for the duration of the Warranty period.

  - during the Warranty period any defective item or part component of the Product be 	repaired or replaced within 3 (three) hours after receiving a written notice from SITA.

  - the Products is maintained during its Warranty Period at no expense to SITA.

  - the Product or solution possesses all material functions and features required for SITA’s 	Operational Requirements.

  - the Service is continued during the term of the Contract.

  - all third-party warranties that the Supplier receives in connection with the Products 	including the corresponding software and the benefits of all such warranties are ceded to SITA without reducing or limiting the Supplier’s obligations under the Contract.

  - no actions, suits, or proceedings, pending or threatened against it or any of its third-party 	suppliers or sub-contractors that have a material adverse effect on the Supplier’s ability to fulfil its obligations under the Contract exist.

  - SITA is notified immediately if it becomes aware of any action, suit, or proceeding, pending or threatened to have a material adverse effect on the Supplier’s ability to fulfil the obligations under the Contract.

  - any Product sold to SITA after the Commencement Date of the Contract remains free from any lien, pledge, encumbrance or security interest.

  - SITA’s use of the Product and Manuals supplied in connection with the Contract does not infringe any Intellectual Property Rights of any third party.

  - the information disclosed to SITA does not contain any trade secrets of any third party, unless disclosure is permitted by such third party.

  - it is financially capable of fulfilling all requirements of the Contract and that the Supplier is a validly organized entity that has the authority to enter the Contract.

  - it is not prohibited by any loan, contract, financing arrangement, trade covenant, or similar restriction from entering the Contract.

  - the prices, charges and fees to SITA as contained in the Contract are at least as favourable as those offered by the Supplier to any of its other customers that are of the same or similar standing and situation as SITA.

  - any misrepresentation by the Supplier amounts to a breach of Contract.

  - The contractor must not undertake any work inside a distribution board or any of the major electrical plant components or switch off any power on a distribution board or any of the major electrical plant components without an approved SITA change request; and

  - The dates for the Change Control requests will depend on SITA suitability. A number of factors influence the Change Control request dates and could be amongst other reasons other high impact SITA Change request work having a higher priority, SITA client approval, anticipated Grid power interruptions and freeze periods.

### 4.3.1.8 Intellectual Property Rights

- SITA retains all Intellectual Property Rights in and to SITA's Intellectual Property. As of the Effective Date, the Supplier is granted a non-exclusive license, for the continued duration of this Contract, to perform any lawful act including the right to use, copy, maintain, modify, enhance and create derivative works of SITA's Intellectual Property for the sole purpose of providing the Products or Services to SITA pursuant to this Contract; provided that the Supplier must not be permitted to use SITA's Intellectual Property for the benefit of any entities other than SITA without the written consent of SITA, which consent may be withheld in SITA's sole and absolute discretion. Except as otherwise requested or approved by SITA, which approval is in SITA's sole and absolute discretion, the Supplier must cease all use of SITA's Intellectual Property, at of the earliest of:

  - termination or expiration date of this Contract;

  - the date of completion of the Services; and

  - the date of rendering of the last of the Deliverables

- If so required by SITA, the Supplier must certify in writing to SITA that it has either returned all SITA Intellectual Property to SITA or destroyed or deleted all other SITA Intellectual Property in its possession or under its control

- SITA, at all times, owns all Intellectual Property Rights in and to all Bespoke Intellectual Property.

- Save for the license granted in terms of this Contract, the Supplier retains all Intellectual Property Rights in and to the Supplier’s pre-existing Intellectual Property that is used or supplied in connection with the Products or Services

- Provide SITA with the compliant Occupational Health and Safety File (required on site for period of installation and proof of compliance).

### 4.3.1.9 Counter Conditions

Bidders’ attention is drawn to the fact that amendments to any of the Bid Conditions or setting of counter conditions by bidders may result in the invalidation of such bids.

### 4.3.1.10 Fronting

- The SITA supports the spirit of Broad Based Black Economic Empowerment and recognizes that real empowerment can only be achieved through individuals and businesses conducting themselves in accordance with the Constitution and in an honest, fair, equitable, transparent and legally compliant manner. Against this background the SITA will not condone any form of fronting.

- The SITA, in ensuring that bidders conduct themselves in an honest manner will, as part of the bid evaluation processes, conduct or initiate the necessary enquiries/investigations to determine the accuracy of the representation made in bid documents. Should any of the fronting indicators as contained in the Guidelines on Complex Structures and Transactions and Fronting, issued by the Department of Trade and Industry, be established during such enquiry/investigation, the onus will be on the bidder / contractor to prove that fronting does not exist. Failure to do so within a period of 14 days from date of notification may invalidate the bid / contract and may also result in the restriction of the bidder/contractor to conduct business with the public sector for a period not exceeding ten (10) years, in addition to any other remedies SITA may have against the bidder/contractor concerned.

### 4.3.1.11 Business Continuity and Disaster Recovery Plans

- The bidder confirms that they have written business continuity and disaster recovery plans that define the roles, responsibilities and procedures necessary to ensure that the required services under this bid specification is in place and will be maintained continuously in the event of a disruption to the bidder’s operations, regardless of the cause of the disruption.

### 4.3.1.12 Supplier Due Diligence

- SITA reserves the right to conduct supplier due diligence prior to final award or at any time during the Contract period and this may include pre-announced / non-announced site visits. During the due diligence process the information submitted by the bidder will be verified and any misrepresentation thereof may disqualify the bid or Contract in whole or parts thereof.

### 4.3.1.13 Preference Goal Requirements conditions

- The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding, and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

- The Bidder must sustain or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

- Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report indicating progress against the Bidder’s Preferential commitments within 30 days of the yearly anniversary of the contract.

- Bidders need to keep auditable substantive records / evidence and upon request by SITA must be made available for audit and, or due diligence purposes.

- SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

- SITA reserves the right to verify information / evidence provided by the Bidder.

- SITA reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA for the prior year if the Bidder fails to comply to paragraphs (a), (b) and (c) above.

### Declaration of compliance and acceptance SCC

I (we), the bidder hereby declare that I (we) accept ALL the Special Conditions of Contract as specified in par 4.3.1 above and shall comply with all stated obligations:

Name of Bidder:_____________________________	Signature: _________________________

Date:______________

## Price and Preference Points Evaluation (Stage 4)

### Costing and Preference Evaluation

- In terms of the SITA Preferential Procurement Policy (PPP), the following preference point system is applicable to all this bid:

The 80/20 system (80 Price, 20 Specific Goals) for requirements with a Rand value of up to R50 000 000 (all applicable taxes included)

- The Applicable Preference Point system for this tender is the 80/20 preference point system.

- Points for this tender shall be awarded for:

  - Price; and

  - Preference points for specific goals.

- The maximum points for this tender will be allocated as follows, subject to par.2.

Table 3: Points allocation

| Description | Points |
| --- | --- |
| Price | 80 |
| Preference points for specific goals | 20 |
| Total points for Price and preference points for specific goals | 100 |

### Costing and Pricing Conditions

- South African Pricing - The total price must be VAT inclusive and be quoted in South African Rand (ZAR).

- Total Price

  - All quoted prices are the total price for the entire scope of required services and deliverables to be provided by the bidder.

  - All additional costs as well as cost of delivery, labour, S&T, overtime, etc. must be included in this bid.

  - All services, accessories, upgrades and options required by the solution or specified by the client must be included in the quoted price. If not included, suppliers will be required to supply these accessories at no cost to the client.

  - SITA reserves the right to negotiate pricing with the successful bidder prior to the award as well as envisaged quantities

- These conditions will form part of the Contract between SITA and the bidder. However, SITA reserves the right to include or waive the condition in the Contract.

- The bidder must complete the declaration of acceptance as per par 4.4.4 below by marking with an “X” either “ACCEPT ALL”, or “DO NOT ACCEPT ALL”, failing which the declaration will be regarded as “DO NOT ACCEPT ALL” and the bid will be disqualified.

### Bid Pricing Schedule

  - Bidders must complete the bid pricing schedule in the Excel spreadsheet format provided and upload this as part of their submission.

### Declaration of Acceptance

|  | ACCEPT ALL | DO NOT ACCEPT ALL |
| --- | --- | --- |
| - The bidder declares to ACCEPT ALL the Costing and Pricing conditions as specified in par 4.4.2 above by indicating with an “X” in the “ACCEPT ALL” column, or - The bidder declares to NOT ACCEPT ALL the Costing and Pricing Conditions as specified in par 4.4.2 above by - - Indicating with an “X” in the “DO NOT ACCEPT ALL” column, and; - Provide reason and proposal for each of the condition not accepted. |  |  |
| Comments by bidder: Provide the condition reference, the reasons for not accepting the condition. |  |  |

## Preference Requirements

- The bidder must complete in full all the PREFERENCE requirements.

- Allocation of points per requirements: The point’s allocation of bidders’ responses to the requirements will be determined by the completeness, relevance, and accuracy of substantiating evidence.

- Points will be allocated for each PREFERENCE requirement as per the criteria set in each section in the table 4 below.

- The bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response. During evaluation, SITA reserves the right to treat substantiation evidence that cannot be in the bid response, as “NOT COMPLY”. The evidence needs to be attached to ANNEX A.

- Preference Goal Requirements:

  - The applicable Preference Point system for this tender and points claimed is 80/20.

  - The specific Preferential Goal Requirements for this tender is indicated in table 4 below.

  - The Bidder must complete 80/20 preference point system and submit proof or documentation required in terms of this tender.

  - The Bidder must indicate their commitment to claim points for each of the preference points by signing at par 4.5 in the Invitation to Bid document.

  - Failure on the part of a bidder to submit proof or documentation required or to comply to paragraph (d) above in terms of this tender to claim preference points for the Preference Goal Requirements for this tender, will be interpreted to mean that preference points are not claimed.

  - The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding, and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

  - The Bidder must sustain or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

  - Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report to SITA indicating progress against the Bidder’s Preferential commitments within 30 days after each quarter from the commencement date of the contract.

  - Bidders need to keep auditable substantive records / evidence and upon request by SITA must be made available for audit and, or due diligence purposes.

  - SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

  - SITA reserves the right to verify information / evidence provided by the Bidder.

  - SITA reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA for the prior year if the Bidder fails to comply to paragraphs (f), (g) and (h) above.

Table 4: Preferential Goal Requirements 80/20 Preference Points system

| Preference Goal Requirement # | Preferential Goal Requirements | Preferential Goal Requirements |  |
| --- | --- | --- | --- |
|  | Preferential Goal Requirements allocated for this tender | Substantiating evidence and evidence reference to be completed by bidder. Evaluation per requirement: Each requirement indicated in the table below must be completed and points will be allocated based on the evidence required below | Evidence Reference |
|  | B-BBEE Requirements |  |  |
| 1) | B-BBEE Requirements Promotion of Transformational Objectives. | Evidence: The Bidder must provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for: - Columns A, B, C and D in table 5 # Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act: - B-BBEE certificate (from a SANAS Accredited Agency/ the department. # or # Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only. # and/ or - Column D in table 5 # Copy of South African Identification Document (ID); and/ or - Column E in table 5 # Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act. Note: The CIPC (Companies and Intellectual Property Commission) registration documents will also be used as evidence to confirm compliance to the Preferential procurement requirements as part of the evaluation process. Points allocation: Points will be allocated for bidders that meets the requirements as indicated in table 5. | <provide unique reference to locate the substantiating evidence in the bid response – Annex A, section 5.5> |

Table 5: B-BBEE Points as part of the Preference Goal requirements (Preferential Goal Requirements for (80/20) system)

Note: Bidder to select the section for points they wish to claim (Mark as Y=Yes) in the table below.

|  |  |  |  | Ownership |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Reference # | Contributor Level as defined in the Broad-Based Black Economic Empowerment Act | EME/QSEs | Black Owned (BO) (51% or more) | Black Woman Owned (BWO) (More than 30%) | Youth Owned | Owned by People living with disabilities | Score | Bidder to select the section for points they wish to claim (Mark as Y= Yes) |  |
|  |  |  | (A) | (B) | (C) | (D) | (E) | (F) |  |  |
|  | 1 | Level 1 | 6 | 4 | 4 | 4 | 2 | 20 |  |  |
|  | 2 | Level 1 | 6 | 4 | 2 | 2 | 0 | 14 |  |  |
|  | 3 | Level 1 | 6 | 4 | 2 | 0 | 0 | 12 |  |  |
|  | 4 | Level 1 | 6 | 4 | 0 | 0 | 0 | 10 |  |  |
|  | 5 | Level 2 and 3 | 4 | 2 | 1 | 1 | 1 | 9 |  |  |
|  | 6 | Level 2 and 3 | 4 | 2 | 1 | 1 | 0 | 8 |  |  |
|  | 7 | Level 2 and 3 | 4 | 2 | 1 | 0 | 0 | 7 |  |  |
|  | 8 | Level 2 and 3 | 4 | 2 | 0 | 0 | 0 | 6 |  |  |
|  | 9 | Level 4 and 5 | 2 | 1 | 0,5 | 0,5 | 0,5 | 4,5 |  |  |
|  | 10 | Level 4 and 5 | 2 | 0,5 | 0,5 | 0,5 | 0 | 3,5 |  |  |
|  | 11 | Level 4 and 5 | 2 | 0,5 | 0,5 | 0 | 0 | 3 |  |  |
|  | 12 | Level 4 and 5 | 2 | 0,5 | 0 | 0 | 0 | 2,5 |  |  |
|  | 13 | Level 6 | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | 14 | Level 7 | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | 15 | Level 8 | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | 16 | Non-Contributor | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | Total Maximum Score Allocation: |  | 20 |  |  |  |  |  |  |  |

# Bidder Substantiating Evidence

# Technical Mandatory Requirement Evidence

## Bidder Certification / Affiliation Requirements

  - Electrical Contractor

Attach a copy of a valid letter from the Department of Labour as evidence that the bidder is registered as an Electrical Contractor here:

The letter must clearly indicate:

  - The name of the registration authority (i.e. Department of Labour).

  - The name of the registered bidder; and

  - That the bidder is an Electrical contractor.

  - A minimum of one installation electrician (licensed with three-phase wireman) must be held by the contractor.

  - Letter must be in writing, dated, signed and on a letterhead of the entity that issued it.

NOTE (1):

SITA reserves the right to verify all information provided.

  - OEM Accreditation

Attach a copy of valid documentation (letter) from OEM indicating the bidder is an accredited reseller to   install, support and maintain the UPS system here.

NOTE (1):

The valid documentation (letter) clearly indicating the following information below:

(a) The Regulator name (OEM); and

(b) The Bidder’s name; and

(c) The date it was issued; and

(d) if applicable, the expiry date.

NOTE (2):

SITA reserves the right to verify information provided.

## Bidders Experience and Capabilities

Provide reference details and/or reference letters for three (3) customers to whom the UPS system was installed, maintained and supported in the past five (5) years from publication date of this bid.

NOTE (1):

The Bidder must provide all of the following information when completing Table 6:

1.	Company name; and

2.	Contact person, telephone and/or e-mail address; and

3.	Project scope of Work; and

4.	Project start and End date.

NOTE (2):

The reference letter/s should be on a company letterhead and include all of the following information:

1.	Company Name; and

2.	Contact person, telephone and/or e-mail address; and

3.	Project scope of Work; and

4.	Project start and End date.

NOTE (3):

Failure to complete Table 6 fully and to submit reference letters as indicated above will result in disqualification.

NOTE (4):

SITA reserves the right to verify information provided.

Table 6: References

| No | Company name | Reference Person Name, Tel and/or email | Project Scope of work | Project Start and End-date |
| --- | --- | --- | --- | --- |
| 1. | <Company name> | <Person Name> <Tel> <email> | < Provide the details of the scope for customers to whom the UPS system was installed, maintained and supported in the past five (5) years from publication date of this bid>. | Start Date: End Date: |

## CIDB Registration Requirements

The Bidder must complete and sign ANNEX B as evidence that the bidder is registered with the CIDB with a minimum rating of 5EB or higher.

NOTE (1):

SITA reserves the right to verify the information provided.

## Special Condition of Contract Verification

The Bidder must accept ALL the Special Conditions of Contract by completing and signing the declaration of Acceptance in the Declaration of Compliance and acceptance under the Special Conditions (Section 4.3.2).

NOTE (1):

Failure to accept ALL the Special Conditions of Contract will result in disqualification.

  - Preference Points Preferential Goals Evidence

The Bidder must provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for:

- Columns A, B, C and D in table 5

# Copy of relevant proof (B-BBEE certificate or sworn affidavit) of B-BBEE status level of contributor as defined in the Broad-Based Black Economic Empowerment Act:

        - B-BBEE certificate (from a SANAS Accredited Agency);

# or

  - Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only;

# and/ or

- Column D in tables 5

# Copy of South African Identification Document (ID);

# and/ or

- Column E in tables 5

# Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act.

Note:

The CIPC (Companies and Intellectual Property Commission) registration documents will also be used as evidence to confirm compliance to the Preferential procurement requirements as part of the evaluation process.

Points allocation: Points will be allocated for bidders that meets the requirements as indicated in table 5.

# CIDB Registration Requirement

The Bidder needs to complete and sign ANNEX B as evidence that the bidder is registered with the CIDB with a minimum rating, or higher of 5 EB or Higher

      - The Bidder needs to indicate their CIDB rating by ticking next to the relevant CIDB rating in the table below:

| Service and Support (Milestones) | CIDB Rating | Indicate the CIDB rating here by ticking next to the appropriate rating |
| --- | --- | --- |
| CIDB Rating | 5EB |  |
|  | Higher |  |

      - The Bidder needs to provide their CRS number and Expiry date in the space in the table below:

| Requirement | Bidder CRS Number |
| --- | --- |
| Bidder to provide their CRS number: |  |

| Requirement | CIDB Expiry Date |
| --- | --- |
| Bidder to provide CIDB Expiry Date |  |

NOTE (1):

SITA reserves the right to verify the information.

      - The Bidder confirms and will ensure compliance to the General Conditions of Contract for Construction Works (Third Edition, 2015 (GCC 2015), as completed by the Contract Data included in Annex E for the Bid Specification Scope of work for the duration of the contract.

I, the Supplier (Full names) …………………………………………………. representing (company name) …………………………………………………………… hereby confirm that the Bidder is registered with Construction Industry Development Board (CIDB) and understand that it will form part of the contract and is legally binding.

Thus, done and signed at ……………………………………. On this………day of……………….20….

__________________

Signature

Designation:

# Technical Specifications

Specification Data Sheet – UPS (280kvA-300 kVA)

| Technical Requirements | Parameter | Specification |
| --- | --- | --- |
|  | UPS Type | Online, double-conversion, transformer-free, modular UPS |
|  | Rated Capacity | 280kVA -300 kVA / 300 kW |
|  | Input Voltage | 400 V / 415 V, 3-phase, 4-wire + PE |
|  | Input Voltage Range | 304 – 478 V |
|  | Input Frequency | 50/60 Hz, ±5% auto-sensing |
|  | Input Power Factor | ≥ 0.99 at full load |
|  | Input THDi | < 3% at full load |
|  | Output Voltage | 400 V / 415 V, 3-phase, 4-wire + PE |
|  | Output Voltage Regulation | ±1% (static), ±5% (dynamic) |
|  | Output Frequency | 50/60 Hz ±0.1% free running |
|  | Output Power Factor | 1.0 (unity) |
|  | Efficiency | Up to 97.5% in double conversion mode |
|  | Battery Voltage | 480 VDC (nominal) |
|  | Battery Runtime | Configurable per site requirements |
|  | Parallel Capability | Up to 4 units for redundancy or capacity increase |
|  | Bypass | Automatic and manual static bypass, maintenance bypass available |
|  | Display & Controls | Color touchscreen LCD with real-time status, alarms, and event logs |
|  | Monitoring & Communication | SNMP, Modbus, BACnet, optional remote monitoring |
|  | Compliance & Standards | IEC 62040-1, IEC 62040-2, IEC 62040-3, UL 924, CE |
| Environmental Requirements | Operating Temperature | 0 °C – 40 °C |
|  | Storage Temperature | -25 °C – 70 °C |
|  | Relative Humidity | 0–95%, non-condensing |
|  | Elevation | Up to 1000 m without derating; derated at higher elevations |
|  | Acoustic Noise | < 65 dBA at 1 m distance |
| Mechanical & Installation | UPS Type | Modular, floor-standing |
|  | Dimensions (L×W×H) | As per Vertiv standard 300 kVA cabinet |
|  | Weight | As per manufacturer data (~600–700 kg depending on configuration) |
|  | Cooling | Built-in forced-air cooling |
|  | Accessibility | Front and rear service access; hot-swappable modules |

- Safety & Compliance - IEC 62040 series compliance - UL 924 Listed - CE marked - Overcurrent, overvoltage, and short-circuit protection - Emergency bypass for maintenance

- Other Features - Remote monitoring - External battery cabinets for extended runtime - Parallel system configuration for N+1 redundancy - Integration with building management system (BMS)

- Warranty & Support - Minimum 12 months warranty on UPS and modules - 24/7 technical support and service agreements - Spare parts and module availability guaranteed

# UPS and Battery Maintenance Requirements

            - Preventative Maintenance

- Preventive maintenance comprises of a program of activities, performed periodically, on site. This includes checks, searching for abnormalities, abnormality corrections, adjustments, tests, measurements, internal and external cleaning, surveys, as well as the analysis and replacement / repair of units, parts, modules, components, and spare parts to ensure optimal performance, effective performance, and performance according to the Original Equipment Manufacturer’s specifications. In terms of this maintenance contract the Maintenance Contractor will regularly and systematically inspect the systems and perform such service and maintenance

- The Maintenance Contractor shall schedule the progress of preventive maintenance and shall adhere to the minimum service timelines specified for each component. The contractor shall maintain a full maintenance schedule per site, indicating the planned Preventive maintenance date for the contract period. Preventive Maintenance shall be a standard tick sheet and job card based and be relevant to the components being serviced/maintained. Where and when requested by SITA, the contractor shall make improvements to these tick sheets to cover areas previously overlooked, lessons learned during the contractual period or from Root Cause Analysis (RCA) reports, or general improvements to the quality of the maintenance performed under this contract. The contractor shall improve his tick sheet continuously as part of his continuous improvement plan.

- Preventive Maintenance job cards shall contain details of all emergencies and corrective maintenance carried out at the site. The information captured on the previous six months’ job cards for a specific site shall be readily available to the maintenance technician. The intention of this is to alert the technician conducting the Preventive maintenance of possible issues he needs to be aware of and to seek the root cause.

- The job cards shall serve as confirmation of servicing done and shall be part of the acceptance certificate sent to the Facility Supervisor (or his representative) for Quality Assurance (QA) approval and payment.

- The acceptance certificate to be sent to the Electrical Technologist (or her representative) for approval shall contain the following minimum information per site.

Acceptance Certificate:

- Site name.

- Service period.

- Summary schedule of job cards on the applicable site.

- Summary of corrective actions on the applicable site.

- Summary of concerns for the applicable site.

- Summary of outstanding issues on the applicable site.

- All job cards, including 3rd party vendors’ job cards.

- A quotation for items that need to be attended to, that is not part of the monthly fixed cost.

- Should a site’s Preventive Maintenance not be successful, or not executed, or not approved, or not completed in full, for whatever reason, the Maintenance Contractor shall not invoice SITA for the attempted Preventive Maintenance. Where the Maintenance Contractor is of opinion that he was prevented by SITA to perform a site’s Preventive Maintenance successfully, a written notification will be made to the Facilities Manager with full details within seven calendar days of the failed/partially Preventive Maintenance for his consideration and ruling. The ruling outcome will then be either Full Payment, Partial Payment (based on cost incurred), or No Payment.

- Preventive Maintenance work at the SITA offices should be done in such a manner as not to cause any discomfort to the occupants. It is therefore required that preventive maintenance work on items that will cause major disruptions to be conducted during weekends or after hours to ensure least disruption to normal activities. Inspections may be carried out during office hours. Low Impacting services may be performed during the week.

- SITA shall conduct ad hoc onsite inspections to determine the quality of Preventive Maintenance performed on site. Where SITA management wishes to inform the maintenance contractor of a site inspection, the maintenance contractor’s Project Manager shall make himself available to join the inspection. The Contractor shall be notified at least 24 hours in advance of an impending site visit for which his attendance is required.

Table D1. Planned Maintenance (Scheduled Services)

| Minor services | Period |
| --- | --- |
| Check UPS alarms, LED indicators, or error messages. | Monthly |
| Ensure proper ventilation and no overheating. | Monthly |
| Verify input/output voltage levels (if monitored). | Monthly |
| Inspect UPS for dust buildup or loose cables. | Monthly |
| Confirm battery charge levels and status. | Monthly |
| Ensure load is within the recommended range | Monthly |
| Perform a basic battery discharge test to check performance. | Monthly |
| Inspect connections and terminal tightness | Monthly |
| Clean internal components, vents, and fans. | Monthly |
| Conduct a full-load test by running the UPS on battery mode to measure backup time | Monthly |
| Check for uneven voltage levels in battery banks (if using multiple batteries | Monthly |
| Conduct a full-load test by running the UPS on battery mode to measure backup time. | Monthly |
| Measure battery voltage levels using a multimeter—should be within manufacturer specifications. | Monthly |
| Perform a battery discharge test to check if the battery holds a charge properly. | Monthly |
| Ensure the UPS charges the battery correctly (verify charging voltage) | Monthly |
| Major service | Period |
| Inspect and replace worn-out power modules (for modular UPS systems) | Annual |
| Test and calibrate the inverter and rectifier components. | Annual |
| Replace capacitors and fans if necessary. | Annual |

            - Corrective Maintenance

- Corrective Maintenance is carried out to repair, replace, fix or adjust significant equipment and defects and failures, including the required replacement of significant units, parts, modules and components that are attributable to the Maintenance Contractor and within the scope of its responsibilities. The need for Corrective Maintenance can be identified by either the Maintenance Contractor during a site inspection or during Preventive Maintenance or identified by SITA (or one of its contractors).

- Where the Maintenance Contractor identifies the need for Corrective Maintenance that does not form part of the standard Preventive Maintenance repair requirements, the contractor shall notify the SITA Technical Manager within 6 hours in detail of such identification. SITA shall then decide on appropriate further action and indicate to the Maintenance Contractor that he may close the case, or provide SITA with a non-obligatory quotation. SITA may also obtain quotations from other service providers. SITA may then decide to proceed with the corrective repair according to the written quotation provided. The repairs will be done on an ad-hoc time and material basis. Permission for the maintenance contractor to proceed with the corrective repair will be issued in writing.  Where SITA identifies the need for Corrective Maintenance, the process shall be the same as (a) above.

- SITA may award work for corrective maintenance or new installations to a different supplier other than the Maintenance contractor. The Maintenance contractor will be required to support and fully co-operate with the other supplier/s. The Maintenance contractor will be required to quality check and pass all work done by other suppliers and provide SITA with written confirmation of completion of the corrective maintenance or new installation.

- Where purchase orders have been issued to the maintenance contractor for Corrective Maintenance, but the maintenance contractor is not performing or providing the quoted works within the agreed timeline, SITA shall have the right to cancel the purchase order, or part thereof.

            - Emergency Maintenance / Call Outs

- The activity involved with restoring, repairing or replacing on a non-scheduled maintenance basis. This maintenance activity would be a result of a service affecting or possible service affecting defect resulting in the loss of operation or potential imminent loss of operation of any part or component of any site. The nature of the defect component is such that it was not identified or known previously (for which the corrective maintenance process could have been followed).

- The contractor shall have a 24/365 call out facility. The maximum response time which the contractor must respond to a call must be as follows:

- Critical (Electrical breakdown) – Within 90 minutes from notification;

- Non-Critical (Electrical breakdown) – within four (4) hours from notification;

- If the above response times are not adhered to it may attract a penalty as set out below; and

- Spares required for ad hoc requests must be quoted for and approved by SITA KZN before the service is rendered.

- Emergency Maintenance action shall be required at any time day or night including weekends and holidays. The Maintenance Contractor shall have a sufficient number of available staff to react on a 24x7x365 basis. The Emergency maintenance response times shall meet or exceed the Service Level Agreements timelines set within this document.

- During Emergency Maintenance action the maintenance contractor’s objective shall always be to prevent a site failure or service failure by any means possible.

- The labour cost (which includes travel cost, overhead cost, etc.) for Call Outs are deemed included in the Scheduled Maintenance rate per site. The rationale is that the maintenance contractor is responsible for the site maintenance and should ensure that the site doesn’t experience any risk. Components that could lead to failure, or that could place the site under risk should thus have been identified during the scheduled maintenance work and visits.

- The component replacement cost under Emergency Maintenance shall be based on the contractual unit rates. Where no unit rates exist for that item, the contractor shall provide a cost based on the item’s cost plus the unit rate markup. Should the Maintenance Contractor have the need to subcontract the work to a third party, the subcontractor’s cost (inclusive of the subcontractor’s supporting documents) shall be presented with the Maintenance Contractor’s unit rate markup. The Maintenance Contractor shall, however, procure expensive components directly from the subcontractor’s supplier, to prevent multiple layer markup cost to SITA. The sub-contractor is not allowed to subcontract any portion of his work assignment to another party. Where the Maintenance Contractor receives trade discounts, these discounts shall be made visible to SITA and be passed on to SITA.

Call out costs for labour that is not directly related to preventive maintenance, such as power tests over and above the specified monthly tests (or the like) shall be based on the contractual unit rates.

Table D2. Corrective Maintenance (Emergency Repairs)

| Activity | Time |
| --- | --- |
| Battery failure – Replace faulty batteries | When needed |
| Overload warning – Reduce connected devices or increase UPS capacity | When needed |
| Overheating issues – Clean fans/vents and check for airflow blockages | When needed |
| Frequent switching to battery mode – Check input power quality or faulty wiring. | When needed |

# Contract Data (UPS)

(To be read with the General Conditions of Contract for Construction Works, 2015 – Third Edition)

## Part 1: Contract Data Provided by the Employer

### General

| Clause / Item | Data |
| --- | --- |
| Employer | SITA |
| Employer’s Address | 333 Jabu Ndlovu street Pietermaritzburg |
| Employer’s Representative | Afika Matebese |
| Project Title | REQUEST FOR BID FOR THE APPOINTMENT OF A SERVICE PROVIDER FOR THE REPLACEMENT OF THE EXISTING UNINTERRUPTABLE POWER SUPPLY (UPS) SYSTEM AT THE PIETERMARITZBURG DATA CENTRE WITH A THIRTY-SIX (36) MONTHS MAINTENANCE AND SERVICE PLAN |
| Site | SITA Office, Pietermaritzburg, KwaZulu-Natal, South Africa |
| Description of Works | Replacement of 2 UPS modules (Platinum Plus 280 KVA Module UPS 1 and 2) associated switchgear, cabling, ATS, testing, commissioning, training, and handover. |
| Law Governing Contract | Laws of South Africa |
| Language of Contract | English |
| Confidentiality | Both parties should keep project-related information confidential. |

### Time and Possession

| Clause / Item | Data |
| --- | --- |
| Commencement Date | To be notified |
| Time for Completion | Installation within 12 months from Commencement Date |
| Access to Site | Granted on Commencement Date |
| Programme Submission | Contractor to submit detailed programme within 14 days of commencement |
| Progress Meetings | To be held monthly as directed by Employer |
| Reporting Requirements | Monthly progress and commissioning reports |

### Contract Price and Payment

| Clause / Item | Data |
| --- | --- |
| Basis of Payment | Measurement Contract |
| Payment Terms | Monthly statements in accordance with GCC Clause 49 |
| Retention Money | 10% of each interim payment, limited to 5% of Contract Price |
| Performance Guarantee | 10% of Contract Price, bank guarantee within 14 days of award |
| Advance Payment | N/A |
| Bid Bond / Tender Security | N/A |
| Retention Release | 50% at Practical Completion, 50% at Final Completion |

### Quality, Materials and Standards

| Clause / Item | Data |
| --- | --- |
| Applicable Standards | SANS 10142 (Wiring Code); SANS/IEC 62040 (UPS Systems); OEM Specifications; OHSA Act No. 85 of 1993; Local Authority Regulations |
| Testing Requirements | Factory Acceptance Test (FAT) and Site Acceptance Test (SAT) for UPS system |
| UPS Redundancy Requirement | Minimum N+1 redundancy |
| Battery Bank Sizing | N/A |
| UPS Efficiency | Minimum 94% with THDi < 5% |
| Load Tests | 100% load test at commissioning |

### 5. Insurance

| Clause / Item | Data |
| --- | --- |
| Contractor’s All Risks Insurance | Covering works, plant, and materials up to Contract Price |
| Third Party Liability | Minimum cover R 4 million |
| Insurance of Equipment | UPS systems insured by Contractor until handover |

### 6. Health & Safety

| Clause / Item | Data |
| --- | --- |
| Compliance | Contractor to comply with OHSA Act No. 85 of 1993 |
| Health & Safety File | To be submitted before commencement of works |
| Working Hours | Monday–Friday 08:00–18:00, after-hours by approval |

### 7. Completion and Defects

| Clause / Item | Data |
| --- | --- |
| Defects Liability Period | 12 months after Practical Completion |
| Option to Extend DLP | Employer reserves right to extend for critical equipment |
| Final Completion | On successful resolution of all defects |

### 8. Dispute Resolution

| Clause / Item | Data |
| --- | --- |
| Adjudicator | To be appointed in terms of GCC 2015 Clause 10 |
| Arbitration | If unresolved, disputes referred to AFSA Arbitration Rules |

### 9. Documentation and Handover

| Clause / Item | Data |
| --- | --- |
| Operation & Maintenance Manuals | 2 hard copies and 1 electronic copy |
| As-Built Drawings | To be submitted within 30 days of Practical Completion |
| Training | Minimum 16 hours of training for Employer’s staff |
| Spare Parts List | List of critical spares to be supplied with system |

### 10. Maintenance & Warranty

| Clause / Item | Data |
| --- | --- |
| Warranty Period | 24 months on UPS system |
| Defects Liability Extension | Option for extended maintenance agreement post-DLP |
| Service Response Time | Critical fault: 4 hrs, non-critical: 24 hrs |
| OEM Support | Contractor to provide OEM authorization and support letter |

### 11. Site & Environmental

| Clause / Item | Data |
| --- | --- |
| Noise & Dust Control | Contractor to limit disruption during works |
| Protection of Existing Services | Contractor responsible for any damages |
| Waste Disposal | To comply with SANS 10263 and NEM:WA Act |
| Environmental Compliance | Contractor to ensure compliance with environmental legislation |

## Part 2: Data Provided by the Contractor

| Clause / Item | Data |
| --- | --- |
| Contractor’s Name & Address |  |
| Representative/Project Manager |  |
| Performance Guarantee Details |  |
| Insurance Provider & Cover Details |  |
| Proposed Subcontractors (if any) |  |
| Programme of Works | To be submitted within 14 days of award |

# Single line diagrams (SLDS)