PROPOSED TECHNICAL SPECIFICATIONS FOR THE SUPPLY, DELIVERY, INSTALLATION & COMMISSIONING OF THE 30kWp ROOFTOP PV SOLAR SYSTEM AT THE FRIEDENHEIM HATCHERY FACILITY, MBOMBELA, MPUMALANGA PROVINCE

# 1. TECHNICAL SPECIFICATIONS

| Item | Description of item | Specification compliance: Yes/No (Indicate ‘Yes’ or ‘No’; describe deviation from requested spec) | Unit Price | Total Price |
| --- | --- | --- | --- | --- |
| 1.1 | The construction must include supply, delivery, installation, certification, and commissioning |  |  |  |
|  | Installation of the 30kWp roof-top PV solar system at the Friedenheim Fish Hatchery Facility complying with the following specifications: - Solar modules 20 x 550Wp - 10 kWp 3phase PV inverter - 30 kWh battery storage - 30kVA inverter (3 x 10kVA) |  |  |  |
| 1.2 | AC Distribution - Upgrade of electrical circuits, where necessary. - Solar power to supply the main distribution board (DB) from the inverter room. |  |  |  |
| 1.3 | Any downtime when connecting new solar power to existing grid should be done after normal working hours (08:00 – 16:30), Monday to Friday) to avoid disruptions to activities on the campus. |  |  |  |

| Item | Description of item | Specification compliance: Yes/No (Indicate ‘Yes’ or ‘No’; describe deviation from requested spec) |  |  | Unit Price | Total Price |
| --- | --- | --- | --- | --- | --- | --- |
| 1.4 | Installation of PV panels to be in most cost/energy efficient location: |  |  |  |  |  |
| 1.5 | PV system type - Roof mount: Perform structural analysis on the roof to ensure the roof structure is fit for installation and to ensure the structural integrity of the building is not compromised. - Roof type – corrugated roof sheets |  |  |  |  |  |
| 1.6 | Type of solar panels - Install Mono-Crystalline PV modules, each solar module should have a maximum power output (Pmax) of 595 W. The selected Mono-Crystalline PV should be finalized in consultations with ARC-TSC personnel who supervise the construction. - Solar PV panels should be installed on the roof with PV mounting structures facing northward and not exposed to shading. - The solar panels placement must comply with building codes. |  |  |  |  |  |
| 1.7 | Battery bank - Install lithium-ion battery bank for a backup power of 2.5 hours (amount of backup 75 kWh: 2.5hrs x 30kWp = 75kWh). - 30 kWh battery storage. |  |  |  |  |  |
| 1.8 | Electrical loads - All lights and other critical loads (refrigeration, ice machines etc). Load isolation is critical. The electrical loads powered must be well balanced according to the expected solar output (30kWp). - Loads will be split into 2 i.e., essential and non-essential loads. |  |  |  |  |  |
| 1.9 | System architecture - The system should allow for seamless integration for future expansion of the PV and battery bank. |  |  |  |  |  |
| 1.10 | Standby generator & UPS - The system should allow for seamless integration with the existing standby generator and the UPS. - During power outage, the generator will automatically replace the grid supply. |  |  |  |  |  |
| 1.11 | Commissioning - The PV system to be signed off by Professional Engineer (Pr. Eng.) or Professional Technologist (Pr. Tech.) – at the commissioning stage and prior to any payments being made. - PV solar system design must be approved by Pr. Eng. Or Pr. Tech. - Designs to be furnished by the appointed supplier/contractor prior to any commencement of works and agreed to with the ARC’s representative. - Letter of installation and commissioning approval from Eskom or municipality. - Installation must have been performed under the supervision of a qualified electrician according to the approved design - Electrician has to sign a certificate of compliance (CoC) for the installation - Pr. Eng. Signs off an as-built drawing, after system works as specified - Installer or supplier provides any additional documents and reports for commissioning the PV system to client (ARC) - All compliance certificates/electrical audit/municipality registration/permission and requirements according to current government regulations at time of commissioning. |  |  |  |  |  |
| 1.12 | Miscellaneous - All preliminary work, including draft technical drawings must be discussed with ARC personnel before construction begins. |  |  |  |  |  |
| 1.13 | Interested suppliers/contractors shall attend a COMPULSORY site briefing on the date yet to be announced. Responses or quotations from suppliers/contractors who failed to attend the COMPULSORY site briefing will not be considered. |  |  |  |  |  |