{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["Template Identifier"," MV Induc. Motor Tech. Schedule"],"not_rendered":{"images":2,"external_links":2,"defined_names":15,"comments":10},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Template Identifier","index":0,"n_rows":6,"n_cols":4,"rows_kept":6,"merged":[[1,0,5,0],[1,1,5,1],[5,2,5,3]],"flags":["formulas_cached_only"]}
[]
[null," MEDIUM VOLTAGE INDUCTION MOTORS TECHNICAL SCHEDULE A&B TEMPLATE","Template Identifier","240-54783039 (Rev 2)"]
[null,null,"Document Identifier","xxx-xxx"]
[null,null,"Revision","x.x"]
[null,null,"Effective Date","2017-12-01"]
[null,null,"Group Technology"]

{"sheet":" MV Induc. Motor Tech. Schedule","index":1,"n_rows":273,"n_cols":10,"rows_kept":273,"merged":[[1,1,3,3],[1,4,1,9],[2,5,2,9],[3,5,3,9],[4,1,4,4],[4,5,4,9],[5,1,5,4],[5,5,5,9],[6,2,6,4],[6,6,6,7],[7,2,7,4],[7,6,7,7],[8,2,8,4],[8,6,8,7],[9,2,9,4],[9,6,9,7],[10,2,10,4],[10,6,10,7],[11,2,11,4],[11,6,11,7],[12,2,12,4],[12,6,12,7],[13,2,13,4],[13,6,13,7],[14,1,15,1],[14,2,15,3],[14,6,14,7],[15,6,15,7],[16,2,16,4],[16,6,16,7],[17,2,17,4],[17,6,17,7],[18,2,18,4],[18,6,18,7],[19,2,19,4],[20,2,20,4],[20,6,20,7],[21,2,21,4],[21,6,21,7],[22,2,22,4],[22,6,22,7],[23,2,23,4],[24,2,24,4],[25,2,25,4],[26,2,26,4],[27,2,27,4],[27,6,27,7],[28,2,28,4],[28,6,28,7],[29,2,29,4],[29,6,29,7],[30,2,30,3],[30,6,30,7],[31,1,32,1],[31,2,32,3],[31,6,31,7],[32,6,32,7],[33,2,33,4],[33,6,33,7],[34,2,34,4],[34,6,34,7],[35,2,35,4],[35,6,35,7],[36,2,36,4],[36,6,36,7],[37,1,37,4],[38,2,38,4],[38,6,38,7],[39,6,39,7],[40,2,40,4],[40,6,40,7],[41,2,41,4],[41,6,41,7],[43,2,43,4],[44,2,44,4],[45,2,45,4],[46,2,46,4],[47,2,47,4],[48,2,48,4],[49,2,49,4],[50,2,50,4],[51,2,51,4],[53,2,53,4],[54,2,54,4],[55,2,55,4],[56,2,56,4],[57,2,57,4],[58,2,58,4],[59,2,59,4],[60,2,60,4],[61,2,61,4],[62,2,62,4],[63,2,63,4],[64,2,64,4],[65,2,65,4],[66,2,66,4],[67,2,67,4],[68,2,68,4],[69,2,69,4],[70,2,70,4],[71,2,71,4],[72,2,72,4],[73,2,73,4],[74,2,74,4],[75,2,75,4],[77,2,77,4],[78,2,78,4],[79,2,79,4],[80,2,80,4],[81,2,81,4],[82,2,82,4],[83,2,83,4],[84,2,84,4],[85,2,85,4],[93,2,93,4],[97,2,97,4],[98,2,98,4],[99,2,99,4],[100,2,100,4],[101,2,101,4],[102,2,102,4],[103,2,103,4],[104,2,104,4],[105,2,105,4],[106,2,106,4],[107,2,107,4],[108,2,108,4],[109,2,109,4],[110,2,110,4],[111,2,111,4],[112,2,112,4],[113,2,113,4],[114,2,114,4],[115,2,115,4],[116,2,116,4],[117,2,117,4],[118,2,118,4],[119,2,119,4],[120,2,120,4],[121,2,121,4],[122,2,122,4],[123,2,123,4],[124,2,124,4],[125,2,125,4],[126,2,126,4],[127,2,127,4],[128,2,128,4],[129,2,129,4],[131,2,131,4],[133,2,133,4],[134,2,134,4],[135,2,135,4],[136,2,136,4],[138,2,138,4],[139,2,139,4],[140,2,140,4],[141,2,141,4],[142,2,142,4],[143,2,143,4],[144,2,144,4],[145,2,145,4],[146,2,146,4],[147,2,147,4],[148,2,148,4],[149,2,149,4],[150,2,150,4],[151,2,151,4],[152,2,152,4],[153,2,153,4],[155,2,155,4],[158,2,158,4],[159,2,159,4],[160,2,160,4],[161,2,161,4],[162,2,162,4],[163,2,163,4],[164,2,164,4],[165,2,165,4],[166,2,166,4],[167,2,167,4],[168,2,168,4],[169,2,169,4],[170,2,170,4],[171,2,171,4],[172,2,172,4],[173,2,173,4],[174,2,174,4],[175,2,175,4],[176,2,176,4],[177,2,177,4],[178,2,178,4],[179,2,179,4],[180,2,180,4],[181,2,181,4],[182,2,182,4],[183,2,183,4],[184,2,184,4],[185,2,185,4],[186,2,186,4],[187,2,187,4],[188,2,188,4],[189,2,189,4],[190,2,190,4],[191,2,191,4],[192,2,192,4],[193,2,193,4],[194,2,194,4],[195,2,195,4],[196,2,196,4],[197,2,197,4],[198,2,198,4],[199,2,199,4],[200,2,200,4],[201,2,201,4],[202,2,202,4],[203,2,203,4],[204,2,204,4],[205,2,205,4],[206,2,206,4],[207,2,207,4],[208,2,208,4],[209,2,209,4],[210,2,210,4],[211,2,211,4],[212,2,212,4],[213,2,213,4],[214,2,214,4],[215,2,215,4],[216,2,216,4],[217,2,217,4],[218,2,218,4],[219,2,219,4],[221,2,221,4],[222,2,222,4],[223,2,223,4],[224,2,224,4],[225,2,225,4],[226,2,226,4],[227,2,227,4],[228,2,228,4],[229,2,229,4],[230,2,230,4],[231,2,231,4],[232,2,232,4],[233,2,233,4],[234,2,234,4],[235,2,235,4],[236,2,236,4],[237,2,237,4],[238,2,238,4],[239,2,239,4],[240,2,240,4],[241,2,241,4],[242,2,242,4],[243,2,243,4],[245,2,245,4],[246,2,246,4],[247,2,247,4],[248,2,248,4],[249,2,249,4],[250,2,250,4],[251,2,251,4],[252,2,252,4],[253,2,253,4],[254,2,254,4],[255,2,255,4],[256,2,256,4],[259,2,259,4],[260,2,260,4],[261,2,261,4],[263,2,263,4],[264,2,264,4],[265,2,265,4],[266,2,266,4],[268,2,268,4],[269,2,269,4],[270,2,270,4],[271,2,271,4],[272,2,272,4],[273,2,273,4],[275,2,275,4],[276,2,276,4]],"flags":["formulas_cached_only"]}
[]
[{"$nulls":4}," MEDIUM VOLTAGE INDUCTION MOTORS TECHNICAL SCHEDULE A&B TEMPLATE"]
[{"$nulls":4},"Project Name:   "]
[{"$nulls":4},"Project No:"]
[null,"PLANT DESCRIPTION  (e.g. Boiler, Turbine, Coal Overland, etc.)"]
[null,"APPLICATION   (e.g. Centrifugal Fan, Screw Pump, Mill, Conveyor, etc.)"]
[null,"ITEM","DESCRIPTION",null,null,"UNITS","ESKOM or SUPPLIER",null,"ESKOM Comments","SUPPLIER Comments"]
[null,{"v":1,"d":"1.0"},"Driven Load Requirements"]
[null,1.01,"Driven machine manufacturer (OEM)",null,null,"Name"]
[null,1.02,"Manufacturer reference code/serial number",null,null,"Code"]
[null,1.03,"Number of units installed or to be installed",null,null,"Number"]
[null,1.04,"Power and Torque vs Speed Characteristic",null,null,"Description"]
[null,1.05,"Power required at duty point (referred to motor shaft) ",null,null,"kW"]
[null,1.06,"Speed at duty point (referred to motor shaft) ",null,null,"RPM"]
[null,1.07,"Speed range \n(Variable Speed application)",null,"1.071)  Minimum  speed","RPM"]
[{"$nulls":4},"1.072)  Maximum speed","RPM"]
[null,1.08,"Efficiency of the driven equipment at duty point   ",null,null,"%"]
[null,1.09,"Load moment of inertia at motor shaft  ",null,null,"kg.m2"]
[null,{"v":1.1,"d":"1.10"},"Required starting torque ",null,null,"Nm"]
[null,1.11,"Rated load torque ",null,null,"Nm"]
[null,1.12,"Maximum permissible start-up time ",null,null,"s"]
[null,{"v":1.1300000000000001,"d":"1.13"},"Maximum permissible deceleration time ",null,null,"s"]
[null,{"v":1.1400000000000001,"d":"1.14"},"Maximum permissible torque margin (Peak Torque)",null,null,"Nm"]
[null,{"v":1.1500000000000001,"d":"1.15"},"Maximum axial movement of half coupling towards motor ",null,null,"mm"]
[null,{"v":1.1600000000000001,"d":"1.16"},"Maximum axial half coupling towards away from motor  ",null,null,"mm"]
[null,{"v":1.1700000000000002,"d":"1.17"},"Maximum Axial Thrust Towards Motor",null,null,"N"]
[null,{"v":1.1800000000000002,"d":"1.18"},"Maximum Axial Thrust Away From the Motor",null,null,"N"]
[null,{"v":1.1900000000000002,"d":"1.19"},"Shaft Rotation (viewed on motor drive end shaft) Clockwise or Anticlockwise",null,null,"Name"]
[null,{"v":1.2000000000000002,"d":"1.20"},"Bearing type (Antifriction or sleeve bearing)",null,null,"Ball / Roller / Sleeve"]
[null,{"v":1.2100000000000002,"d":"1.21"},"Lubrication type (Grease or oil)",null,null,"Name"]
[null,{"v":1.2200000000000002,"d":"1.22"},"Area classification",null,"(Zone 20, 21, 22)  (e.g. Zone 22 for dust - coal areas)","Zone"]
[null,{"v":1.2300000000000002,"d":"1.23"},"Application environmental conditions",null,"1.2301)  Indoor or Outdoor","Indoor / Outdoor"]
[{"$nulls":4},"1.2302)  Clean or Dusty","Clean / Dusty"]
[null,{"v":1.2400000000000002,"d":"1.24"},"Starting method  (Direct-on-line starting, Soft starting or Soft starting with speed variation)",null,null,"DOL/Softstater/VSD"]
[null,{"v":1.2500000000000002,"d":"1.25"},"Method of stopping (Coast to stop, Mechanical braking or Electrical braking)",null,null,"Name"]
[null,{"v":1.2600000000000002,"d":"1.26"},"Drive coupling method (e.g. direct, gearbox)",null,null,"Name"]
[null,{"v":1.2700000000000002,"d":"1.27"},"Coupling type (e.g. belt, chain)",null,null,"Name"]
[null,"Required Drawings & Curves"]
[null,{"v":1.2800000000000002,"d":"1.28"}," Load Torque-Speed curve(s) reference number",null,null,"Number"]
[null,{"v":1.2900000000000003,"d":"1.29"}," Load performance curve reference number",null,null,"Number"]
[null,{"v":1.3000000000000003,"d":"1.30"}," Coupling drawing reference number",null,null,"Number"]
[null,{"v":1.3100000000000003,"d":"1.31"}," Motor and Load Layout drawing reference number",null,null,"Number"]
[]
[null,{"v":2,"d":"2.0"},"Power Supply ",null,null,"UNITS","ESKOM","SUPPLIER","ESKOM Comments","SUPPLIER Comments"]
[null,2.1,"Normal Supply",{"$nulls":3},"Schedule A ","Schedule B ","Eskom Spec - 240-57617975"]
[null,2.101,"Supply Voltage, 3-phase,  ± 5%     (e.g. 3.3kV, 6.6kV, 11kV and 15kV)",null,null,"kV","?? ± 5%"]
[null,2.102,"Supply frequency, 50Hz ± 2%",null,null,"Hz ","50 ± 2%"]
[null,2.1029999999999998,"Voltage unbalance: Negative sequence voltage up to 2 % of positive sequence voltage (Vp).",null,null,"%",{"v":0.02,"d":"2%"}]
[null,2.1039999999999996,"Voltage harmonic distortion ",null,null,"%","<= 5%."]
[null,2.2,"Abnormal power supply (prevailing simultaneously for up to 6 hours)"]
[null,2.201,"Supply Voltage, 3-phase, ± 10% (e.g. 3.3kV, 6.6kV, 11kV and 15kV)",null,null,"V","??   ± 10% "]
[null,2.202,"Supply frequency, 50 Hz ± 2% for 80 minutes",null,null,"Hz ","50 ± 2%"]
[null,2.203,"Voltage unbalance: Negative sequence voltage up to 3 % of nominal positive sequence voltage.",null,null,"%",{"v":0.03,"d":"3%"}]
[null,2.2039999999999997,"V/F ratio < 1.1pu",null,null,"pu"," <= 1.1"]
[null,2.3000000000000003,"Transient - voltage within 10% of nominal within 3 seconds after the transient:"]
[null,2.301,"Complete loss of supply for 0.2 seconds",null,null,"s",0.2]
[null,2.302,"Voltage depression up to 85% of nominal for up to 60 second",null,null,"%","85% for 1 minute"]
[null,2.303,"Voltage depression up to 75% of nominal for up to 1 second",null,null,"%","75% , 1 second"]
[]
[null,{"v":3,"d":"3.0"},"Operating Conditions",null,null,"UNITS","ESKOM","SUPPLIER","ESKOM Comments","SUPPLIER Comments"]
[null,3.01,"Altitude above see level   (e.g. 1000, 1600)",null,null,"m"]
[null,3.0199999999999996,"Normal daily maximum temperature",null,null,"ºC"]
[null,3.0299999999999994,"Normal daily minimum temperature",null,null,"ºC"]
[null,3.039999999999999,"Extreme maximum temperature",null,null,"ºC"]
[null,3.049999999999999,"Extreme minimum temperature",null,null,"ºC"]
[null,3.0599999999999987,"Ambient Air Quality ",null,null,"Describe"]
[null,3.0699999999999985,"Average humidity",null,null,"%"]
[null,3.0799999999999983,"Extent of Base Vibrations ",null,null,"Low / Med / High"]
[null,{"v":4,"d":"4.0"},"Motor General Information"]
[null,4.01,"Applicable SANS standard",null,null,"Code","SANS 60034"]
[null,4.02,"Applicable Eskom Standard",null,null,"Number","240-50237155"]
[null,4.029999999999999,"Motor manufacturer (of existing motor where applicable - not the requirement)",null,null,"Name"]
[null,4.039999999999999,"Motor manufacturer reference code/serial number (of existing motor where applicable)",null,null,"Code"]
[null,4.049999999999999,"Fabrication factory",null,null,"Name"]
[null,4.059999999999999,"Motor life expectancy",null,null,"Yrs",">20"]
[null,{"v":5,"d":"5.0"},"Motor Electrical Details  "]
[null,{"v":5.1,"d":"5.10"},"Motor Rating"]
[null,5.101,"Rated output power",null,null,"kW"]
[null,5.102,"Supply voltage  (e.g. 3.3kV, 6.6kV, 11kV and 15kV)",null,null,"V"]
[null,5.103000000000001,"Frequency (e.g. 50 or 60)",null,null,"Hz"]
[null,5.104000000000001,"Full load current ",null,null,"A"]
[null,5.105000000000001,"Rated Speed  ",null,null,"RPM"]
[null,5.106000000000002,"Winding connection",null,null,"Star / Delta"]
[null,5.107000000000002,"Duty-class as per IEC 60034-1 (e.g. S1, S2, S3, etc.)",null,null,"Code"]
[null,5.108000000000002,"Utilization factor (Load power at duty point/motor rated power), >=75%,=<90%",null,null,"%"]
[null,5.109000000000003,"Ex rating (required for Zone 20-22 Classification)  (e.g. Zone 22 for dust - coal areas)",null,null,"Yes / No"]
[null,5.110000000000003,"Ex Code (e.g. Ex td)",null,null,"Code"]
[null,{"v":5.2,"d":"5.20"},"Motor Performance Guarantees"]
[null,{"v":5.2010000000000005,"d":"5.201"},"Full load torque ",null,null,"Nm"]
[null,{"v":5.202000000000001,"d":"5.202"},"Locked rotor torque ",null,null,"Nm"]
[null,{"v":5.203000000000001,"d":"5.203"},"Pull up torque",null,null,"Nm"]
[null,{"v":5.2040000000000015,"d":"5.204"},"Breakdown torque ",null,null,"Nm"]
[null,{"v":5.205000000000002,"d":"5.205"},"Locked rotor current ",null,null,"A"]
[null,{"v":5.206000000000002,"d":"5.206"},"Efficiency at 100% Loading",null,null,"%"]
[null,{"v":5.2070000000000025,"d":"5.207"},"Efficiency at 75% Loading",null,null,"%"]
[null,{"v":5.208000000000003,"d":"5.208"},"Efficiency at 50% Loading",null,null,"%"]
[null,{"v":5.209000000000003,"d":"5.209"},"Power factor at 100% Loading",null,null,"%"]
[null,{"v":5.2100000000000035,"d":"5.210"},"Power factor at 75% Loading",null,null,"%"]
[null,{"v":5.211000000000004,"d":"5.211"},"Power factor at  50% Loading",null,null,"%"]
[null,{"v":5.3,"d":"5.30"},"Motor parameters "]
[null,5.301,"X/R Ratio",null,null,"%"]
[null,{"v":5.3020000000000005,"d":"5.302"},"Stator Resistance @ Standstill (slip = 1)",null,null,"W"]
[null,{"v":5.303000000000001,"d":"5.303"},"Stator Reactance @ Standstill (slip = 1)",null,null,"W"]
[null,{"v":5.304000000000001,"d":"5.304"},"Rotor Resistance @ Standstill (slip = 1)",null,null,"W"]
[null,{"v":5.3050000000000015,"d":"5.305"},"Rotor Reactance @ Standstill (slip = 1)",null,null,"W"]
[null,{"v":5.306000000000002,"d":"5.306"},"Stator Resistance @ Full Load",null,null,"W"]
[null,{"v":5.307000000000002,"d":"5.307"},"Stator Reactance @ Full Load",null,null,"W"]
[null,{"v":5.3080000000000025,"d":"5.308"},"Rotor Resistance @ Full Load",null,null,"W"]
[null,{"v":5.309000000000003,"d":"5.309"},"Rotor Reactance @ Full Load",null,null,"W"]
[null,{"v":5.310000000000003,"d":"5.310"},"Full Load Slip",null,null,"%"]
[null,{"v":5.3110000000000035,"d":"5.311"},"Specified Temperature",null,null,"ºC"]
[null,{"v":5.312000000000004,"d":"5.312"},"Magnetic Reactance (Xm)",null,null,"W"]
[null,{"v":5.313000000000004,"d":"5.313"},"Magnetic Resistance (Rm)",null,null,"W"]
[null,{"v":6,"d":"6.0"},"Motor Thermal Details  "]
[null,{"v":6.1,"d":"6.10"},"Temperature rise"]
[null,6.101,"Stator winding insulation class (Minimum class F)",null,null,"Name","F or H"]
[null,6.102,"Stator winding temperature rise at 1.0 Service Factor  (Maximum class B)",null,null,"K",80]
[null,{"v":6.199999999999999,"d":"6.20"},"Performance and Thermal Capacity "]
[null,6.201,"Run-up time at 100% of rated voltage",null,null,"s"]
[null,6.202,"Run-up time at 85% of rated voltage",null,null,"s"]
[null,6.203,"Run-up time at 75% of rated voltage",null,null,"s"]
[null,{"v":6.204000000000001,"d":"6.204"},"Maximum Hot Locked Rotor Time at 100% of rated voltage",null,null,"s"]
[null,{"v":6.205000000000001,"d":"6.205"},"Maximum Hot Locked Rotor Time at 85% of rated voltage",null,null,"s"]
[null,{"v":6.206000000000001,"d":"6.206"},"Maximum Hot Locked Rotor Time at 75% of rated voltage",null,null,"s"]
[null,{"v":6.207000000000002,"d":"6.207"},"Maximum Hot Acceleration Time at 100% of rated voltage",null,null,"s"]
[null,{"v":6.208000000000002,"d":"6.208"},"Maximum Hot Acceleration Time at 85% of rated voltage",null,null,"s"]
[null,{"v":6.209000000000002,"d":"6.209"},"Maximum Hot Acceleration Time at 75% of rated voltage",null,null,"s"]
[null,{"v":6.210000000000003,"d":"6.210"},"Are safe stall and acceleration times rotor or stator limited? ",null,null,"Rotor / Stator"]
[null,{"v":6.211000000000003,"d":"6.211"},"Motor Current at Breakdown Torque",null,null,"A"]
[null,{"v":6.212000000000003,"d":"6.212"},"Maximum Overload Time at Breakdown Torque Current from FLC operation",null,null,"s"]
[null,{"v":6.213000000000004,"d":"6.213"},"Thermal time constant ",null,null,"Minutes"]
[null,{"v":6.214000000000004,"d":"6.214"},"Cooling time constant ",null,null,"Minutes"]
[null,{"v":6.215000000000004,"d":"6.215"},"Number of starts from Hot, within an hour ",null,null,"Number",2]
[null,{"v":6.216000000000005,"d":"6.216"},"Number of starts from cold, within an hour ",null,null,"Number",3]
[null,{"v":7,"d":"7.0"},"Mechanical Details  "]
[null,7.1,"Motor winding systems"]
[null,7.101,"Method of stator winding Impregnation ",null,null,"Name","VPI"]
[null,7.102,"Stator winding type (form-wound / roebel bar, etc)",null,null,"Name"]
[null,7.103000000000001,"Type of Wedges (Epoxy glass preferred) ",null,null,"Epoxy Glass / Magnetic"]
[null,7.104000000000001,"Squirrel cage rotor type (Fabricated Cu are preferred) ",null,null,"Fabricated Cu/Al or Cast Al"]
[null,7.105000000000001,"Rotor Cage Type",null,null,"Single / Double"]
[null,7.199999999999999,"Enclosure and Cooling "]
[null,7.201,"Enclosure -  Degree of protection (IP Code) ",null,null,"IP Code"]
[null,7.202,"Cooling Method (IC code) ",null,null,"IC Code"]
[null,7.203,"Primary Air Cooler (Heat Exchanger):"]
[null,7.2031,"Type",null,null,"CACA / CACW"]
[null,7.2032,"Cooler Tube Material ",null,null,"Describe"]
[null,7.2033,"CW Flow Rate",null,null,"Litres per minute"]
[null,7.203399999999999,"CW Pressure",null,null,"kPa"]
[null,7.203499999999999,"CACW Cooler Leak Detectors",null,null,"Yes / No"]
[null,7.203599999999999,"Location, if yes",null,null,"Describe"]
[null,7.203699999999999,"Type of Alarm Contact",null,null,"N/C or N/O"]
[null,7.299999999999999,"Bearings"]
[null,7.300999999999999,"Bearing type (Sleeve bearing for all motors ≥1MW and for 2-pole motors  ≥ 500kW",null,null," Ball / Roller / Sleeve"]
[null,7.302,"Bearing size",null,null,"Name"]
[null,7.303,"Lubricant Grade",null,null,"Describe"]
[null,7.304,"Lubrication interval ",null,null,"hrs",">= 4000"]
[null,7.305000000000001,"Bearing life ",null,null,"hrs"]
[null,7.306000000000001,"Bearing Maximum Operating Temperature (loaded)",null,null,"ºC"]
[null,7.307000000000001,"Bearing Oil Cooler",null,null,"Yes / No"]
[null,7.308000000000002,"Special Tube Material",null,null,"Describe"]
[null,7.309000000000002,"Cooling Water Pressure",null,null,"kPa"]
[null,7.310000000000002,"Cooling Water Flow Rate",null,null,"Litres per minute"]
[null,7.311000000000003,"Vibration Sensor",null,null,"Yes / No"]
[null,7.312000000000003,"Vibration Sensor Type",null,null,"Describe"]
[null,7.313000000000003,"Easy Access Oil Top Up Plugs",null,null,"Yes / No"]
[null,7.314000000000004,"Easy Access Oil Drain Plugs",null,null,"Yes / No"]
[null,7.315000000000004,"Grease Relief Valve / Plug",null,null,"Yes / No"]
[null,7.316000000000004,"Insulated Bearings (all motors ≥ 800kW)",null,null,"Yes / No"]
[null,7.317000000000005,"Location of Bearing Insulation",null,null,"Describe"]
[null,7.399999999999999,"Motor Size and Rotation"]
[null,7.400999999999999,"Frame size",null,null,"Code"]
[null,7.401999999999999,"Frame H(A/B/C)D/E Dimensions as per IEC 60072-2",null,null,"Number"]
[null,7.403,"Rotor Moment of inertia  ",null,null,"kgm²"]
[null,7.404,"Motor total mass ",null,null,"kg"]
[null,7.405,"Heat Exchanger Weight ",null,null,"kg"]
[null,7.406000000000001,"Unidirectional Fans Acceptable?",null,null,"Yes / No"]
[null,7.407000000000001,"Shaft Rotational Direction (DE View)",null,null,"Describe"]
[null,7.499999999999998,"Power Terminal Box/es:"]
[null,7.500999999999999,"Main TB Location (DE View)",null,null,"RHS / LHS / Top"]
[null,7.501999999999999,"Main TB Phase Segregation",null,null,"Yes / No"]
[null,7.502999999999999,"Number of Terminals",null,null,"Number"]
[null,7.504,"Duplicate Terminals for Alternate Power Supply Connection",null,null,"Yes / No"]
[null,7.505,"Parallel Terminals for Current Sharing",null,null,"Yes / No"]
[null,7.506,"Blow Out Panel/s",null,null,"Yes / No"]
[null,7.599999999999998,"Auxiliary Terminal Box/es:"]
[null,7.600999999999998,"Duplicate Auxiliary Terminal Boxes",null,null,"Yes / No"]
[null,7.6999999999999975,"Vibration and Noise"]
[null,7.700999999999998,"Bearing vibration limits ",null,null,"mm/s"]
[null,7.701999999999998,"Noise level ",null,null,"dB"]
[null,{"v":8,"d":"8.0"},"Monitoring, Protection and Accessories         "]
[null,8.1,"Temperature Measuring Devices "]
[null,8.100999999999999,"Stator Winding Embedded Temperature Detectors (ETDs)",null,null,"Yes / No","YES"]
[null,8.101999999999999,"Winding ETD Type",null,null,"Thermocouple / RTD"]
[null,8.102999999999998,"Number per Phase (minimum 2 per phase for < 800kW and minimum 3 for  ≥ 800kW",null,null,"Number"]
[null,8.103999999999997,"Primary Cooling Air Temperature Detectors ",null,null,"Yes / No"]
[null,8.104999999999997,"ETD Type",null,null,"Thermocouple / RTD"]
[null,8.105999999999996,"Number to be Installed ",null,null,"Number"]
[null,8.106999999999996,"Bearing ETDs",null,null,"Yes / No","YES"]
[null,8.107999999999995,"ETD Type",null,null,"Thermocouple / RTD"]
[null,8.108999999999995,"Number per Bearing",null,null,"Number"]
[null,8.109999999999994,"Terminal Box Air Temperature Detectors (for Critical and High duty Motors)",null,null,"Yes / No"]
[null,8.110999999999994,"ETD Type",null,null,"Thermocouple / RTD"]
[null,8.111999999999993,"Number to be Installed (1 for Main and 1 for Neutral box)   (ID, PA, FD and EFPs)",null,null,"Number"]
[null,8.112999999999992,"Dial Type Temperature Indicators",null,null,"Yes / No"]
[null,8.113999999999992,"Part/s to be Monitored",null,null,"Describe"]
[null,8.114999999999991,"Indicator Type",null,null,"Temp. Range"]
[null,8.11599999999999,"Preferred Vendor Type",null,null,"Describe"]
[null,8.2,"Differential Protection CTs:",null,null,"Yes / No"]
[null,8.200999999999999,"Motor Supplied with Neutral Side CTs Installed",null,null,"Yes / No"]
[null,8.201999999999998,"CT Ratio",null,null,"Ip/Is"]
[null,8.202999999999998,"Knee Point Voltage",null,null,"Volts"]
[null,8.203999999999997,"Max. I0 @ Vkp",null,null,"Amps"]
[null,8.204999999999997,"Class"]
[null,8.205999999999996,"Line Side CTs Already or to be Installed",null,null,"Yes / No"]
[null,8.206999999999995,"Burden",null,null,"VA"]
[null,8.207999999999995,"Maximum Secondary Resistance",null,null,"W"]
[null,8.299999999999999,"Surge suppresser "]
[null,8.300999999999998,"Surge suppresser required",null,null,"Yes / No"]
[null,8.301999999999998,"Make",null,null,"Name"]
[null,8.302999999999997,"Number to be Installed per machine",null,null,"Number"]
[null,8.303999999999997,"Technical information reference number",null,null,"Number"]
[null,8.399999999999999,"Partial Discharge Monitoring"]
[null,8.400999999999998,"Partial Discharge Capacitors with  Termination Box (required for Motor Power ≥ 1MW, ≥  6.6kV Critical and High duty)",null,null,"Yes / No"]
[null,8.401999999999997,"Partial Discharge Capacitors Specification, (80pf)",null,null,"Number"]
[null,8.402999999999997,"Number Partial Discharge Capacitors (3x1phase)",null,null,"Number"]
[null,8.403999999999996,"Partial Discharge Analyser compatible with PD Capacitors",null,null,"Yes / No"]
[null,8.404999999999996,"Partial Discharge Analyser Specification including analysis software, communication & certification",null,null,"Number"]
[null,8.499999999999998,"Other Accessories:"]
[null,8.500999999999998,"Lightning Arresters",null,null,"Yes / No"]
[null,8.501999999999997,"Speed Switch",null,null,"Yes / No"]
[null,8.502999999999997,"Earthing Brush",null,null,"Yes / No"]
[null,8.503999999999996,"Reversing Shaft Interlock/Switch",null,null,"Yes / No"]
[null,8.599999999999998,"Space Heaters"]
[null,8.600999999999997,"Installed",null,null,"Yes / No","YES"]
[null,8.601999999999997,"Voltage Rating",null,null,"Volts AC",230]
[null,8.602999999999996,"Power Rating",null,null,"W"]
[null,8.603999999999996,"\"ON\" Pilot Lamp",null,null,"Yes / No","YES"]
[null,{"v":9,"d":"9.0"},"Interface  to Plant"]
[null,9.01,"Motor mounting (Horizontal / Vertical)  (Foot/Flange)",null,null,"IM Code"]
[null,9.02,"Rotation (viewed on motor drive shaft) with U- V- W",null,null,"Name"]
[null,9.03,"Maximum cable size that can fit on the terminal box",null,null,"mm2"]
[null,9.04,"Direction of cable entry (Line terminal box view) ",null,null,"Top / Bot / Left / Right"]
[null,9.049999999999999,"Cable type",null,null,"Code"]
[null,9.059999999999999,"Cable size",null,null,"mm2"]
[null,9.069999999999999,"Flood Lubricated Bearing Total Oil Flow",null,null,"Litres per minute"]
[null,9.079999999999998,"Oil Pressure",null,null,"kPa"]
[null,{"v":9.089999999999998,"d":"9.09"},"Inlet Oil Temperature Range",null,null,"ºC"]
[null,{"v":9.099999999999998,"d":"9.10"},"Water Cooled Bearing Total H2O Flow",null,null,"Litres per minute"]
[null,9.109999999999998,"Water Pressure",null,null,"kPa"]
[null,9.119999999999997,"Inlet Water Temperature",null,null,"ºC"]
[null,{"v":10,"d":"10.0"},"Motor Painting"]
[null,10.01,"Paint Finish",null,null,"Standard / Special"]
[null,10.02,"Number of Anti-rust Primer Coats",null,null,"Number"]
[null,10.03,"Internal Metal Surface Finish",null,null,"Describe"]
[null,10.04,"External Metal Surface Finish",null,null,"Describe"]
[null,10.049999999999999,"External Final Color Coding ",null,null,"SANS 1091 ","G29 - Light Grey"]
[null,{"v":11,"d":"11.0"},"Station Limitations"]
[null,11.01,"Maximum Motor Mass (Station limit)",null,null,"Ton",null,null,"Supplier not to exceed the limit"]
[null,11.02,"Maximum Allowed Overall Motor Height (Station limit)",null,null,"mm",null,null,"Supplier not to exceed the limit"]
[null,11.03,"Maximum Allowed Overall Motor Length (Station limit)",null,null,"mm",null,null,"Supplier not to exceed the limit"]
[null,11.04,"Maximum Allowed Overall Motor Breadth (Station limit)",null,null,"mm",null,null,"Supplier not to exceed the limit"]
[null,11.049999999999999,"Other",null,null,"Describe"]
[null,{"v":12,"d":"12.0"},"Documentation            "]
[null,12.1," Drawings "]
[null,12.100999999999999,"Motor Outline Drawing reference number",null,null,"Number"]
[null,12.101999999999999,"Power winding schematic diagrams  and  Auxiliaries schematic diagrams (PT100s, thermistor and  heaters) reference number",null,null,"Number"]
[null,12.102999999999998,"Location of RTDs around the stator",null,null,"Number"]
[null,12.2,"Motor Curves "]
[null,12.200999999999999,"Torque-speed curves plotted over the driven machine torque-speed curve \nat 100%, 85% and 75% Voltage reference number",null,null,"Number"]
[null,12.201999999999998,"Current-speed curves at 100%, 85% and 75% Voltage ",null,null,"Number"]
[null,12.202999999999998,"Efficiency and Power factor vs. load curves at rated voltage reference number",null,null,"Number"]
[null,12.203999999999997,"Thermal limit curves reference number",null,null,"Number"]