{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["Mnaual Valves"],"not_rendered":{"images":1,"defined_names":1},"read":"whole","date_system":"1900"}

{"sheet":"Mnaual Valves","index":0,"n_rows":15,"n_cols":16,"rows_kept":15,"merged":[[0,1,0,4],[0,5,0,9],[0,10,0,14],[1,1,1,3],[2,0,3,0],[2,1,3,1],[2,2,3,2],[2,3,3,3],[2,4,2,5],[2,6,2,7],[2,8,3,8],[2,9,3,9],[2,10,3,10],[2,11,3,11],[2,12,3,12],[2,13,3,13],[2,14,3,14],[2,15,3,15],[14,1,14,8],[14,12,14,14],[17,1,17,8]]}
[{"$nulls":5}," PTFE Filter Destruction Plant System Valve List\nFor procurement.",{"$nulls":4},"Page 1 of 4"]
[null,"Manual Valves"]
[null,"Valve type ","Valve code","Valve size","Design Conditions",null,"Operating Conditions",null,"Safety Class ","Valve Description","Quantity","NOTES   ","Supplier of Purchase","Lead-time","UNIT PRICING","PRICING"]
[{"$nulls":4},"Temp [°C]","Press.[kPa(g)]","Temp [°C]","Press.[kPa(g)]"]
[10,"Ball Valve ","CB","40 mm",93,1795,30,520,"SC  3","Connection ends: RF, B16.5, Class 150\nBody: CS, ASTM A105/A126 WCB\nTrim: 316 SS\nPacking/Seal: Graphite\nBall material: 316 SS\nBonnet/Cap: 316 SS",1]
[13,"Ball Valve ","CB","50 mm",93,1795,35,600,"SC  3","Connection ends: RF, B16.5, Class 150\nBody: CS ASTM A105/A216 WCB\nTrim: 316 SS\nPacking/Seal: Graphite\nBall material: 316 SS\nBonnet/Cap: 316 SS",3]
[15,"Ball Valve ","CB","100 mm",93,1585,45,-10,"SC  3","Connection ends: RF, B16.5, Class 150\nBody: CS ASTM A105/A216 WCB\nTrim: 316 SS\nPacking/Seal: Graphite\nBall material: 316 SS\nBonnet/Cap: 316 SS",2]
[17,"Globe Valve ","CG","15 mm",93,1795,25,4.4,"SC  3","Connection ends: RF, B16.15 or NPT-M/F as B1.20.1, Class 150\nBody: CS ASTM A105/A216 WCB\nTrim: 316 SS\nPacking/Seal: API 600\nBall material: 316 SS\nBonnet/Cap: 316 SS",1]
[19,"Globe Valve ","CG","25 mm",93,1795,"Amb",-5,"SC  3","Connection ends: RF, B16.5 or  NPT-M/F as B1.20.1, Class 150\nBody: CS, ASTM A105/A216 WCB\nTrim: CS\nPacking/Seal: API 600\nBall material: CS\nBonnet/Cap: CS",1]
[26,"Non-return Valve","CU","15 mm",93,1965,"Amb",520,"SC  3","Connection ends: RF, B16.5 OR NPT-F/M B1.20.1, Class 150\nBody: CS, ASTM A105/A216 WCB\nTrim: 13 CR\nPacking/Seal: API 602\nBall material: CS\nBonnet/Cap: CS",1]
[28,"Non-return Valve","CU","25 mm",93,1795,"Amb",-5,"SC  3","Connection ends: RF, B16.5 OR NPT -F/M B1.20.1, Class 150\nBody: CS, ASTM A105/A216 WCB\nTrim: 13 CR\nPacking/Seal: API 602\nBall material: CS\nBonnet/Cap: CS",1]
[31,"Non-return Valve","CU","50 mm",93,1795,25,247,"SC  3","Connection ends: RF, B16.5, Class 150\nBody: CS, ASTM A105/A126 WCB\nTrim: 13 CR\nPacking/Seal: API 602\nBonnet/Cap: CS",1]
[35," Strainer","CQ","50 mm",93,1795,25,4.4,"SC  3","Connection ends: RF, B16.5, Class 150\nBody: CS, ASTM A105/A126 WCB\nTrim: 13 CR\nPacking/Seal: CAF ( supplier to advise) \nBonnet/Cap: CS",1]
[36,"Floating Valve","CB","50 mm",93,1795,"Amb",600,"SC  3","Connection ends: RF, B16.5, Class 150\nBody: CS, ASTM A105/A126 WCB\nTrim: 13 CR\nPacking/Seal: CAF ( supplier to advise) \nBonnet/Cap: CS",1]
[{"$nulls":9},"Total:",{"$f":"SUM(K5:K14)","v":13},null,"TOTAL:",null,null,{"$f":"SUM( P5:P14)","v":0}]