NEC3 Engineering & Construction Contract

| Between | ESKOM HOLDINGS SOC Ltd (Reg No. 2002/015527/30) |  |
| --- | --- | --- |
| and | [Insert at award stage] (Reg No. ___________) |  |
| for | Tenant Installation for Eskom Parliament office in Cape town for Eskom Executive Office |  |
| Contents: |  | No of pages |
| Part C1 | Agreements & Contract Data | [?] |
| Part C2 | Pricing Data | [?] |
| Part C3 | Scope of Work | [?] |
| Part C4 | Site Information | [?] |
| CONTRACT No. | [Insert at award stage] |  |

Part C1: Agreements & Contract Data

| contents: |  | No of pages |
| --- | --- | --- |
| C1.1 | Form of Offer and Acceptance [to be inserted from Returnable Documents at award stage] | [ ] |
| C1.2a | Contract Data provided by the Employer | [ ] |
| C1.2b | Contract Data provided by the Contractor [to be inserted from Returnable Documents at award stage] | [ ] |
| C1.3 | Proforma Guarantees | [ ] |

C1.1 Form of Offer & Acceptance

## Offer

The Employer, identified in the Acceptance signature block, has solicited offers to enter into a contract for the procurement of:

# Tenant Installation for Eskom Parliament office in Cape town for Eskom Executives

The tenderer, identified in the Offer signature block, has examined the documents listed in the Tender Data and addenda thereto and by submitting this Offer has accepted the Conditions of Tender.

By the representative of the tenderer, deemed to be duly authorised, signing this part of this Form of Offer and Acceptance the tenderer offers to perform all of the obligations and liabilities of the Contractor under the contract including compliance with all its terms and conditions according to their true intent and meaning for an amount to be determined in accordance with the conditions of contract identified in the Contract Data.

Delete the Options which do not apply

| Options B, | The offered total of the Prices exclusive of VAT is | R [●] |
| --- | --- | --- |
|  | The first forecast of the total Defined Cost plus the Fee exclusive of VAT is | R [●] |
|  | Sub total | R [●] |
|  | Value Added Tax @ 15% is | R [●] |
|  | The offered total of the amount due inclusive of VAT is | R [●] |
|  | (in words) [●] |  |

This Offer may be accepted by the Employer by signing the Acceptance part of this Form of Offer and Acceptance and returning one copy of this document including the Schedule of Deviations (if any) to the tenderer before the end of the period of validity stated in the Tender Data, or other period as agreed, whereupon the tenderer becomes the party named as the Contractor in the conditions of contract identified in the Contract Data.

| Signature(s) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name(s) |  |  |  |  |
| Capacity |  |  |  |  |
| For the tenderer: |  |  |  |  |
| Name & signature of witness | (Insert name and address of organisation) |  | Date |  |
| Tenderer’s CIDB registration number (if applicable) |  |  |  |  |

## Acceptance

By signing this part of this Form of Offer and Acceptance, the Employer identified below accepts the tenderer’s Offer.  In consideration thereof, the Employer shall pay the Contractor the amount due in accordance with the conditions of contract identified in the Contract Data.  Acceptance of the tenderer’s Offer shall form an agreement between the Employer and the tenderer upon the terms and conditions contained in this agreement and in the contract that is the subject of this agreement.

The terms of the contract, are contained in:

Part C1		Agreements and Contract Data, (which includes this Form of Offer and Acceptance)

Part C2		Pricing Data

Part C3		Scope of Work: Works Information

Part C4		Site Information

and drawings and documents (or parts thereof), which may be incorporated by reference into the above listed Parts.

Deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Returnable Schedules as well as any changes to the terms of the Offer agreed by the tenderer and the Employer during this process of offer and acceptance, are contained in the Schedule of Deviations attached to and forming part of this Form of Offer and Acceptance.  No amendments to or deviations from said documents are valid unless contained in this Schedule.

The tenderer shall within two weeks of receiving a completed copy of this agreement, including the Schedule of Deviations (if any), contact the Employer’s agent (whose details are given in the Contract Data) to arrange the delivery of any securities, bonds, guarantees, proof of insurance and any other documentation to be provided in terms of the conditions of contract identified in the Contract Data at, or just after, the date this agreement comes into effect.  Failure to fulfil any of these obligations in accordance with those terms shall constitute a repudiation of this agreement.

Notwithstanding anything contained herein, this agreement comes into effect on the date when the tenderer receives one fully completed original copy signed between them of this document, including the Schedule of Deviations (if any).

Unless the tenderer (now Contractor) within five working days of the date of such receipt notifies the Employer in writing of any reason why he cannot accept the contents of this agreement, this agreement shall constitute a binding contract between the Parties.

| Signature(s) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name(s) |  |  |  |  |
| Capacity |  |  |  |  |
| for the Employer | Eskom Holdings SOC Ltd, 1 Maxwell Drive, Sunninghill, Sandton, 2157 |  |  |  |
| Name & signature of witness | (Insert name and address of organisation) |  | Date |  |

Note: If a tenderer wishes to submit alternative tenders, use another copy of this Form of Offer and Acceptance.

## Schedule of Deviations to be completed by the Employer prior to contract award

Note:

- This part of the Offer & Acceptance would not be required if the contract has been developed by negotiation between the Parties and is not the result of a process of competitive tendering.

- The extent of deviations from the tender documents issued by the Employer prior to the tender closing date is limited to those permitted in terms of the Conditions of Tender.

- A tenderer’s covering letter must not be included in the final contract document.  Should any matter in such letter, which constitutes a deviation as aforesaid be the subject of agreement reached during the process of Offer and Acceptance, the outcome of such agreement shall be recorded here and the final draft of the contract documents shall be revised to incorporate the effect of it.

| No. | Subject | Details |
| --- | --- | --- |
| 1 | Not Applicable [●] | Not Applicable [●] |
| 2 | [●] | [●] |
| 3 | [●] | [●] |
| 4 | [●] | [●] |
| 5 | [●] | [●] |
| 6 | [●] | [●] |
| 7 | [●] | [●] |

By the duly authorised representatives signing this Schedule of Deviations below, the Employer and the tenderer agree to and accept this Schedule of Deviations as the only deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules, as well as any confirmation, clarification or changes to the terms of the Offer agreed by the tenderer and the Employer during this process of Offer and Acceptance.

It is expressly agreed that no other matter whether in writing, oral communication or implied during the period between the issue of the tender documents and the receipt by the tenderer of a completed signed copy of this Form shall have any meaning or effect in the contract between the parties arising from this Agreement.

|  | #### For the tenderer: |  | #### For the Employer |
| --- | --- | --- | --- |
| Signature |  |  |  |
| Name |  |  |  |
| Capacity |  |  |  |
| On behalf of | (Insert name and address of organisation) |  | (Insert name and address of organisation) Eskom Holdings SOC Ltd, 1 Maxwell Drive, Sunninghill, Sandton, 2157 |
| Name & signature of witness |  |  |  |
| Date |  |  |  |

C1.2 ECC3 Contract Data

# Part one - Data provided by the Employer

Completion of the data in full, according to the Options chosen, is essential to create a complete contract.

This contract is based on the NEC3 Engineering and Construction Contract (April 2013 edition). The full provisions of the NEC3 ECC, including its Core Clauses and selected Main and Secondary Options, shall apply and are deemed incorporated herein, except where expressly amended by the Employer’s Z-clauses

| ## Clause | ## Statement | ## Data |
| --- | --- | --- |
| 1 | ## General |  |
|  | The conditions of contract are the core clauses and the clauses for main Option |  |
|  |  | B: Priced contract with bill of quantities |
|  | dispute resolution Option | W1: Dispute resolution procedure |
|  | and secondary Options |  |
|  |  | X1: Price adjustment for inflation |
|  |  | X2 Changes in the law |
|  |  | X7: Delay damages |
|  |  | X12: Partnering |
|  |  | X13: Performance Bond |
|  |  | X16: Retention |
|  |  | X17: Low performance damages |
|  |  | X18: Limitation of liability |
|  |  | Z: Additional conditions of contract |
|  | of the NEC3 Engineering and Construction Contract, April 2013 (ECC3) | If 2005 Edition is to be used delete “April 2013” and replace with “June 2005 with amendments June 2006”. Always delete this note before finalising this Data |

| 10.1 | The Employer is (Name): |  |  | Eskom Holdings SOC Ltd (reg no: 2002/015527/30), a state-owned company incorporated in terms of the company laws of the Republic of South Africa |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Address |  |  | Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg |  |  |  |  |  |  |  |
| 10.1 | The Project Manager is: (Name) |  |  | [●] Likotsi Matlali |  |  |  |  |  |  |  |
|  | Address |  |  | Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg |  |  |  |  |  |  |  |
|  | Tel |  |  | [●] 011 800 3332 |  |  |  |  |  |  |  |
|  | Fax |  |  | [●] 086538 1915 |  |  |  |  |  |  |  |
|  | e-mail |  |  | [●] matlalLP@eskom.co.za |  |  |  |  |  |  |  |
| 10.1 | The Supervisor is: (Name) |  |  | [●] Sifiso Gwala |  |  |  |  |  |  |  |
|  | Address |  |  | Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg |  |  |  |  |  |  |  |
|  | Tel No. |  |  | [●] 073 053 6961 |  |  |  |  |  |  |  |
|  | Fax No. |  |  | [●] 0865381915 |  |  |  |  |  |  |  |
|  | e-mail |  |  | [●]GwalaSH@eskom.co.za |  |  |  |  |  |  |  |
| 11.2(13) | The works are |  |  | Tenant Installation for Eskom Parliament office in Cape town for Eskom Executive Office including all associated works in accordance with the Works Information. |  |  |  |  |  |  |  |
| 11.2(14) | The following matters will be included in the Risk Register |  |  | - The Contractor is aware that the site surroundings are operational during the construction and provides the necessary Health & Safety and security measures to ensure that mitigations are in place. - Further risks to be identified at the initial project meeting and on an ongoing basis. - The Contractor is aware of the Eskom Health & Safety and security requirements and standard that must be adhered to and comply with. - Limited as-built, operation and maintenance information available |  |  |  |  |  |  |  |
| 11.2(15) | The boundaries of the site are |  |  | 8th Floor 8 Riebeek Street Building Thibault Square in Cape town |  |  |  |  |  |  |  |
| 11.2(16) | The Site Information is in |  |  | Part 4: Site Information: 8th Floor 8 Riebeek Street Building Thibault Square in Cape town |  |  |  |  |  |  |  |
| 11.2(19) | The Works Information is in |  |  | Part 3: Scope of Work and all documents and drawings to which it makes reference. |  |  |  |  |  |  |  |
| 12.2 | The law of the contract is the law of |  |  | the Republic of South Africa |  |  |  |  |  |  |  |
| 13.1 | The language of this contract is |  |  | English |  |  |  |  |  |  |  |
| 13.3 | The period for reply is |  |  | Five (5) working days |  |  |  |  |  |  |  |
| ## 2 | ## The Contractor's main responsibilities |  |  | Data required by this section of the core clauses is provided by the Contractor in Part 2 and terms in italics used in this section are identified elsewhere in this Contract Data. |  |  |  |  |  |  |  |
| ## 3 | ## Time |  |  |  |  |  |  |  |  |  |  |
| 11.2(3) | The completion date for the whole of the works is |  |  | 3 months (post appointment) |  |  |  |  |  |  |  |
| 11.2(9) | The key dates and the conditions to be met are: |  |  | Condition to be met |  |  |  |  |  | key date |  |
|  |  |  |  | 1 | The appointment to access the site during tender should be granted by the Project Manager |  |  |  |  | As per approved schedule to be provided |  |
|  |  |  |  | 2 3 | Installation completed Issue Compliance certificate and hand over to Eskom |  |  |  |  | Date Date |  |
| 30.1 | The access dates are: |  |  | Part of the Site |  |  |  |  | Date |  |  |
|  |  |  |  | 1 | 8th Floor 8 Riebeek Street Building Thibault Square in Cape town with all regulation approvals to access and work |  |  |  | Before execution of work |  |  |
| 31.1 | The Contractor is to submit a first programme for acceptance within |  |  | 1 weeks of the Contract Date. |  |  |  |  |  |  |  |
| 31.2 | The starting date is |  |  |  |  |  |  |  |  |  |  |
| 32.2 | The Contractor submits revised programmes at intervals no longer than |  |  | 2 weeks. |  |  |  |  |  |  |  |
| 35.1 | The Employer is not willing to take over the works before the Completion Date. |  |  | All works are completed before the Employer takes over the works – full work completed |  |  |  |  |  |  |  |
| ## 4 | ## Testing and Defects |  |  |  |  |  |  |  |  |  |  |
| 42.2 | The defects date is |  |  | 52 weeks after Completion of the whole of the works. |  |  |  |  |  |  |  |
| 43.2 | The defect correction period is |  |  | One (1) week |  |  |  |  |  |  |  |
| ## 5 | ## Payment |  |  |  |  |  |  |  |  |  |  |
| 50.1 | The assessment interval is |  |  | On the 25 days of each successive month. |  |  |  |  |  |  |  |
| 51.1 | The currency of this contract is the |  |  | South African Rand. |  |  |  |  |  |  |  |
| 51.2 | The period within which payments are made is |  |  | 2 weeks |  |  |  |  |  |  |  |
| 51.4 | The interest rate is |  |  | the publicly quoted prime rate of interest (calculated on a 365-day year) charged from time to time by the Standard Bank of South Africa Limited (as certified, in the event of any dispute, by any manager of such bank, whose appointment it shall not be necessary to prove) for amounts due in Rands and (ii) the LIBOR rate applicable at the time for amounts due in other currencies. LIBOR is the 6 month London Interbank Offered Rate quoted under the caption “Money Rates” in The Wall Street Journal for the applicable currency or if no rate is quoted for the currency in question then the rate for United States Dollars, and if no such rate appears in The Wall Street Journal then the rate as quoted by the Reuters Monitor Money Rates Service (or such service as may replace the Reuters Monitor Money Rates Service) on the due date for the payment in question, adjusted mutatis mutandis every 6 months thereafter and as certified, in the event of any dispute, by any manager employed in the foreign exchange department of The Standard Bank of South Africa Limited, whose appointment it shall not be necessary to prove. |  |  |  |  |  |  |  |
| ## 6 | ## Compensation events |  |  |  |  |  |  |  |  |  |  |
| 60.1(13) | The place where weather is to be recorded is: |  |  | Cape town ,Western cape and surrounding areas to the site |  |  |  |  |  |  |  |
|  | The weather measurements to be recorded for each calendar month are, |  |  | the cumulative rainfall (mm) |  |  |  |  |  |  |  |
|  |  |  |  | the number of days with rainfall more than 10 mm |  |  |  |  |  |  |  |
|  |  |  |  | the number of days with minimum air temperature less than 0 degrees Celsius |  |  |  |  |  |  |  |
|  |  |  |  | the number of days with snow lying at 09:00 hours South African Time |  |  |  |  |  |  |  |
|  |  |  |  | and these measurements: |  |  |  |  |  |  |  |
|  | The weather measurements are supplied by |  |  | The South African Weather Bureau at the nearest station next to the site. |  |  |  |  |  |  |  |
|  | The weather data are the records of past weather measurements for each calendar month which were recorded at: |  |  |  |  |  |  |  |  |  |  |
|  | and which are available from: |  |  | the South African Weather Bureau and included in Annexure A to this Contract Data provided by the Employer |  |  |  |  |  |  |  |
| 60.1(13) | Assumed values for the ten-year return weather data for each weather measurement for each calendar month are: |  |  | As stated in Annexure A to this Contract Data provided by the Employer. Note: If this arrangement is used, delete the rows above for 60.1(13) and delete this note. |  |  |  |  |  |  |  |
| ## 7 | ## Title |  |  | There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data. |  |  |  |  |  |  |  |
| ## 8 | ## Risks and insurance |  |  |  |  |  |  |  |  |  |  |
| 80.1 | These are Employer's risks |  |  | - Health & Safety - Time/ project to be completed on time - Legal/Regulatory - Commercial - Environmental - Security - Coordination |  |  |  |  |  |  |  |
| ## 9 | ## Termination |  |  | There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data. |  |  |  |  |  |  |  |
| ## 10 | ## Data for main Option clause |  |  |  |  |  |  |  |  |  |  |
| B | Priced contract with bill of quantities |  |  |  |  |  |  |  |  |  |  |
| 60.6 | The method of measurement is |  |  | Option B published by NEC 3 Engineering and Construction Contract of June 2005 and amended as stated in Part C2.1, Pricing Assumptions. |  |  |  |  |  |  |  |
| ## 11 | ## Data for Option W1 |  |  |  |  |  |  |  |  |  |  |
| W1.1 | The Adjudicator is |  |  | the person selected from the ICE-SA Division (or its successor body) of the South African Institution of Civil Engineering Panel of Adjudicators by the Party intending to refer a dispute to him. (see www.ice-sa.org.za). If the Parties do not agree on an Adjudicator the Adjudicator will be appointed by the Arbitration Foundation of Southern Africa (AFSA). |  |  |  |  |  |  |  |
|  | Address |  |  | [●]TBA |  |  |  |  |  |  |  |
|  | Tel No. |  |  | [●]TBA |  |  |  |  |  |  |  |
|  | Fax No. |  |  | [●]TBA |  |  |  |  |  |  |  |
|  | e-mail |  |  | [●]TBA |  |  |  |  |  |  |  |
| W1.2(3) | The Adjudicator nominating body is: |  |  | the Chairman of ICE-SA a joint Division of the South African Institution of Civil Engineering and the London Institution of Civil Engineers. (See www.ice-sa.org.za ) or its successor body. |  |  |  |  |  |  |  |
| W1.4(2) | The tribunal is: |  |  | arbitration. |  |  |  |  |  |  |  |
| W1.4(5) | The arbitration procedure is |  |  | the latest edition of Rules for the Conduct of Arbitrations published by The Association of Arbitrators (Southern Africa) or its successor body. |  |  |  |  |  |  |  |
|  | The place where arbitration is to be held is |  |  | Gauteng in South Africa |  |  |  |  |  |  |  |
|  | The person or organisation who will choose an arbitrator - if the Parties cannot agree a choice or - if the arbitration procedure does not state who selects an arbitrator, is |  |  | the Chairman for the time being or his nominee of the Association of Arbitrators (Southern Africa) or its successor body. |  |  |  |  |  |  |  |
| ## 12 | ## Data for secondary Option clauses |  |  |  |  |  |  |  |  |  |  |
| X1 | Price adjustment for inflation |  |  |  |  |  |  |  |  |  |  |
| X1.1(a) | The base date for indices is |  |  | CPI applicable if project is 12 months or more. Base date is one month prior to tender close |  |  |  |  |  |  |  |
| X1.1(c) | The proportions used to calculate the Price Adjustment Factor are: |  |  | proportion |  | linked to index for |  | Index prepared by |  |  |  |
|  |  |  |  | N/A |  | N/A |  | N/A |  |  |  |
|  | Total |  |  |  |  |  |  |  |  |  |  |
| X2 | Changes in the law |  |  | The law of the Republic of South Africa |  |  |  |  |  |  |  |
| X7 | Delay damages |  |  |  |  |  |  |  |  |  |  |
| X7.1 | Delay damages for Completion of the whole of the works are |  |  | R10,000.00 per day up to a limit of 20% of the Contract Value. |  |  |  |  |  |  |  |
| X12 | Partnering |  |  |  |  |  |  |  |  |  |  |
| X12.1(1) | The Client is (Name) |  |  | [●] |  |  |  |  |  |  |  |  |
|  | Address |  |  | [●] |  |  |  |  |  |  |  |  |
|  | Tel |  |  | [●] |  |  |  |  |  |  |  |  |
|  | Fax |  |  | [●] |  |  |  |  |  |  |  |  |
| X12.2(1) | The Client’s objective is. |  |  | [●] |  |  |  |  |  |  |  |  |
| X12.1(4) | The Partnering Information is in |  |  | [●] |  |  |  |  |  |  |  |  |
| X13 | Performance bond |  | N/A |  |  |  |  |  |  |  |  |  |
| X13.1 | The amount of the performance bond is |  | R [●]. N/A |  |  |  |  |  |  |  |
| X16 | Retention (not used with Option F) |  |  |  |  |  |  |  |  |  |
| X16.1 | The retention free amount is |  | As per above |  |  |  |  |  |  |  |
|  | The retention percentage is |  | 10% of the payment certificate 50% will be released 6 months after completion, another 50 % on expiry of the defect period. |  |  |  |  |  |  |  |
| X17 | Low performance damages |  |  |  |  |  |  |  |  |  |  |
| X17.1 | The amounts for low performance damages are: |  |  | Amount |  |  | Performance level |  |  |  |  |
|  |  |  |  | R 2,000 per day |  |  | Compliance with Safety file/ plan requirements. (If not approved as per the Accepted Programme within 1 week from submission, it shall be deemed to be approved) |  |  |  |  |
|  |  |  |  | R 7,500 per day |  |  | Failure to complete the task on a critical path on time as per the agreed Programme. |  |  |  |  |
|  |  |  |  | R 2,000 per day |  |  | For every incident where a Quality Control Plan is not submitted in accordance with the schedule and delays the starting of that activity |  |  |  |  |
|  |  |  |  | R 2,000 per day |  |  | For every incident of quality non- compliance where Contractor fails to notify the Employer. And witness points on Quality Control Plan’s |  |  |  |  |
|  |  |  |  | R 2,000 per day |  |  | For every incident where reworks is done three times and more. |  |  |  |  |
|  | The total low performance damages payable by the Contractor does not exceed: |  |  |  |  |  | The total delay damages payable by the Contractor does not exceed 2% of the Contract Price |  |  |  |  |
| X18 | Limitation of liability |  |  |  |  |  |  |  |  |  |  |
| X18.1 | The Contractor’s liability to the Employer for indirect or consequential loss is limited to: |  |  | R0.0 (zero Rand) |  |  |  |  |  |  |  |
| X18.2 | For any one event, the Contractor’s liability to the Employer for loss of or damage to the Employer’s property is limited to: |  |  | the amount of the deductibles relevant to the event |  |  |  |  |  |  |  |
| X18.3 | The Contractor’s liability for Defects due to his design which are not listed on the Defects Certificate is limited to |  |  | The greater of the total of the Prices at the Contract Date and - the amounts excluded and unrecoverable from the Employer’s assets policy for correcting the Defect (other than the resulting physical damage which is not excluded) plus the applicable deductible as at contract date. |  |  |  |  |  |  |  |
| X18.4 | The Contractor’s total liability to the Employer for all matters arising under or in connection with this contract, other than excluded matters, is limited to: |  |  | the total of the Prices other than for the additional excluded matters. The Contractor’s total liability for the additional excluded matters is not limited. The additional excluded matters are amounts for which the Contractor is liable under this contract for Defects due to his design which arise before the Defects Certificate is issued, loss of or damage to property (other than the works, Plant and Materials), defects that arise to structures outside of the scope as well as damages to equipment and services that the Contractor is required to protect. death of or injury to a person and infringement of an intellectual property right. |  |  |  |  |  |  |  |
| X18.5 | The end of liability date is |  |  | (i) one (1) year after the defects date for latent Defects and (ii) the date on which the liability in question prescribes in accordance with the Prescription Act No. 68 of 1969 (as amended or in terms of any replacement legislation) for any other matter. A latent Defect is a Defect which would not have been discovered on reasonable inspection by the Employer or the Supervisor before the defects date, without requiring any inspection not ordinarily carried out by the Employer or the Supervisor during that period. If the Employer or the Supervisor do undertake any inspection over and above the reasonable inspection, this does not place a greater responsibility on the Employer or the Supervisor to have discovered the Defect. |  |  |  |  |  |  |  |
| Z | The Additional conditions of contract are |  |  | Z1 to Z15 always apply. |  |  |  |  |  |  |  |
| Z1 | Cession delegation and assignment |  |  |  |  |  |  |  |  |  |  |
| Z1.1 | The Contractor does not cede, delegate or assign any of its rights or obligations to any person without the written consent of the Employer. |  |  |  |  |  |  |  |  |  |  |
| Z1.2 | Notwithstanding the above, the Employer may on written notice to the Contractor cede and delegate its rights and obligations under this contract to any of its subsidiaries or any of its present divisions or operations which may be converted into separate legal entities as a result of the restructuring of the Electricity Supply Industry. |  |  |  |  |  |  |  |  |  |  |
| Z2 | Joint ventures |  |  |  |  |  |  |  |  |  |  |
| Z2.1 | If the Contractor constitutes a joint venture, consortium or other unincorporated grouping of two or more persons or organisations then these persons or organisations are deemed to be jointly and severally liable to the Employer for the performance of this contract. |  |  |  |  |  |  |  |  |  |  |
| Z2.2 | Unless already notified to the Employer, the persons or organisations notify the Project Manager within two weeks of the Contract Date of the key person who has the authority to bind the Contractor on their behalf. |  |  |  |  |  |  |  |  |  |  |
| Z2.3 | The Contractor does not alter the composition of the joint venture, consortium or other unincorporated grouping of two or more persons without the consent of the Employer having been given to the Contractor in writing. |  |  |  |  |  |  |  |  |  |  |
| Z3 | Change of Broad Based Black Economic Empowerment (B-BBEE) status |  |  |  |  |  |  |  |  |  |  |
| Z3.1 | Where a change in the Contractor’s legal status, ownership or any other change to his business composition or business dealings results in a change to the Contractor’s B-BBEE status, the Contractor notifies the Employer within seven days of the change. |  |  |  |  |  |  |  |  |  |  |
| Z3.2 | The Contractor is required to submit an updated verification certificate and necessary supporting documentation confirming the change in his B-BBEE status to the Project Manager within thirty days of the notification or as otherwise instructed by the Project Manager. |  |  |  |  |  |  |  |  |  |  |
| Z3.3 | Where, as a result, the Contractor’s B-BBEE status has decreased since the Contract Date the Employer may either re-negotiate this contract or alternatively, terminate the Contractor’s obligation to Provide the Works. |  |  |  |  |  |  |  |  |  |  |
| Z3.4 | Failure by the Contractor to notify the Employer of a change in its B-BBEE status may constitute a reason for termination. If the Employer terminates in terms of this clause, the procedures on termination are P1, P2 and P3 as stated in clause 92, and the amount due is A1 and A3 as stated in clause 93. |  |  |  |  |  |  |  |  |  |  |
| Z4 | Confidentiality |  |  |  |  |  |  |  |  |  |  |
| Z4.1 | The Contractor does not disclose or make any information arising from or in connection with this contract available to Others. This undertaking does not, however, apply to information which at the time of disclosure or thereafter, without default on the part of the Contractor, enters the public domain or to information which was already in the possession of the Contractor at the time of disclosure (evidenced by written records in existence at that time). Should the Contractor disclose information to Others in terms of clause 25.1, the Contractor ensures that the provisions of this clause are complied with by the recipient. |  |  |  |  |  |  |  |  |  |  |
| Z4.2 | If the Contractor is uncertain about whether any such information is confidential, it is to be regarded as such until notified otherwise by the Project Manager. |  |  |  |  |  |  |  |  |  |  |
| Z4.3 | In the event that the Contractor is, at any time, required by law to disclose any such information which is required to be kept confidential, the Contractor, to the extent permitted by law prior to disclosure, notifies the Employer so that an appropriate protection order and/or any other action can be taken if possible, prior to any disclosure. In the event that such protective order is not, or cannot, be obtained, then the Contractor may disclose that portion of the information which it is required to be disclosed by law and uses reasonable efforts to obtain assurances that confidential treatment will be afforded to the information so disclosed. |  |  |  |  |  |  |  |  |  |  |
| Z4.4 | The taking of images (whether photographs, video footage or otherwise) of the works or any portion thereof, in the course of Providing the Works and after Completion, requires the prior written consent of the Project Manager. All rights in and to all such images vests exclusively in the Employer. |  |  |  |  |  |  |  |  |  |  |
| Z4.5 | The Contractor ensures that all his subcontractors abide by the undertakings in this clause. |  |  |  |  |  |  |  |  |  |  |
| Z5 | Waiver and estoppel: Add to core clause 12.3: |  |  |  |  |  |  |  |  |  |  |
| Z5.1 | Any extension, concession, waiver or relaxation of any action stated in this contract by the Parties, the Project Manager, the Supervisor, or the Adjudicator does not constitute a waiver of rights and does not give rise to an estoppel unless the Parties agree otherwise and confirm such agreement in writing. |  |  |  |  |  |  |  |  |  |  |
| Z6 | Health, safety and the environment: Add to core clause 27.4 |  |  |  |  |  |  |  |  |  |  |
| Z6.1 | The Contractor undertakes to take all reasonable precautions to maintain the health and safety of persons in and about the execution of the works. Without limitation the Contractor: accepts that the Employer may appoint him as the “Principal Contractor” (as defined and provided for under the Construction Regulations 2014 (promulgated under the Occupational Health & Safety Act 85 of 1993) (“the Construction Regulations”) for the Site; warrants that the total of the Prices as at the Contract Date includes a sufficient amount for proper compliance with the Construction Regulations, all applicable health & safety laws and regulations and the health and safety rules, guidelines and procedures provided for in this contract and generally for the proper maintenance of health & safety in and about the execution of works; and undertakes, in and about the execution of the works, to comply with the Construction Regulations and with all applicable health & safety laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |  |  |  |  |  |  |  |  |  |  |
| Z6.2 | The Contractor, in and about the execution of the works, complies with all applicable environmental laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |  |  |  |  |  |  |  |  |  |  |
| Z7 | Provision of a Tax Invoice and interest. Add to core clause 51 |  |  |  |  |  |  |  |  |  |  |
| Z7.1 | Within one week of receiving a payment certificate from the Project Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice in accordance with the Employer's procedures stated in the Works Information, showing the amount due for payment equal to that stated in the payment certificate. |  |  |  |  |  |  |  |  |  |  |
| Z7.2 | If the Contractor does not provide a tax invoice in the form and by the time required by this contract, the time by when the Employer is to make a payment is extended by a period equal in time to the delayed submission of the correct tax invoice. Interest due by the Employer in terms of core clause 51.2 is then calculated from the delayed date by when payment is to be made. |  |  |  |  |  |  |  |  |  |  |
| Z7.3 | The Contractor (if registered in South Africa in terms of the companies Act) is required to comply with the requirements of the Value Added Tax Act, no 89 of 1991 (as amended) and to include the Employer’s VAT number 4740101508 on each invoice he submits for payment. |  |  |  |  |  |  |  |  |  |  |
| Z8 | Notifying compensation events |  |  |  |  |  |  |  |  |  |  |
| Z8.1 | Delete from the last sentence in core clause 61.3, “unless the Project Manager should have notified the event to the Contractor but did not”. |  |  |  |  |  |  |  |  |  |  |
| Z9 | Employer’s limitation of liability |  |  |  |  |  |  |  |  |  |  |
| Z9.1 | The Employer’s liability to the Contractor for the Contractor’s indirect or consequential loss is limited to R0.00 (zero Rand) |  |  |  |  |  |  |  |  |  |  |
| Z9.2 | The Contractor’s entitlement under the indemnity in 83.1 is provided for in 60.1(14) and the Employer’s liability under the indemnity is limited. |  |  |  |  |  |  |  |  |  |  |
| Z10 | Termination: Add to core clause 91.1, at the second main bullet point, fourth sub-bullet point, after the words "against it": |  |  |  |  |  |  |  |  |  |  |
| Z10.1 | or had a business rescue order granted against it. |  |  |  |  |  |  |  |  |  |  |
| Z11 | Addition to secondary Option X7 Delay damages (if applicable in this contract) |  |  |  |  |  |  |  |  |  |  |
| Z11.1 | If the amount due for the Contractor’s payment of delay damages reaches the limits stated in this Contract Data for Option X7 or Options X5 and X7 used together, the Employer may terminate the Contractor’s obligation to Provide the Works using the same procedures and payment on termination as those applied for reasons R1 to R15 or R18 stated in the Termination Table. |  |  |  |  |  |  |  |  |  |  |
| Z12 | Ethics |  |  |  |  |  |  |  |  |  |  |
| For the purposes of this Z-clause, the following definitions apply: |  |  |  |  |  |  |  |  |  |  |  |
| Affected Party |  | means, as the context requires, any party, irrespective of whether it is the Contractor or a third party, such party’s employees, agents, or Subcontractors or Subcontractor’s employees, or any one or more of all of these parties’ relatives or friends, |  |  |  |  |  |  |  |  |  |
| Coercive Action |  | means to harm or threaten to harm, directly or indirectly, an Affected Party or the property of an Affected Party, or to otherwise influence or attempt to influence an Affected Party to act unlawfully or illegally, |  |  |  |  |  |  |  |  |  |
| Collusive Action |  | means where two or more parties co-operate to achieve an unlawful or illegal purpose, including to influence an Affected Party to act unlawfully or illegally, |  |  |  |  |  |  |  |  |  |
| Committing Party |  | means, as the context requires, the Contractor, or any member thereof in the case of a joint venture, or its employees, agents, or Subcontractor or the Subcontractor’s employees, |  |  |  |  |  |  |  |  |  |
| Corrupt Action |  | means the offering, giving, taking, or soliciting, directly or indirectly, of a good or service to unlawfully or illegally influence the actions of an Affected Party, |  |  |  |  |  |  |  |  |  |
| Fraudulent Action |  | means any unlawfully or illegally intentional act or omission that misleads, or attempts to mislead, an Affected Party, in order to obtain a financial or other benefit or to avoid an obligation or incurring an obligation, |  |  |  |  |  |  |  |  |  |
| Obstructive Action |  | means a Committing Party unlawfully or illegally destroying, falsifying, altering or concealing information or making false statements to materially impede an investigation into allegations of Prohibited Action, and |  |  |  |  |  |  |  |  |  |
| Prohibited Action |  | means any one or more of a Coercive Action, Collusive Action Corrupt Action, Fraudulent Action or Obstructive Action. |  |  |  |  |  |  |  |  |  |
| Z12.1 | A Committing Party may not take any Prohibited Action during the course of the procurement of this contract or in execution thereof. |  |  |  |  |  |  |  |  |  |  |
| Z12.2 | The Employer may terminate the Contractor’s obligation to Provide the Services if a Committing Party has taken such Prohibited Action and the Contractor did not take timely and appropriate action to prevent or remedy the situation, without limiting any other rights or remedies the Employer has. It is not required that the Committing Party had to have been found guilty, in court or in any other similar process, of such Prohibited Action before the Employer can terminate the Contractor’s obligation to Provide the Services for this reason. |  |  |  |  |  |  |  |  |  |  |
| Z12.3 | If the Employer terminates the Contractor’s obligation to Provide the Services for this reason, the amounts due on termination are those intended in core clauses 92.1 and 92.2. |  |  |  |  |  |  |  |  |  |  |
| Z12.4 | A Committing Party co-operates fully with any investigation pursuant to alleged Prohibited Action. Where the Employer does not have a contractual bond with the Committing Party, the Contractor ensures that the Committing Party co-operates fully with an investigation. |  |  |  |  |  |  |  |  |  |  |
| Z13 | Insurance |  |  |  |  |  |  |  |  |  |  |
| Z 13.1 | Replace core clause 84 with the following: |  |  |  |  |  |  |  |  |  |  |

| Insurance cover |  | 84 |  |  |
| --- | --- | --- | --- | --- |
|  |  | 84.1 |  | When requested by a Party, the other Party provides certificates from his insurer or broker stating that the insurances required by this contract are in force. |
|  |  | 84.2 |  | The Contractor provides the insurances stated in the Insurance Table A. |
|  |  | 84.3 |  | The insurances provide cover for events which are at the Contractor’s risk from the starting date until the earlier of Completion and the date of the termination certificate. |
|  |  |  |  | ### INSURANCE TABLE A Insurance against; Minimum amount of cover or minimum limit of indemnity. Loss of or damage to the works, Plant and Materials; The replacement cost where not covered by the Employer’s insurance The Employer’s policy deductible, as at Contract Date, where covered by the Employer’s insurance. Loss of or damage to Equipment; The replacement cost. Liability for loss of or damage to property (except the works, Plant and Materials and Equipment) and liability for bodily injury to or death of a person (not an employee of the Contractor) caused by activity in connection with this contract; Loss of or damage to property Employer’s property The replacement cost where not covered by the Employer’s insurance The Employer’s policy deductible, as at Contract Date, where covered by the Employer’s insurance Other property The replacement cost Bodily injury to or death of a person The amount required by applicable law. Liability for death of or bodily injury to employees of the Contractor arising out of and in the course of their employment in connection with this contract; The amount required by the applicable law. |
| Z 13.2 |  |  |  | Replace core clause 87 with the following: The Employer provides the insurances stated in the Insurance Table B. |
|  |  |  |  | #### INSURANCE TABLE B Insurance against or name of policy; Minimum amount of cover or minimum limit of indemnity. Assets All Risk; Per the insurance policy document. Contract Works insurance; Per the insurance policy document. Environmental Liability; Per the insurance policy document. General and Public Liability; Per the insurance policy document. Transportation (Marine); Per the insurance policy document. Motor Fleet and Mobile Plant; Per the insurance policy document. Terrorism; Per the insurance policy document. Cyber Liability; Per the insurance policy document. Nuclear Material Damage and Business Interruption; Per the insurance policy document. Nuclear Material Damage Terrorism; Per the insurance policy document. |
| Ambient Air |  | means breathable air in area of work with specific reference to breathing zone, which is defined to be a virtual area within a radius of approximately 30cm from the nose inlet. |  |  |
| Compliance Monitoring |  | means compliance sampling used to assess whether or not the personal exposure of workers to regulated asbestos fibres is in compliance with the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles. |  |  |
| OEL |  | means occupational exposure limit. |  |  |
| Parallel Measurements |  | means measurements performed in parallel, yet separately, to existing measurements to verify validity of results. |  |  |
| Safe Levels |  | means airborne asbestos exposure levels conforming to the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles. |  |  |
| Standard |  | means the Employer’s Asbestos Standard 32-303: Requirements for Safe Processing, Handling, Storing, Disposal and Phase-out of Asbestos and Asbestos Containing Material, Equipment and Articles. |  |  |
| SANAS |  | means the South African National Accreditation System. |  |  |

# Annexure A:	 One-in-ten-year-return weather data obtained from SA Weather Bureau for [weather station]

If any one of these weather measurements recorded within a calendar month, before the Completion Date for the whole of the works and at the place stated in this Contract Data is shown to be more adverse than the amount stated below then the Contractor may notify a compensation event.

|  | Weather measurement |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Month | Cumulative rainfall (mm) | Number of days with rain more than 10mm | Number of days with min air temp < 0 deg.C | Number of days with snow lying at 08:00 CAT | [Other measurements if applicable] |
| January | [●] | [●] | [●] | [●] |  |
| February | [●] | [●] | [●] | [●] |  |
| March | [●] | [●] | [●] | [●] |  |
| April | [●] | [●] | [●] | [●] |  |
| May | [●] | [●] | [●] | [●] |  |
| June | [●] | [●] | [●] | [●] |  |
| July | [●] | [●] | [●] | [●] |  |
| August | [●] | [●] | [●] | [●] |  |
| September | [●] | [●] | [●] | [●] |  |
| October | [●] | [●] | [●] | [●] |  |
| November | [●] | [●] | [●] | [●] |  |
| December | [●] | [●] | [●] | [●] |  |

Only the difference between the more adverse recorded weather and the equivalent measurement given above is taken into account in assessing a compensation event.

C2.1 Pricing assumptions: Option B

# How work is priced and assessed for payment

Clause 11 in NEC3 Engineering and Construction Contract (ECC3) Option B states:

| Identified and defined terms | 11 11.2 | (21) The Bill of Quantities is the bill of quantities as changed in accordance with this contract to accommodate implemented compensation events and for accepted quotations for acceleration. |
| --- | --- | --- |
|  |  | (28) The Price for Work Done to Date is the total of the quantity of the work which the Contractor has completed for each item in the Bill of Quantities multiplied by the rate and a proportion of each lump sum which is the proportion of the work covered by the item which the Contractor has completed. Completed work is work without Defects which would either delay or be covered by immediately following work. |
|  |  | (31) The Prices are the lump sums and the amounts obtained by multiplying the rates by the quantities for the items in the Bill of Quantities. |

This confirms that Option B is a re-measurement contract and the bill comprises only items measured using quantities and rates or stated as lump sums.  Value related items are not used.  Time related items are items measured using rates where the rate is a unit of time.

# Function of the Bill of Quantities

Clause 55.1 in Option B states, “Information in the Bill of Quantities is not Works Information or Site Information”.  This confirms that specifications and descriptions of the work or any constraints on how it is to be done are not included in the Bill, but in the Works Information.  This is further confirmed by Clause 20.1 which states, “The Contractor Provides the Works in accordance with the Works Information”. Hence the Contractor does not Provide the Works in accordance with the Bill of Quantities.  The Bill of Quantities is only a pricing document.

# Guidance before pricing and measuring

Employers preparing tenders or contract documents, and tendering contractors are advised to consult the sections dealing with the bill of quantities in the NEC3 Engineering and Construction Contract Guidance Notes before preparing the bill of quantities or before entering rates and lump sums into the bill.

There is no general provision in Option B for payment for materials on Site before incorporation into the works.  If secondary Option X14 Advanced payment has not been used then the tendering contractor may obtain the same effect by inserting appropriate items in the method related charges where the method of measurement allows, or alternatively making allowance in the rates of the bill of quantities for the financing of Plant and Materials until they are incorporated in the works.

When compensation events arise, the default position is that the Bill of Quantities is not used to calculate the cost effect of the event.  Defined Cost and the resulting Fee is used and Defined Cost includes all components of cost which the Contractor is likely to incur, including so called P & G items.  Rates and lump sums from the Bill of Quantities, or from any other source, may be used instead of Defined Cost and the Fee only if the Contractor and Project Manager agree.  If they are unable to agree, then Defined Cost plus Fee is used.

# Measurement and payment

## Symbols

The units of measurement described in the Bill of Quantities are metric units abbreviated as follows:

[add or delete as required]

| Abbreviation | Unit |
| --- | --- |
| % | percent |
| H | hour |
| Ha | hectare |
| Kg | kilogram |
| Kl | kilolitre |
| Km | kilometre |
| km-pass | kilometre-pass |
| kPa | kilopascal |
| kW | kilowatt |
| L | litre |
| M | metre |
| Mm | millimetre |
| m2 | square metre |
| m2-pass | square metre pass |
| m3 | cubic metre |
| m3-km | cubic metre-kilometre |
| MN | meganewton |
| MN.m | meganewton-metre |
| MPa | megapascal |
| No. | number |
| Sum | Lump sum |
| T | tonne (1000kg) |

## General assumptions

### Unless otherwise stated, items are measured net in accordance with the drawings, and no allowance has been made in the quantities for waste.

### The Prices and rates stated for each item in the Bill of Quantities shall be treated as being fully inclusive of all work, risks, liabilities, obligations, overheads, profit and everything necessary as incurred or required by the Contractor in carrying out or providing that item.

### An item against which no Price is entered will be treated as covered by other Prices or rates in the bill of quantities.

### The quantities contained in the Bill of Quantities may not be final and do not necessarily represent the actual amount of work to be done.  The quantities of work assessed and certified for payment by the Project Manager at each assessment date will be used for determining payments due.

### The short descriptions of the items of payment given in the bill of quantities are only for the purposes of identifying the items.  Detail regarding the extent of the work entailed under each item is provided in the Works Information.

## Departures from the method of measurementOnly use this section if the statement for Option B in the Contract Data, “The method of measurement is ________ amended as follows” refers the reader to this section rather than include the amendments within the Contract Data statement.  Otherwise delete this heading.  In any case delete this note when complied with.

## Amplification of or assumptions about measurement items

The following is provided to assist in the interpretation of descriptions given in the method of measurement.  In the event of any ambiguity or inconsistency between the statements in the method of measurement and this section, the interpretation given in this section shall be used.

C2.2 the bill of quantities

Use this page as a summary page or as a cover page to the bill of quantities.

# Part 3: Scope of Work

| Document reference | Title | No of pages |
| --- | --- | --- |
|  | This cover page | 1 |
| C3.1 | Employer’s Works Information |  |
| C3.2 | Contractor’s Works Information (insert at award stage or delete if not applicable) |  |
|  | Total number of pages |  |

# C3.1: Employer’s works Information

Contents

# C3.1: Employer’s works Information

Contents

Part 3: Scope of Work	1

C3.1: Employer’s works Information	2

1	Description of the works	5

1.1	Executive overview	5

1.2	Employer’s objectives and purpose of the works	5

1.3	Interpretation and terminology	5

2	Management and start up.	7

2.1	Management meetings	7

2.2	Documentation control	7

2.3	Health and safety risk management	7

2.4	Environmental constraints and management	8

2.5	Quality assurance requirements	8

2.6	Programming constraints	9

2.7	Contractor’s management, supervision and key people	9

2.8	Invoicing and payment	9

2.9	Insurance provided by the Employer	10

2.10	Contract change management	10

2.11	Provision of bonds and guarantees	10

2.12	Records of Defined Cost, payments & assessments of compensation events to be kept by the Contractor	10

2.13	Training workshops and technology transfer	10

3	Engineering and the Contractor’s design	10

3.1	Employer’s design	10

3.2	Parts of the works which the Contractor is to design	23

3.3	Procedure for submission and acceptance of Contractor’s design	23

3.4	Other requirements of the Contractor’s design	25

3.5	Use of Contractor’s design	25

3.6	Design of Equipment	25

3.7	Equipment required to be included in the works	25

3.8	As-built drawings, operating manuals and maintenance schedules	25

4	Procurement	26

4.1	People	26

4.1.1	Minimum requirements of people employed on the Site	27

4.1.2	BBBEE and preferencing scheme	27

4.1.3	Accelerated Shared Growth Initiative – South Africa (ASGI-SA)	27

4.2	Subcontracting	27

4.2.1	Preferred subcontractors	27

4.2.2	Subcontract documentation, and assessment of subcontract tenders	27

4.2.3	Limitations on subcontracting	27

4.2.4	Attendance on subcontractors	28

4.3	Plant and Materials	28

4.3.1	Quality	28

4.3.2	Plant & Materials provided “free issue” by the Employer	29

4.3.3	Contractor’s procurement of Plant and Materials	29

4.3.4	Spares and consumables	29

4.4	Tests and inspections before delivery	29

4.5	Marking Plant and Materials outside the Working Areas	29

4.6	Contractor’s Equipment (including temporary works).	29

4.7	Cataloguing requirements	29

5	Construction	29

5.1	Temporary works, Site services & construction constraints	29

5.1.1	Employer’s Site entry and security control, permits, and Site regulations	30

5.1.2	Restrictions to access on Site, roads, walkways and barricades	30

5.1.3	People restrictions on Site; hours of work, conduct and records	30

5.1.4	Health and safety facilities on Site	30

5.1.5	Environmental controls, fauna & flora, dealing with objects of historical interest	30

5.1.6	Title to materials from demolition and excavation	30

5.1.7	Cooperating with and obtaining acceptance of Others	31

5.1.8	Publicity and progress photographs	31

5.1.9	Contractor’s Equipment	31

5.1.10	Equipment provided by the Employer	31

5.1.11	Site services and facilities	31

5.1.12	Facilities provided by the Contractor	31

5.1.13	Existing premises, inspection of adjoining properties and checking work of Others	31

5.1.14	Survey control and setting out of the works	31

5.1.15	Excavations and associated water control	32

5.1.16	Underground services, other existing services, cable and pipe trenches and covers	32

5.1.17	Control of noise, dust, water and waste	32

5.1.18	Sequences of construction or installation	32

5.1.19	Giving notice of work to be covered up	32

5.1.20	Hook ups to existing works	32

5.2	Completion, testing, commissioning and correction of Defects	32

5.2.1	Work to be done by the Completion Date	32

5.2.2	Use of the works before Completion has been certified	32

5.2.3	Materials facilities and samples for tests and inspections	33

5.2.4	Commissioning	33

5.2.5	Start-up procedures required to put the works into operation	33

5.2.6	Take over procedures	33

5.2.7	Access given by the Employer for correction of Defects	33

5.2.8	Performance tests after Completion	33

5.2.9	Training and technology transfer	33

5.2.10	Operational maintenance after Completion	33

5.2.11	Handover Requirements	33

5.3	Contractor Commitments Arising from Tender and Negotiations	32

6	Plant and Materials standards and workmanship	35

6.1	Investigation, survey and Site clearance	35

6.2	Building works	35

6.3	Civil engineering and structural works	35

6.4	Electrical & mechanical engineering works	35

6.5	Process control and IT works	35

6.6	Other [as required]	35

7	List of drawings	36

7.1	Drawings issued by the Employer	36

C3.2	Contractor’s Works Information	37

# Description of the Parliament executive suite works

# Tenant Installation for Parliament Executive Suite Overview

The scope of works for this package includes the engineering design, procurement and construction work as indicated in this document for Tenant Installation , construction of office and board rooms with drywall partitions where specified Fire Detection System (FDS), Public Address (PA) System, Electricity Metering, Environmental Monitoring, Fire Protection System (FPS), Heating, Ventilation and Air Conditioning (HVAC) System, Security System, Electrical and Auxiliary Power System, Architectural/Space Planning and General Interior Building, Safety, Accessibility, Branding and Informational Signage.

The Parliament Executive Suite will serve as a dedicated executive engagement facility aimed at improving collaboration between Eskom and Shareholder. Through the provision of secure meeting spaces, executive work areas, and enabling technologies, the facility will support the efficient management of shareholder engagements, improve responsiveness, and contribute to the timely execution of strategic and governance-related activities. This 8th Floor Executive Suite at Thibault Square Building is designed to accommodate:

- Group Chief Executive (GCE) and Chairman offices.

- General Managers offices.

- Executive Boardrooms.

- Large Multi-Use Space.

- Reception and Visitor Areas.

- Meeting Rooms.

- Information Technology (IT) Server Room.

- Kitchen and Tea Stations.

- Dining/Entertainment Facilities.

- VIP facilities.

- Accessible toilets that are friendly for the disabled and

- Support Amenities.

The executive suite layout is shown in Figure 1a and b below.

Figure 1a: 8th Floor Area.

Figure 1b: Proposed Parliament Executive Suite Floor Layout

This detail design report outlines the architectural and interior fit-out specifications for the Eskom Executive Suite located on 8th of floor of Thibault Square Building. The primary design objective for this phase is the creation of a high-performance, acoustically secure executive workspace that integrates seamlessly with the existing building infrastructure. Key achievements in this design iteration include the finalization of the spatial layout, the specification of high-density acoustic drywall systems to ensure executive privacy, and the coordination of interior finishes including Luxury Vinyl Plank (LVP) and heavy commercial carpet tiles over the existing raised access floors. Major technical integration points involve sealing the ceiling plenum barriers within the existing waffle slab.

A non-loadbearing interior architectural fit-out utilizing high-performance acoustic drywalls, specialized acoustic glazing, and coordinated floor/ceiling systems adapted to an existing raised-floor office environment.

# Existing offices at Thibault Square Building

# Architectural/Space planning

The existing 8th Floor office accommodation at Thibault Square, Cape Town, was designed for a previous tenant requirement and is not compliant with Eskom office space standard, Eskom's Universal Access Specification (240-157602340), access control & security standard, and the requirements of SANS 10400-S for persons with disabilities. The current layout consists of a mostly enclosed offices, meeting facilities, and a centrally positioned kitchen. The male and female ablution facilities are located on split levels between Floors 8 and 9, and Floors 7 and 8 respectively, resulting in accessibility constraints that require remediation as part of the proposed Parliament Executive Suite development.

Figure 2a: 8th floor Thibault Square as-built space planning layout.

The existing windows were provided with normal blinds and compensated with UV blinds as shown in the figure 2b below.

Figure 2b: 8th Floor Thibault Square Building window finishes

# EXISTING CONTROL AND INSTRUMENTATION SYSTEMS

The 8th Floor Executive Suite at Thibault Square Building currently does not Building Management. The active fire detection system is a Ziton ZP3 system.

The Thibault Square Building is currently equipped with a TOA Public Address system which is gradually being phased out by the equipment manufacturer and retrofitted with the SX2000 series which is backwards compatible with the installed series meaning that, if a migration route s followed, peripherals such as speakers, amplifiers etc. can be reutilised.

# EXISTING HEATING, VENTILATION AND AIR CONDITIONING (HVAC) SYSTEM:

The base system that forms the primary section of the air conditioning system is a chilled water system utilizing a combination of centrifugal and screw chillers at roof level. The chillers supply chilled water to a series of large air-handling plants at the roof the building. Refer to figure 3a below for the HVAC components and figure 3a for the HVAC during layout.

Figure 3a: HVAC components at the Thibault Square Building.

These air handling plants supply air directly into the ducts located in the building six cores.

Return air reaches these plants via the masonry riser ducts and is therefore a mixed return from all the levels served by the plant. There is a large concrete duct beneath the air handling plant rooms that brings fresh air into the plant.

The fresh air, supply air and return air volumes are controlled with a combination of dampers and variable speed fan drives.

This equipment will not be attended in any way as it is outside the terminal points of this project.

HVAC Reticulation System

This entails variable air volume system including supply air ducting, diffusers and control system. The design has variable volume diffusers for both the perimeter and the internal zones. The diffusers and the new room (space) temperature control system are electric / electronic.

Figure 3: 8th Floor Thibault Square Building HVAC ducting arrangement.

# EXISTING FIRE PROTECTION SYSTEM (FPS):

The 8th Floor Executive Suite at Thibault Square Building is equipped with Fire protection system comprising of automatic fire sprinklers, pipe risers, fire extinguishers, fire hydrants and fire hose reels fed from the existing building fire mains reticulation.

Figure 4a: Fire hose reel, fire signage and fire extinguisher.

The 8th Floor Executive Suite at Thibault Square Building is equipped with existing fire hydrants, hose reels, fire extinguishers and SABS approved photo luminescent symbolic fire signage. The passage had smoke detectors and fire alarm. Most the offices had fire sprinklers, but the smoke detectors were not provided for as depicted below in figure 5.

Figure 5: Sprinkler, smoke detector and fire alarm.

# EXISTING ELECTRICAL AND AUXILIARY POWER SYSTEM:

The existing electrical installation on the 8th floor is currently supplied by a 160A incoming feed. This supply provides power to the floor’s lighting and socket outlets, which are to be removed as part of the planned refurbishment. The floor also has established connections to both the building’s generator and the existing Uninterrupted Power Supply (UPS) system, which together provide partial backup capability for selected loads. The current UPS arrangement does not extend to full coverage of all electrical systems on the floor, meaning that only certain circuits benefit from backup power in the event of a supply interruption. The lighting and socket outlets are configured to suit the previous layout and therefore do not align with the new partitioning and space planning requirements.

In summary, the existing system comprises a 160A supply, partial 200 KVA generator and UPS backup, and a distribution network of lights and sockets that are no longer suitable for the revised design. This forms the baseline from which the new electrical design will be developed.

# Distribution Board

The 8th Floor Executive Suite at Thibault Square is supplied with a Distribution Board (DB) located on the roof named “DB8” rated at 160 A. The current DB is to be reused as a supply source to the proposed development.

Figure 5a: Floor 8 distribution board.

# Lighting

The existing lighting will be adapted for the proposed 8th floor layout and energy efficient lighting type will be used. This supply source is to be reused. Refer to Eskom 8th Floor Thibault Square Building Lighting Layout – Drawing no: Parliament office-10002- Rev 0.

# Small Power

Small Power is currently supplied from the roof distribution board. This supply source is to be reused. Refer to 8th Floor Thibault Square Building Small Power Layout – Drawing no: Parliament Office-10001- Rev 0.

# Existing power backup

The 8th Floor Executive Suite at Thibault Square Building is equipped with a power backup system that is rated at 186 kW as shown below. This caterpillar generator is located at the building roof in an enclosed area. Reliability statistics of the of the power backup generator could not be established but it was stated that it was about 40 years old and this generator was only able to provide partial backup.

Figure 6: Power Generator Nameplate.

# Existing eighth (8th) floor Closed-Circuit Television (CCTV) Surveillance, Access control system and Security system, Information and Cyber Security.

# Access control

The access control system was a manual system based on guards that are placed at the main entrance ground floor to manage the entry and exit of the personnel.  Every visitor had to sign the access register and declare his or her identity.

# Closed-Circuit Television (CCTV) Surveillance

The facility was provided with 24-hour CCTV and the command control centre was at the ground floor next to the lifts. Below in figure 7 is the typical command and control centre of the Thibault Square Building.

Figure 7: Power Generator Nameplate.

# Information and Cyber Security

The facility did not have Information and Cyber Security for the tenants.

# Management and start up.

# Management meetings

| Title and purpose | Approximate time & interval | Location | Attendance by: |
| --- | --- | --- | --- |
| Risk register | Weekly on _____ at ___ | Microsoft teams | Employer, Contractor |
| Progress report, reporting on actual work completed. | Weekly on _____ at ___ | Megawatt Park | Employer, Contractor, Supervisor, and ___ |
| Compensation events | When required | Megawatt Park | Employer, Contractor |
| Project Progress meetings | Weekly on _____ at ___ | Megawatt Park | Employer, Contractor |
| Overall contract progress | Weekly on _____ at ___ | Megawatt Park | Employer, Contractor |
| Look ahead schedule | Bi-weekly on _____ at ___ | Megawatt Park | Employer, Contractor |

Meetings of a specialist nature may be convened as specified elsewhere in this Works Information or if not so specified by persons and at times and locations to suit the Parties, the nature and the progress of the works.  Records of these meetings shall be submitted to the Project Manager by the person convening the meeting within five days of the meeting.

All meetings shall be recorded using minutes or a register prepared and circulated by the person who convened the meeting. Such minutes or register shall not be used for the purpose of confirming actions or instructions under the contract as these shall be done separately by the person identified in the conditions of contract to carry out such actions or instructions.

# Documentation control

All documents supplied by the Contractor are subject to Eskom’s acceptance. The language of all documentation is English.

The Contractor includes the Employer’s drawing number in the drawing title block. This requirement only applies to design drawings developed by the Contractor and Subcontractors.

Drawing numbers are assigned by the Employer as drawings are developed.

All review documentation is submitted with transmittals. Any review information submitted without transmittals are considered rejected automatically.

The Contractor complies a Master Document List (MDL) which contains a list of all documents issued for review, document number, document title, transmittal number, date of submission, overall document review status. The MDL is a live document, the contractor issues an updated MDL within the progress report to the Project Manager

# Health and safety risk management

The supplier/contractor/tenderer is expected to comply to the following documents when working at/rendering a service to Eskom but not limited to the following:

a. Occupational Health and Safety Act 85 of 1993 and its Regulations (OHS Act)

b. Disaster Management Act, no 57 of 2002.

c. Safety, Health and Environmental requirements contained in the SHE Specification for Contractors.

d. Eskom SHEQ Policy, Standards, Procedures, Guidelines, Specifications and Regulations as listed below:

i. Eskom Safety, Health, Environmental and Quality Policy: 32-727

ii. Eskom Lifesaving Rules, Directive: 32-421

iii. Eskom Procedure on Smoking: 32-36

iv. Eskom Incident Management Procedure 32-95 (latest revision)

v. Implementation of Occupational Hygiene management programme, Standard 240-42262670

vi. Eskom Life Saving Rules, Directive: 240- 62196227

vii. Eskom vehicle and driver safety management 32-93

viii. Eskom vehicle specification 32-345

ix. Eskom Contractor Health and Safety requirements standards 32-136

x. Employees’ right of refusal to work in an unsafe situation 240-43848327

xi. Eskom Waste Management Standard 32-245

xii. Annexure B: Acknowledgement Form for Eskom SHE Rules and other Requirements

The Contractor requests all applicable Eskom procedures & requirements. The Contractor ensures safety awareness at all times through continuous training. The Contractor, at all times is responsible for the supervision of his employees, agents, Subcontractors and takes full responsibility and accountability for ensuring they are competent, compliant and aware of the legal requirements and other requirements and execute the works accordingly.

The Contractor ensures that all statutory appointments and appointments required by any Eskom Regulations are made in writing and that all appointees fully understand their responsibilities and are trained and competent to execute their duties.

The Divisional/Regional Safety Risk Manager or his representative having jurisdiction over the works must provide the relevant safety, health and environmental (SHE) criteria for incorporation into this Works Information. The SHE specification / scope must be signed off by the Divisional/Regional Safety Risk Manager or his representative confirming that the applicable safety criteria have been considered.

The Commodity Manager / Buyer must refer the tender to the Divisional/Regional Safety Risk Manager or his representative in order to evaluate against enquiry-specific safety criteria.

The Divisional Safety Risk Managers who will be responsible for the allocation of resources to assist P&SCM with the above processes are as follows:

- Generation: Roley McIntyre

- Transmission: Tony Patterson

- Distribution: Alex Stramrood

- Enterprises: Jace Naidoo

- Corporate: Kerseri Pather

The Contractor shall comply with the health and safety requirements.

# Environmental constraints and management

All waste introduced and/or produced on the Employer’s premises by the Contractor for this contract is handled in accordance with the minimum requirements for the Handling and Disposal of Hazardous Waste in terms of Government Legislation as proclaimed by the Department of Water Affairs and Forestry and Employer’s environmental requirements.

All environmental incidents are reported to the Employer within 24 hours of such occurrence. All environmental incidents occurring on the Project Site (or on any other places, if any, as may be specified under the Contract as forming part of the Site) are recorded, detailing how each incident was dealt with in an Environmental Incident register.

The Contractor shall construct and/or implement all the necessary environmental protection measures in each area before any production work will be allowed to proceed. The Employer may suspend the Works at any time in terms the Conditions of Contract should the Contractor, in the Employer’s opinion, fail to implement, operate or maintain any of the environmental protection measures adequately.

The Contractor ensures that all goods, services or works supplied in terms of the Contract comply with all applicable environmental legislations (National Environmental Management Act, 1998 [Act No 107 of 1998]). The Contractor is responsible for keeping the work area clean of any environmental waste.

The Contractor shall comply with all relevant applicable laws, environmental legislation and regulations, conditions of environmental approvals, environmental management plans, and Employers Policies and Procedures. The Contractor must submit an Environmental Policy demonstrating commitment to protection of the environment. The Environmental Policy shall form part of the SHE file submission. Upon the Employer’s approval, the Contractor shall immediately implement the policy and any amendments and keep it in operation for the full duration of the Contract. The policy shall be communicated to all personnel and copies of the policy shall be prominently displayed at all places of work.

The Contractor shall determine and develop the aspects and impacts register related to the scope of work. All aspects of the planning, manufacturing, pre-construction, construction and operational phases shall be considered. During the designing activity, the Contractor must always take into account the product’s life cycle perspective in mind.

The Contractor shall comply with the environmental criteria and constraints.

# Quality assurance requirements

The Contractor complies to the following documents when working at/rendering a service to Eskom but not limited to the following:

i. 240-12248652 - List of Tender Returnable/Quality Requirement Document

ii. 240-68099512 - FORM A: Tender & Contract Quality Requirements for QM 58 and Quality Requirements for ISO 9001 Standard

iii. 240-105658000 (QM 58)- Supplier Quality Management: Specification

iv. 240-109253698- Contract Quality Plan (CQP)

v. 240-109253302- Quality Control Plan (QCP)/ Inspection and Test Plan (ITP)

After the acceptance of the construction drawings the contractor submits the associated construction Method Statements and relevant QCP/ITP for acceptance and determination of intervention points prior to construction.

Failure to comply with an accepted Method Statement/QCP or ITP may result the issuing of a Non-conformance report (NCR), rejection of the works as well as the withholding of payment until the appropriate remedial actions have occurred.

- The Contractor demonstrates, provide, and maintains a Quality Management System that is ISO 9001:2008 certified or compliant thereto. Compliance with the provisions of this clause in no way relieves the Contractor of the final responsibility to furnish an acceptable product and/or services.

- The Contractor agrees to control and professionally preserve and store appropriate documents, records, and recordings for a period of at least 3 years after termination of the agreement to guarantee the traceability of the services rendered and inspection thereof.

- The Contractor agrees to regularly update and implement all the latest technology available as well as the necessary improvements for the installation, production and organisation deemed necessary to meet the requirements of the agreement and in order to enhance all system capabilities and effectiveness to deliver high quality, cost-effective services.

- The delivered product and / or services shall be uniform in Quality and condition, sound and free from defects or external copyright or intellectual property rights, consistent with good industry practices and adhere to requested Eskom requirements, without deviation.

- Eskom shall have the right to conduct surveys and perform surveillance of the Contractor’s and/or Sub-Contractor facilities to evaluate their capability to comply with the requirements necessary to conform to contractual requirements.

- Eskom reserves the right to inspect, at reasonable times, any or all of the work included in the Works Information at the Contractor’s or Sub-Contractor’s premises or elsewhere. Verification by Eskom shall not absolve the Contractor of the responsibility to provide acceptable product and / or services, nor shall it preclude subsequent rejection by Eskom.

- The services must comply with the agreed specifications and the applicable directives and technical standards set out in the contract and annexures. Defects notified by Eskom shall be remedied by the Contractor upon demand by Eskom without undue delay and at no extra cost. The Contractor shall continuously monitor and identify non-conformances, both internal and external, as signals of opportunities for improvement making process and other relevant changes to prevent recurrence.

- The Contractor shall further identify potential problems before they occur by identifying deviations in patterns or trends in product, service or process performance.

- Nothing contained in the contract and/or scope of work and /or Works information shall relieve in any way the Contractor from the obligation of quality control thereof.

- The Contractor guarantees that the quantity, quality and outward appearance of the delivered Product / services comply with the requirements of the contract and/or relevant specifications.

- The Contractor shall, on request, prove its ability to relate to the proposed scope of work which establishes the manner in which the Contractor intends to perform the Contract.

- The Contractor shall, on request, prove its organisational, logistics and support resources to ensure the requirements of the contract can and will be achieved.

- Eskom reserves the right to assess and measure, during the existence of the agreement, the qualifications, capability and competence of the key staff (assigned personnel) in relation to the scope of work and to interview any / all Contractors to confirm the Quality evaluation.

- The professional personnel who will be conducting the service will be available on a continuous basis until the conclusion of the project.

- The Contractor shall demonstrate experience in comparable projects or specific aspects of the project and / or performance in similar projects, on request.

- The Quality of the service / product and the contents thereof will always be in accordance with professional standards.

- For the duration of the Contract, the professional staff rendering the service / product, must be and remain a member of his/her Professional Society (where available/applicable)

- The Contractor must, at all relevant times, scrutinise and be aware of Eskom’s requirements with specific focus on, inter alia, its philosophy, principles, strategies, practises, mission, vision, models, policies and practises.

- It is the Contractor’s obligation to ensure that their operations and the products and services it provides to Eskom comply with any applicable statutes and or regulations. Any non-compliance by the Contractor and the resultant corrective actions shall be the responsibility of the Contractor.

- The Contractor shall ensure that he complies with the Works Information and that appropriate quality requirements (as in the main contract) are included in subcontracts placed by Contractors to ensure subcontractor’s compliance with the Works Information.

- The Contractor shall execute the Works in accordance with Eskom’s Quality requirements set out in QM 58 document: Supplier Contract Quality Requirements Specification.

# Programming constraints

A programme showing the key activities is to be submitted with the tender documents and once appointed within two weeks. The Contractor submits a single integrated programme that incorporates all the work to be performed including that of his Subcontractors.

The interfaces between Subcontractors as well as the interfaces between Subcontractors and the Contractor are clearly identified.

Project key dates are incorporated into the programme.

All critical path items are indicated and outlined on the programme.

The order and timing of operations which the Contractor plans in order to provide the Works. Strict adherence to the programme will be monitored and updated on fortnightly basis to achieve the completion dates and submitted to Eskom Project Co-ordinator. Non-conformance to the stated programme will be liable for delay damages. Any deviations on time and cost are subject to Eskom approval.

The Contractor provides the Project Programme in Microsoft Projects Format to the level 3 detail. The programme is to be updated weekly and submitted to the Project Manager for review.

# Contractor’s management, supervision and key people

The Contractor provides the Employer with a detailed organogram of all staff and management on the contract, showing their lines of authority / communication, within two weeks of contract award. This is revised monthly and reflects any changes to the staff and management structure. The Employer reserves the right to audit and verify the structure. The Contractor has a full-time Safety and Health Officers onsite.

Roles and responsibilities shall be as per the Employer’s design review procedure 240-53113685.

Contracts Manager:

The contracts manager is responsible to incorporate this Technical Specification into a contract based on the NEC conditions of contract.

Architectural Practitioner:

The Architectural Practitioners are responsible to review the completed contract to ensure that this Technical Specification has been incorporated correctly.

Project Manager:

The project manager is responsible for facilitating and ensuring continuous coordination and management of the requirements during the design development, execution phase and closing out of the project.

Facilities Manager:

The facilities manager is responsible for ensuring continuous sustainable performance of facilities. During construction phase he/she ensures that there are smooth interactions with tenants and stakeholders where required.

Contractor:

The Contractor's responsibility is to build the project according to the contract documentation within the required cost and time budgets and the specified standards.

The Contractor will play the role of the design authority ensuring the following:

- The design satisfies the design requirements.

- All relevant Eskom design standards, procedures and guidelines have been adhered to.

- The design is suitable and correct calculations, philosophy, functionality, etc. have been applied.

- The design is integrated by identifying all interfaces with other packages/plant systems/assets and ensuring that these interfaces are catered for.

Eskom Engineering

Eskom Engineering will play the role of architect engineer and ensure that:

- The design satisfies the stakeholder requirements (i.e., validation of design deliverables against stakeholder requirements).

- The design is integrated by identifying all interfaces with other packages/plant systems/ assets and ensuring that these interfaces are catered for.

- Foreseen technical risks are identified and addressed/challenged with the Design Authority

- General technical oversight is provided over the design.

# Invoicing and payment

Within one week of receiving a payment certificate from the Project Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice showing the amount due for payment equal to that stated in the Project Manager’s payment certificate.

The Contractor shall address the tax invoice to Eskom Holdings SOC Ltd and include on each invoice the following information:

- Name and address of the Contractor and the Project Manager;

- The contract number and title;

- Contractor’s VAT registration number;

- The Employer’s VAT registration number 4740101508;

- Description of service provided for each item invoiced based on the Price List;

- Total amount invoiced excluding VAT, the VAT and the invoiced amount including VAT;

- (add other as required)

Add procedures for invoice submission and payment (e. g. electronic payment instructions)

# Insurance provided by the Employer

The Contractor familiarises themselves with the Eskom Insurance Format A as provided in the Contract Data and make provision for all items that they are liable for.

# Contract change management

The Employer instructs changes to the scope at any time, each instruction sets out the change and the date on which it becomes effective; and is issued to the Contractor in writing to be valid.

# Provision of bonds and guarantees

The form in which a bond or guarantee required by the conditions of contract (if any) is to be provided by the Contractor is given in Part 1 Agreements and Contract Data, document C1.3, Sureties.

The Employer may withhold payment of amounts due to the Contractor until the bond or guarantee required in terms of this contract has been received and accepted by the person notified to the Contractor by the Project Manager to receive and accept such bond or guarantee.  Such withholding of payment due to the Contractor does not affect the Employer’s right to termination stated in this contract.

# Records of Defined Cost, payments & assessments of compensation events to be kept by the Contractor

      - The Contractor to keep accurate and detailed records of:

- Defined Cost – the actual costs the Contractor incurs (e.g. People, Equipment, Materials, Subcontractors)

- Payments received – for completed work or milestones

- Compensation events – including supporting evidence of time and cost impacts

# Training workshops and technology transfer

After Completion of the contract, the Contractor is required to provide training and transfer system knowledge to the building owner/manager by submitting documented Design Intent, As-built drawings, Operational and Maintenance Manual, Commissioning Records, Commissioning Report and by providing training on all the systems to the building management staff to ensure that they have all the information and understanding needed to operate and maintain the features and systems in the building.

The Contractor is to provide on-site training and training material to the Engineers, Operators and Maintenance personnel prior to taking-over of the Works. The training will preferable be offered during the commissioning and testing. The Contractor will, prior to handing over of the Works, satisfy the Employer or authorized representative that maintenance and operational personnel are competent and adequately trained to maintain and operate the Plant and Materials supplied.

The training is to cover the following, however not limited to:

a. Information provided in the design intent report (including energy/environmental features)

b. Review of controls set up, programming, alarms and troubleshooting

c. Review of Operation & Maintenance manuals

d. Building operation (start up, normal operation, unoccupied operation, seasonal changeover, shutdown)

e. Measures that can be taken to optimise energy efficiency

f. Occupational health and safety (OH&S) issues

g. Maintenance requirements and sourcing replacements

h. Obtaining and addressing occupant satisfaction feedback Steps for Conducting On site Training are to include, but not limited to:

          - Preparation

          - Introduction

          - Explanation

          - Demonstration

          - Practice Under Supervision

          - Conclusion

The operating and maintenance manual must be available during the training of site staff. Site staff must also be made familiar with the contents of that manual.

# Engineering and the Contractor’s Design

# Employer’s design

# ARCHITECTURAL/SPACE PLANNING DESIGN

The project entails the demolition of existing and modernisation of the entire 8th Floor to accommodate Executives and Support Staff. The works include full architectural and space-planning upgrades to all internal building elements. This involves redesigning the entire floor, consisting of Executive Offices; Support Staff Workstations and Office spaces; Meeting rooms, and Support areas. All existing finishes within the whole Floor to be removed and replaced with new flooring, walls, and ceiling systems throughout the floor and link structures.

Meeting Rooms; Printer Room; and Storerooms will be strategically located adjacent to service cores for improved efficiency. All existing dry walls will be demolished and re-established within the link areas to enhance accessibility and user experience. New Ablution facilities will be added closer to the Reception Area to allow easy access, to meet current standards.

# Overview of the Floor Layout

New Concept design drawings below have been completed for 8th Floor Eskom Executive Suite at Thibault Square Building, in line with SANS and Eskom Standards. The design is envisioned to embody a cohesive, modern, and efficient design language that reflects international best practice for the Executive Offices of a large state-owned enterprise.

The extent of the works includes demolition, construction of permanent fixtures and finishing of permanent fixtures to the following areas:

- All dry walls; flooring and ceilings to be replaced.

- New additional ablution facilities to be added.

- Upgrade security and access control.

- Add new meeting areas, workspaces and supporting spaces

- Add new storage areas.

The floor to accommodate:

- Eskom Executives and their Support Staff

Eskom employs very specific standards and guidelines regarding corporate image, interior design and space planning. The floor plates are planned with a very specific zoning in place resulting in the following:

- Open plan work areas on the perimeters; Closed spaces (i.e. offices, meeting rooms, print rooms, storerooms) positioned around the central core, as shown in the new Floor Layout.

- The resulting benefits of this planning include:

- Maximisation and better use of natural light as it can penetrate further into the office space

Figure 8: Proposed 8th floor Eskom Executive Layout at Thibault Square.

# DEMOLITION OF 8TH FLOOR PARTITION WALLS AND FINISHES

The Contractor provides a solution for the demolition of the existing 8th floor offices at the Thibault Square Building in line with the requirements of the technical specification. Demolition solutions are developed by a competent person up to a detailed design level, in accordance with section 14 of the Construction Regulations. Refer to Figure 9 for the demolition drawing layout.

- Remove all existing dry walls, partitioning and other fixtures as per Demolition Drawings

- Remove all ceiling boards and suspension structures

- Remove all services as required, as per the drawings.

- Remove all demolished materials and dispose of them in an accepted and proper way with minor disturbance of office staff working within other Floors of the building.

- Care to be taken not to damage any materials or portion of the building that remains for re-use on completion.

Figure 9: Demolition of the existing offices at the 8th Floor Thibault Square offices infrastructure.

          - Partitions

The Contractor shall demolish and remove all non-load-bearing internal partition walls indicated on the demolition drawings shown above, including:

- Existing drywall partitions.

- Gypsum board partitions.

- Glazed partition systems and associated framing.

- Associated doors, ironmongery, door frames and sidelights.

- Skirting, architraves and wall finishes attached to demolished partitions.

Based on the drawing, the majority of the existing office cellular layout identified by the red dashed demolition lines is to be removed to create an open-plan workspace and facilitate the new space planning arrangement. Existing core structural walls surrounding lifts, staircases and service shafts shall remain.

          - Ceilings

The Contractor shall demolish and remove:

- Existing suspended ceiling tiles.

- Ceiling grid systems.

- Suspension hangers and support channels.

- Bulkheads identified for removal.

- Existing access panels.

- Associated ceiling finishes and trims.

The extent of demolition shall cover the entire refurbishment area to allow installation of new ceiling systems, lighting layouts, air distribution systems and other building services.

          - Electrical Wiring and Services

Prior to demolition, all electrical services shall be isolated by authorized personnel.

The Contractor shall demolish and remove:

- Existing lighting fittings identified for demolition.

- Electrical wiring and cabling associated with removed areas.

- Conduits and trunking rendered redundant by the new layout.

- Power outlets and socket outlets.

- Floor boxes and recessed floor boxes.

- Data points, VGA points and communication outlets.

- Power skirting systems.

- Distribution boards identified for replacement.

- Associated containment systems and supports.

The red and blue service symbols displayed on the demolition layout indicate extensive removal of electrical points, floor boxes, data outlets and lighting installations throughout the floor.

          - Flooring

The Contractor shall remove and dispose of:

- Existing carpet tiles.

- Carpet sheeting.

- Raised access flooring systems.

- Existing floor screeds where required.

- Ceramic floor tiles identified for replacement.

- Adhesives and floor preparation materials.

Following demolition:

- All floor penetrations shall be repaired.

- Existing floor box openings shall be made good.

- Floors shall be re-screeded and levelled using approved self-levelling compounds.

- All damaged walls shall be repaired.

- All damaged fire protection systems shall be repaired.

- All damaged central air-conditioning system (HVAC) shall be repaired.

- Surfaces shall be prepared for installation of new floor finishes.

          - Extent of Demolition

The demolition works shall comprise the complete strip-out of existing architectural, electrical and floor finish elements within the designated refurbishment area, including:

- Cellular office partitions.

- Suspended ceiling system.

- Lighting installations.

- Power and data reticulation.

- Floor finishes and floor service outlets.

The intended outcome is to provide a clean, unobstructed shell suitable for the installation of the new architectural layout, HVAC systems (Diffusers and split units), electrical reticulation, ICT infrastructure, building monitoring instruments and associated building services.

The Contractor shall provide a Quality Control Plan (QCP) indicating Architectural/Space Planning and Demolition hold points are enforced to ensure full compliance with applicable standards.

# Thibault Square 8th Floor Executive Suite Finishes

          - Flooring

- Remove all existing floor finishes.

- Make good of the entire floor.

- Refill and make good all electrical outlets in floors.

- Re-screed all floors with accepted self-levelling compound

- Install products strictly to manufacturer’s specifications.

Refer to Drawing list for floor finishes.

          - Services First Fix

- Install all required services in ceiling voids.

- The Architects drawings are to be read in conjunction with the BoQ.

- Complete First Fix of:

  - Electrical

  - Fire protection

  - HVAC

  - Control & Instrumentation

          - Services Second Fix

Install all services in ceiling void to complete for final fittings on completion of ceiling insulation / installation.

          - Partitioning

- All partitioning is installed after complete floor finishes are laid.

- Install partitioning Light Steel Frame (LSF) wall system in configuration with ceiling grid system, strictly in accordance with manufacturer’s specifications.

- Install all services as required into partitioning walls prior to installation of double boarding system as accepted.

- Install sound dampening materials as accepted and strictly to manufacturers specification.

- Install new frameless glass double doors.

- Install new full-height glass and timber doors in closed office spaces.

- Install black anodised frames.

- The Architects Drawings are to be read in conjunction with the Bill of Quantities (BoQ).

Refer to Partitioning Layout Drawings.

# Ceiling Tiles and Plasterboard

- Install 1200mm x 600mm accepted acoustic ceiling tiles in grid system, strictly in accordance with manufacturer’s details and specifications. (CF-1),

- Install 600mm x 600mm accepted acoustic ceiling tiles in grid system strictly in accordance with manufacturer’s details and specifications. (CF-2),

- Install 9.5mm plasterboard suspended ceilings, strictly in accordance with manufacturer’s specifications

- Install 9.5mm flush plasterboard bulkheads strictly in accordance with manufacturer’s specifications. (CF-3),

- Install new flush plaster ceiling with shadow line detail.

- Install custom bulkheads suspended on exposed slab.

- Install new LED strip lights in bulkheads.

- Install suspended designer pendants.

- The Architect’s Drawings are to be read in conjunction with the BoQ,

See Ceiling Layout drawing for ceiling material details, refer to drawings list

# Specialised Fittings and Installation

Approved specialists to design and install their own equipment during the building process:

- Specialised furniture in Entrance and Executive Areas

- Access Control and Fire Equipment,

- Safe Doors and Security Equipment are installed by the Employers subcontractor as indicated on drawings),

- High Energy Absorbing Material,

- Specialised protective film on glass as specified,

- Seamless flooring,

- Meeting Rooms: - 1200mm high white filmed glass writing boards & TV screens recessed into walls, where possible.

# Internal Façade

- The internal façades will be an interplay of new dry walls; new frameless glass and aluminium shopfronts installed in the entire floor.

- The only access to this floor plates will be through access-controlled doors.

- These internal facades will also feature actuator-controlled smoke vents.

# Workspace Screens

# Wall and floors - finishes

- Install tiled/ painted glass splashbacks in kitchen.

- Install ceramic wall tiles in the toilets.

- Plaster skim and paint new walls.

- Install customer specified printed vinyl to glass partitions.

- Install faggot wall cladding on some columns.

- Install new epoxy flooring in designated areas.

- Install acoustic decorative panels.

- Install new timber flooring in specified areas.

# Window Coverings

- Install new motorised roller blinds. Refer to figure 10 below for details.

- Install new wooden venetian blinds.

- Install Veneer, Duco, Stone, Glass, Solid wood coverings as per design.

- Install heavy commercial acoustic curtains.

WOOD FURNITURE

`

Figure 10: Window coverings.

# Furniture Specification

- Workspace furniture, desks, chairs and cabinets are placed as per furniture layouts

- Loose furniture supplied by the Employer.

Refer to furniture layout drawings.

# Universal Access

The design for all the entire floor meets the latest standards regarding Universal Access.

# CONTROL AND INSTRUMENTATION DESIGN

The scope for 8th Floor Executive Suite at Thibault Square Building includes the Fire Detection System (FDS), Public Address and Voice Evacuation System, Physical Security System, Access Control System, Closed-Circuit Television (CCTV) Surveillance and Boardroom Audio Visual System.

The Contractor provides preliminary designs by registered engineers to the Engineering Lead and Project Manager for acceptance. These would have to be reviewed with possible amendments having to be made to comply with Eskom requirements. Adequate time is allowed for this. After acceptance of preliminary designs, the Contractor provides detailed designs.

The scope of works includes the detail design, drawings, procurement, manufacture, fabrication, quality control, supply, delivery, installation, commissioning, testing, handing over, training and maintenance during the guarantee period of all materials and equipment necessary for a complete works.

By virtue of the Department of Employment and Labour (DEOL) mandate to the South African Qualifications and Certification Committee (SAQCC), any person designing, installing, commissioning or maintaining Fire Detection System needs to be certified by SAQCC at the appropriate level.

The Contractor provides proof of valid certification as part of the tender returnable. In the absence of the main Contractor’s personnel being certified he/she can submit an agreement with a certified sub-contractor to perform the duties that require certification. In this case, proof of certification of sub-contractor and formal agreement shall be supplied.

The descriptions below cover 8th Floor Executive Suite at Thibault Square Building but, it goes without saying that for full compliance of the entire 8th floor must be serviced and therefore form part of the scope of this contract.

# Fire Detection and GAS Suppression Detection Systems

The primary purpose of the Fire Detection and GAS Suppression Detection Systems is to provide early fire warning and to notify the building occupants and the 1st responder at the Main Control Room in case of a fire event.

The secondary purpose of the Fire Detection and GAS Suppression Detection Systems is to provide a fire alarm signal to 3rd party systems such as HVAC, fire dampers, smoke extraction systems, etc. required to initiate the necessary safety functions in the event of a fire. These 3rd party interfaces are identified during the assessment and built into the Contractor’s design.

Smoke / Heat Detection

With the installation of partitions, some of the rooms/offices are now not fully covered by smoke detectors. Also, some of the existing detectors are situated closer to the partitioning walls than what is allowed by SANS standards. At the junction of a wall and a ceiling, there is a "dead space", within which heat or smoke detection would not be adequately effective. For this reason, heat and smoke detectors should not be mounted within 500 mm of any walls, partitions or obstructions.

Manual Call Points

With the change in occupation from open plan to closed offices together with a new access controlled entrance/exit point, the positioning of manual call points does not meet the SANS standards stating that manual call points need to be distributed such that, from any point in the building, it is impossible to leave the storey or the building without passing a manual call point.

Sounders / Strobes

Previously, with the open space occupancy, the sound levels of the exiting sounders could freely travel to all corners of the floor. With the introduction of lockable offices this may not be the case anymore. Sound levels will have to be tested to ensure compliance with SANS 10139 stating that the sound levels at any given point should not be less than 65 dB. It is also recommended to add visual alarms for the hearing impaired.

Because the floor layout and orientation are being changed from the current layout, all fire detection devices such as detectors, sounders and manual call points must be redesigned to ensure compliance.

- There is an existing Ziton ZP 3 fire alarm panel servicing this floor.

- The Contractor designs and install a fire detection system for this floor that is compliant with the National Building Regulations and SANS 10139. This includes the Control and Indicating Equipment (CIE), power supply equipment, communication networks, detectors, alarm devices, cabling and 3rd party system interfaces.

- The Contractor ensures that this fire panel s interfaced with the existing network and configures the system to have the alarms initiated at the 8th Floor Executive Suite at Thibault Square Building main control room master panel.

The Fire Detection and Alarm contractor shall assess the existing building fire detection and alarm system and develop a detailed design for the 8th Floor refurbishment. The design shall comply with the latest editions of SANS 10139, ISO 7240, SANS 10400-T, and all other applicable legislation and Employer standards. The scope shall include verification of the existing fire alarm infrastructure, loop capacity, network topology, and available panel capacity to accommodate the additional field devices.

The contractor shall design, supply, install, test and commission a complete fire detection and alarm system for the refurbished floor, including but not limited to smoke detectors, heat detectors where applicable, manual call points, sounders, sounder-beacons, interface modules, detector bases, loop wiring, containment, and associated accessories. Detector selection shall be based on the occupancy classification and environmental conditions of each space.

The fire alarm system shall be fully integrated with the existing building fire alarm control panel and network, ensuring that all alarms, faults, supervisory conditions, and device status are reported at the building's main fire alarm control panel and any central monitoring station. Cause-and-effect programming shall be updated to include the refurbished floor, ensuring that alarm initiation results in the correct operation of sounders, visual alarms, HVAC shutdown, smoke control systems, access control release, lift interfaces and other fire engineering functions where applicable.

The contractor shall prepare fire alarm layouts, loop drawings, cause-and-effect matrices, cable schedules, equipment schedules, testing and commissioning procedures, operation and maintenance manuals, and as-built documentation. The scope shall include factory acceptance testing (where applicable), site acceptance testing, integrated system testing, commissioning, and user training.

The assessment done by the Contractor is done with compliance in mind and must identify and resolve all areas of no-compliance.

# 8th Floor Executive Suite at Thibault Square Building Public Address and Voice Evacuation System

The main function of the Public Address and Voice Evacuation System is to ensure effective communication to all employees, contractors and visitors during emergency evacuation. The system shall be primarily used to provide clear one-way voice communication and audio alarm tones during an emergency to affect a rapid and orderly evacuation of everyone in response to the emergency.

With the installation of partitions, some of the rooms/offices are now not covered by public address system speakers.

- The Contractor performs an assessment of the 8th Floor Executive Suite at Thibault Square Building Public Address and Voice Evacuation System and speakers pertaining to coverage and then designs a new layout and install additional speakers to cover the new layout.

- The assessment by the Contractor is done with compliance in mind and must identify and resolve all areas of no-compliance.

The Public Address (PA) and Voice Evacuation contractor shall assess the existing building PA/Voice Alarm system and develop a detailed design for the 8th Floor refurbishment. The design shall comply with the applicable requirements of ISO 7240-16, EN 54-16, SANS 10139, and other relevant standards governing emergency voice communication systems.

The scope shall include the design, supply, installation, testing and commissioning of ceiling speakers, wall speakers where required, speaker circuits, speaker line monitoring, attenuators where applicable, amplifier capacity verification, zone allocation and associated cabling.

The contractor shall verify the capacity of the existing PA/Voice Alarm equipment, including controllers, amplifiers, battery systems and network infrastructure, and upgrade these where necessary to accommodate the additional speaker circuits.

The refurbished floor shall be fully integrated into the building's existing PA and Voice Evacuation System to enable emergency evacuation announcements and routine testing of the system. Speaker coverage shall be designed to achieve the required speech intelligibility throughout all occupied areas including reception areas, passages, meeting rooms, boardrooms, offices, exhibition spaces, kitchens and support areas.

# Closed-circuit television (CCTV)system

The Security and Access Control contractor shall assess the existing building security infrastructure and prepare a detailed design for the refurbished 8th Floor in accordance with the Employer's security requirements and applicable industry standards.

The scope shall include the design, supply, installation, testing and commissioning of smart access control systems, including access control panels, intelligent door controllers, card readers, biometric readers where required, electromagnetic locks, electric strikes, request-to-exit devices, emergency break-glass units, door contacts, locking hardware, power supplies and associated cabling.

Access control shall be provided for the main office entrance, executive offices where required, IT/server room, communication rooms, security-sensitive areas and other locations identified by the Employer.

The system shall be fully integrated with the floor Access Control Management System, ensuring central monitoring, alarm reporting, cardholder management and event logging.

The scope shall further include CCTV coordination, interface with the fire alarm system for emergency door release, integration with visitor management where applicable, testing, commissioning, operation and maintenance manuals, system administration training and as-built documentation.

# Boardroom Audio Visual System

The Audio Visual (AV) Contractor shall design a modern integrated boardroom communication system suitable for executive meetings, presentations and hybrid collaboration.

The scope shall include the design, supply, installation, programming, testing and commissioning of a fully integrated Audio-Visual solution comprising:

•	High-definition display screens or laser display systems.

•	Video conferencing equipment (Microsoft Teams and Zoom compatible).

•	PTZ conference cameras.

•	Ceiling or table microphones.

•	Digital signal processors (DSPs).

•	Wireless presentation systems.

•	HDMI, USB-C and wireless content sharing.

•	Audio amplifiers.

•	Ceiling or wall-mounted loudspeakers.

•	Touch-screen room control panels.

•	Equipment racks.

•	AV switching equipment.

•	Cable management systems.

•	Digital room scheduling panels where required.

The AV system shall provide high-quality audio reproduction, speech reinforcement, echo cancellation, automatic camera tracking where required, wireless presentation capability and seamless integration with corporate communication platforms.

The Engineer shall coordinate the installation with the architectural reflected ceiling plan, furniture layouts, lighting, HVAC, ICT and electrical services to ensure optimum equipment positioning and user experience.

The scope shall include network integration, configuration, programming, functional testing, user acceptance testing, commissioning, end-user training, operation and maintenance manuals, equipment schedules, rack layouts, single-line diagrams and as-built documentation.

The Contractor shall provide a Quality Control Plan (QCP) indicating Control & Instrumentation hold points are enforced to ensure full compliance with applicable standards

# HVAC DESIGN

# Terminal Points

The terminal point interface with existing HVAC services will be at the existing duct risers currently serving parliament office park eighth floor.

# Scope of work Summary

This includes for the existing, supply, co-ordination, fabrication, delivery, installation, painting, testing, commissioning and handing over in complete working order a new HVAC system, ducting, diffusers, controllers of parliament office park eighth floor in Cape Town.

- The works covered under this section includes the installation of:

- Supply and installation of new Variable air volume diffusers and Return air grilles for partitioned offices.

- Upgrade HVAC and Supply and install new space controllers and supply additional controllers to the partitioned offices.

- Supply and installation of two direct expansion (Dx) Under ceiling units for IT / Server Room.

- Mechanical Ventilation – Toilet ventilation

- Supply and install (if required) metal sheet and flexible ducting in accordance with provided Construction HVAC Layout.

- Each section is discussed in detail within the document.

# Contractor's Drawing, Equipment Selection and Sample Submissions

The contractor shall select material, submit selected materials for approval to the employer, submit shop drawing to the employer for approval, the contractor shall submit method statements, quality control documents to the employer for approval prior construction, the contractor shall construct, test balance and commission the units and hand it over to the employer, the contactor shall decommission existing plant in preparation to install new plant.

# Variable Air Volume Diffusers and Return air grilles

The Contractor to supply and install variable air volume diffusers for each office partitioned office and boardroom for Indoor Air Quality to comply with SANS 10400-part O and SANS 10147 according to the Construction Layout for parliament office park eighth floor.

The Contractor shall supply and install additional return air grilles for the new office space and boardrooms.

Each of the diffusers will be connected to the ceiling ducts with a 1.5-meter length of insulated flexible ducting.

It is important that the positioning and co-ordination of the ceiling grid, diffusers, the lighting and the sprinkler heads are carefully checked to ensure the correct and most suitable positioning of the various services is achieved.

# Variable air flow HVAC system as standby plant

The Contractor shall supply and install new variable air volume indoor and outdoor units as a standby plant for the central HVAC system.

The Contractor to supply and install variable air volume diffusers for each office partitioned office and boardroom for Indoor Air Quality to comply with SANS 10400-part O and SANS 10147 according to the Construction Layout for parliament office park eighth floor.

# Upgrade Temperature senser controllers

The Contractor shall supply and install the Temperatures Sensor Controllers for every office.

The contractor shall supply and install new additional install temperature sensor controllers for each office partitioned offices and boardrooms.

Each new partitioned office and boardroom should have their own dedicated temperature controllers.

# Installation of Dx Under ceiling units for Server Room.

The Contractor shall supply and install Dx Under ceiling units for Server Room to the new position of the IT Server Room to comply with SAN10400-part O and SANS 10147.

# Mechanical Ventilation – Toilet ventilation

The existing ablutions on Eighth Floor have separately mechanically Extraction air system consisting of extraction disc valves and sheet metal ducts located on the Eighth Floor connected to a duct riser and Extraction fan at the located Roof.

The Contractor shall supply and install galvanised sheet metal Ducting and Extract Disc Valves extracting from the Ablutions for the new ablutions on the Eighth Floor as per SANS 10400-part O.

The Contractor shall supply and install Ablution doors with ventilation grilles.

The Contractor shall provide a Quality Control Plan (QCP) indicating HVAC hold points are enforced to ensure full compliance with applicable standards.

# Supply Air Ducting

This existing Supply Air Ducting will not be modified.

The Contractor shall clean the supply ducts to remove in built dust and allergens to improve indoor Air Quality.

The terminal point interface with existing HVAC services will be at the existing duct risers currently serving 8th Floor Eskom Executive Suite at Thibault Square Building.

The Contractor shall provide a Quality Control Plan (QCP) indicating HVAC hold points are enforced to ensure full compliance with applicable standards.

# WET SERVICES DESIGN

# Terminal Points

The terminal point of the scope of work will be the existing inner wall terminal interfaces of the hot and cold-water reticulation, sewage and drainage systems within the existing ablution facilities for 8th Floor Executive Suite at Thibault Square Building.

# Scope of work Summary

This includes for the decommission existing, supply, co-ordination, fabrication, delivery, installation, painting, testing, commissioning and handing over in complete working order a new wet services system and drainage system for the refurbishment of 8th Floor Executive Suite at Thibault Square Building

The works covered under this section includes the installation of:

•	cold water supply pipes and fittings for ablutions and kitchens

•	Drainage, sanitary fixtures and plumbing equipment for the ablutions and kitchens

The contractor shall decommission existing Wet services and drainage system and replace with new wet services and drainage system for 8th Floor Executive Suite at Thibault Square Building.

Each section is discussed in detail within the document.

# Contractor's Drawing, Equipment Selection and Sample Submissions

The contractor shall select material, submit selected materials for approval to the employer, submit shop drawing to the employer for approval, the contractor shall submit method statements, quality control documents to the employer for approval prior construction, the contractor shall construct, test balance and commission the units and hand it over to the employer, the contactor shall decommission existing plant in preparation to install new plant.

# Cold Water Supply

The contractor shall strip existing Coldwater pipes and valves for the existing ablutions and kitchens and supply and install new piping and valves for 8th Floor Executive Suite at Thibault Square Building.

The Contractor shall supply and install new piping and fixtures for the new ablutions for the 8th Floor Executive Suite at Thibault Square Building to connect to existing cold water pipe risers.

The Contractor shall where required make provision for suitable material for the Terminal interface between copper pipes supplying the ablutions and kitchen and galvanized mild steel pipe risers.

# Metering

The Contractor shall supply and install Smart meter(s) for the cold-water supply system to block 8th Floor Executive Suite at Thibault Square Building.

# Drainage system, sanitary fixtures and plumbing equipment

The contractor shall strip existing drainage pipes, sanitary fixtures and plumbing equipment for the Ablutions and Kitchen and design, supply and install new drainage pipes, sanitary fixtures and plumbing equipment for 8th Floor Executive Suite at Thibault Square Building as per SANS.

The Contractor shall design, supply and install new drainage pipes, sanitary fixtures and plumbing equipment for the new Ablutions for the 8th Floor Executive Suite at Thibault Square Building to connect to existing drainage pipe Risers.

The Contractor shall provide a Quality Control Plan (QCP) indicating HVAC hold points are enforced to ensure full compliance with applicable standards.

# FIRE PROTECTION DESIGN

# Terminal Points

The terminal point interface with existing fire protection system will be at the existing pipe risers currently serving 8th Floor Eskom Executive Suite at Thibault Square Building.

# Existing Fire Protection System (FPS):

Parliament building is equipped with Fire protection system comprising of automatic fire sprinklers, pipe risers, fire hydrants, fire hose reels fed from the existing building fire mains reticulation and fire extinguishers and SABS approved photo luminescent symbolic fire signage.

# Scope of work Summary

This includes for the design (Where required), decommission existing, supply, co-ordination, fabrication, delivery, installation, painting, testing, commissioning and handing over in complete working order automatic fire sprinkler system, fire hydrants, hose reels, portable fire extinguishers, fire sealing, fire signage installations for the refurbishment of 8th Floor Eskom Executive Suite at Thibault Square Building.

The works covered under this section includes the installation of:

- An automatic fire sprinkler system within the voids and below the new ceilings.

- Fire protection equipment

- Fire signage

- Fire sealing

Each section is discussed in detail within the document.

# Contractor's Drawing, Equipment Selection and Sample Submissions

The contractor shall select material, submit selected materials for approval to the employer, submit shop drawing to the employer for approval, the contractor shall submit method statements, quality control documents to the employer for approval prior construction, the contractor shall construct, test balance and commission the units and hand it over to the employer, the contactor shall decommission existing plant in preparation to install new plant.

# Automatic Fire Sprinklers

There is an existing Automatic fire sprinkler system however, there are no existing approved as built for the Fire Protection system

The Contractor shall design, supply, install and commission the automatic fire sprinkler system for the 8th Floor Eskom Executive Suite at Thibault Square Building.

The Contractor shall submit design layouts to Municipal for Approval prior installation of the Fire protection System.

It is important that the positioning and co-ordination of the ceiling grid, diffusers, the lighting and the sprinkler heads are carefully checked to ensure the correct and most suitable positioning of the various services is achieved.

# Fire Protection equipment (Fire Hydrants, hose reels and extinguishers)

There are existing Fire Hydrants, fire hose reels and extinguishers for the Eight Floor however, there are no existing approved as built for the Fire Protection system for 8th Floor Eskom Executive Suite at Thibault Square Building.

The Contractor shall design, supply, install and commission Fire protection system comprised of Fire Hydrants and Fire Hose reels to connect with existing pipe risers for the Eighth Floor.

The Contractor shall submit all design Layouts to Municipal for Approval prior installation.

# Fire suppression system for Information Technology (IT) / Server Room

The Contractor shall design, supply and install gas suppression system for the IT / Server Room, compliance is based upon SANS14520, SANS10139 and SANS10400-T

All gas installations must be designed, installed, commissioned and serviced by a competent professional registered with South African Qualification and Certification Committee (SAQCC) For Fire.

The Contractor shall submit design Layouts to Municipal for Approval prior installation.

# Symbolic Fire Signage

The contractor shall install were required SABS approved photo luminescent (glow in the dark) symbolic signs mounted in aluminium frames indicating all firefighting equipment, fire escape routes and exit doors in accordance with SANS 1186.

# Fire Sealing

The Contractor shall where required seal all service penetrations through concrete floors and walls for block 8th Floor Eskom Executive Suite at Thibault Square Building to achieve a 120-minute fire rating in accordance with SANS 10400-T-2011.

# Piping

Piping for sprinkler system for 8th Floor Eskom Executive Suite at Thibault Square Building shall be galvanized and in accordance with SANS 62 and SANS 719.

Fire piping shall be fully painted signal red in accordance with SANS 1091. Note that the contractor is accountable to provide the proper priming on galvanised pipes before it is painted to ensure the paint does not flake off.

# Welding

Welding shall be done according to 240-106628253 Standard for Welding requirement on Eskom Plant.

The Contractor shall provide a Quality Control Plan (QCP) indicating Fire Protection System hold points are enforced to ensure full compliance with applicable standards.

# ELECTRICAL DESIGN

The primary objective of the project is to upgrade and reconfigure the electrical infrastructure on the 8th floor to align with the new office layout and operational requirements. This includes removing outdated installations, providing a new UPS system capable of delivering 100% backup, and installing new lighting and socket outlets that are coordinated with the revised partitioning plan.

The purpose of these works is to ensure that the 8th floor is fully equipped with a reliable, resilient, and modern electrical system that supports business continuity and workplace functionality. By integrating a new UPS with full backup capacity, the project guarantees uninterrupted power supply for critical operations. The state of the art of lighting and socket outlets will enhance usability, safety, and compliance, while supporting the flexibility of the new partitioned layout.

This specification covers the manufacture, supply, delivery, offloading, installation, testing, commissioning and handing over of all the electrical works required for the proposed 8th Floor Eskom Executive Suite at Thibault Square Building Project.

The attention of the Contractor is drawn to the Bill of Quantities (BoQ) that forms an integral part of the specification and especially the following clauses:

- Where the term “or other approved” is used in connection with proprietary materials or articles, it is to be understood that approval shall be at the sole discretion of the Engineer.  Where brand or trade names are referred to in the Drawings and Bill of Quantities, these shall indicate the quality and type of material or fitting required and no substitution of materials so specified will be permitted, unless the authority of the Engineer has been obtained, in writing, before tenders close.

- The drawings listed in the index form an integral part of this specification but are issued for tender purposes only and are not intended to be used for construction without the prior written approval of the Employer’s Representative.

- The positioning of all equipment, light fittings, light switches, socket outlets etc. on the drawing, is schematic only and in some cases may not correspond to the actual layout of the buildings.  The successful Contractor shall be responsible for indicating the correct position of all electrical equipment on their working drawings to enable the Employer’s Representative to produce “as built” drawings.

The successful Contractor shall provide all labour, materials, equipment, tools and supervision to transport, assemble, erect, install, connect, test and place into service the complete electrical works.  The works shall consist of, but are not limited to:

- Supply and installation of light fittings and occupancy sensors.

- Supply and installation complete with termination of conduit, wiring earthing, etc where required.

Contractors are to allow for ALL work and materials indicated and implied on the drawings, whether indicated in the specification or not, to deliver a complete and operational project.

All work shall be done by an electrical contractor registered with the following regulatory bodies:

- Electrical Contractor with the Department of Labour - Compulsory

- CIDB (Construction Industry Development Board) - Compulsory

- Electrical Contracting Association of South Africa (ECA) - Optional.

The electrical contractor shall provide valid and certified copies as proof of accreditation and registration with the CIDB and Electrical Contractor certificate prior to commencement at the site hand-over meeting and prior to commencement of any work.

# Balancing of load

The successful Contractor is required to balance the load as equally as possible over the multiphase supply where applicable.

# Low Voltage Cable Installation

All low voltage cables shall be in accordance with the standard and detail specifications.

Use the existing cables to terminate on the lighting fixtures and small power as per drawings.

The minimum radius of bends in all cables shall be as per the manufacturer recommendation to ensure that the minimum bending radii of the cables are maintained at all times during and after installation.  Failure to adhere to this requirement may result in the rejection of the particular cable.

# Distribution Boards

Issue a Certificate of Compliance (CoC) as per SANS 10142-1 for the existing supply Distribution Board (DB). The existing 160A supply will remain as the primary incoming feed, but all current lighting and socket outlets are to be removed to allow for a complete redesign. The existing generator and UPS connections will be retained (UPS to be relocated to new position); however, the Employer requires the installation of a new 60kVA UPS system capable of delivering 100% backup coverage to all critical loads, ensuring full resilience and continuity of operations for minimum time of 1 hour at full capacity occupancy.

The generator will kick in and provide supply to the lights and a few socket outlets once the UPS batteries are depleted. The generator will provide partial backup solution which will ensure that operations can continue as long as the generator is running.

# Wiring

In general, all wiring, where applicable used in installations shall be of at least 600/1000V grade in accordance with SABS 1507 and PVC insulated.

Light circuits shall be wired with 2.5mm² 7 strand copper conductor PVC insulated wire.

Switched socket outlets and power points shall be wired with 4mm² 7 strand copper conductor PVC insulated wire.

Air conditioner and heater circuits, where applicable shall be wired with 6mm² 7 strand copper conductor PVC insulated wire.

Wiring for circuits not specified shall be according to SANS 10142-1.

Associated with every circuit, a stranded copper earth conductor shall be run and connected to the terminal of the appliance or outlet and on the installed earth bar within the distribution board.  Wire sizes shall be as follows:

- 6mm² conductor		:	4mm² earth wire

- 4mm² conductor		:	2.5mm² earth wire

- 2.5mm² conductor		:	2.5mm² earth wire

- 1.5mm² conductor		:	2.5mm² earth wire

Where circuits are run in metal conduit, bare earth conductor shall be used and PVC insulated earth conductor shall be used for circuits run in PVC conduit.

# Power skirting

The power skirting shall provide for all the services detailed on the layout diagrams and shall be in accordance with the type specified in the legend, or equal approved.  Wiring shall conform to the standards detailed within this specification.  The power skirting shall be of the type detailed on the layout diagrams complete with all bends and end caps.

The per meter rate quoted for the supply of the power skirting shall include for all necessary covers, fitting mechanisms, fixers and consumables, but shall not include for switched socket, telephone or computer LAN outlets plus cover plates and other hardware fitted into the power skirting.

Conduits linking between sections of power skirting and between the power skirting and the relevant distribution boards shall be provided as per the requirements for plug, telephone and computer LAN circuits.

# Workstation Point Consisting

- 1 X 16A Normal Power SSO (White)

- 1 X 16A Euro Plug

- 1 X 16A SSO With Shaved Earth Pin (Red)

- 1 X USB Type A

- 1 X USB Type C

- 1 X Data Connector

- 1 X Voice Connectors

# Lighting

The new electrical design incorporates lighting systems that are tailored to the new partitioning arrangement, providing appropriate illumination levels and compliance with workplace standards as per the lighting layout. All light fittings will be new and made of Type A 50W 2433x96x66mm Recessed LED Linear Light fixture, Type B 18W recessed LED Downlight, Type C 10W recessed LED Downlight and will be controlled using the occupancy sensors as directed in Drawing No: parliament office-100002-Rev 0. Supply DB is the existing SDB-8TH Floor as per the single line diagram.

- Lighting Conduit Work

Lighting circuits are to be conduited using 20 mm conduit, and all lighting circuits are to be routed via the ceiling.  A separate circuit shall be run from the distribution board for each of the light circuits as indicated on the layout diagrams.

The successful Contractor is to co-operate closely with the building contractor to ensure that luminaires are symmetrically positioned with regards to the ceiling pattern. The exact positioning of lights and switches is to be confirmed with the Client’s Representative.

- Lighting General

Lighting shall comply with the SABS standards where applicable.  The luminaires specified are detailed in the Bill of Quantities and drawings.  Where alternative luminaires and lamps are offered, the details shall be submitted with the tender.  All alternatives shall be subject to the approval of the Client’s Representative.

Earth conductors shall be connected to the earthing terminal of all luminaires and in accordance with SANS 10142-1. All luminaires shall be supplied complete with a first working fitting of the appropriate lamp in each lamp holder. Each lighting circuit on the Distribution Board shall consist of a 10A single pole MCB of 5 kA rupturing capacity, unless specified otherwise on the single line diagram.

Lighting will be controlled by occupancy sensors in most spaces to maximize energy efficiency and automate switching. In service ducts and utility areas, lighting will be operated by manual switches only. DALI (Digital Addressable Lighting Interface) system will be implemented to allow individual control of luminaires and enable dimming.

The contractor shall be responsible for the design, supply and installation of the DALI system that will enable the efficient control of lighting.

Lighting shall comply with the SABS standards where applicable.  The luminaires specified are detailed in the Bill of Quantities and drawings.  Where alternative luminaires and lamps are offered, the details shall be submitted with the tender.  All alternatives shall be subject to the approval of the Client’s Representative.

# Air Conditioner Circuits

Air conditioner circuits are to be conduited using 25mm conduit, and all air conditioner circuits are to be routed via the ceiling.

The Contractor shall provide a Quality Control Plan (QCP) indicating Electrical System hold points are enforced to ensure full compliance with applicable standards

# Electrical health and safety risk management

The works on the 8th floor involve the removal of existing electrical installations, the installation of a new UPS system, and the redesign of lighting and socket outlets to suit the revised partitioning. These activities present a range of health and safety risks that must be carefully managed to ensure compliance with statutory requirements and the protection of all personnel on site.

Key risks include electrical hazards during the strip out and installation phases, potential exposure to live circuits, manual handling injuries from the movement of heavy equipment such as UPS units and working at height during the removal and installation of lighting fixtures. Dust, noise, and general construction hazards associated with demolition and fit out works also need to be controlled.

Risk management will be achieved through strict adherence to established health and safety protocols. This includes isolating and locking out electrical supplies before removal works commence, ensuring all operatives are competent and trained, and providing appropriate personal protective equipment (PPE). Safe systems of work will be implemented for manual handling and working at height, supported by risk assessments and method statements. Fire safety and emergency procedures will be reviewed and updated to reflect the temporary removal of existing systems and the installation of new equipment. Regular site inspections, toolbox talks, and coordination meetings will be conducted to reinforce safety awareness and address emerging risks. All activities will be monitored to ensure compliance with occupational health and safety legislation, and a dedicated safety officer will oversee the implementation of risk management measures throughout the project.

# Electrical environmental constraints and management

The refurbishment of the 8th floor presents several environmental considerations that must be addressed to ensure compliance with sustainability standards and minimize adverse impacts. The removal of existing lighting and socket outlets will generate electrical and construction waste, which must be managed responsibly. Hazardous materials, such as fluorescent lamps require safe handling and disposal in accordance with environmental regulations. Noise and dust generated during strip out and installation activities may also affect building occupants and the surrounding environment, necessitating appropriate mitigation measures.

Environmental management will focus on waste reduction, segregation, and recycling wherever possible. All redundant electrical components will be collected and disposed of through certified recycling channels. The procurement of the new UPS system and lighting will prioritize energy efficient equipment to reduce long term environmental impact and operational carbon footprint. Dust suppression techniques controlled working hours, and noise management strategies will be implemented to minimize disruption to occupants and neighbouring areas.

In addition, the new design will incorporate modern, energy efficient lighting and power distribution systems that align with sustainability objectives. The UPS installation will be specified to optimize efficiency and reduce energy losses, supporting the organization’s broader environmental commitments. Regular monitoring and reporting will be undertaken to ensure compliance with environmental legislation and to demonstrate responsible management throughout the project lifecycle.

# Electrical spares and consumables

To ensure the long term reliability and maintainability of the refurbished electrical installation, a comprehensive package of spares and consumables will be provided as part of the project handover. These items will support routine maintenance, facilitate rapid replacement in the event of component failure, and minimize downtime for critical systems.For the UPS system, spare batteries, fuses, and control modules will be supplied to allow for immediate replacement of high wear or failure prone components. The lighting installation will be supported with spare luminaires, drivers, and lamps to cover potential failures and ensure consistent illumination across the floor. Similarly, spare socket outlets, switches, and circuit breakers will be provided to maintain the integrity of the power distribution system.

Consumables such as cabling, connectors, fasteners, and protective covers will also be included to support minor repairs and adjustments during the operational phase. All spares and consumables will be catalogued and documented within the operating manuals, ensuring that building management has clear guidance on usage, storage, and replacement procedures. This structured provision of spares and consumables ensures that the Employer can maintain the installation efficiently, safeguard against unexpected failures, and uphold the quality and resilience of the electrical systems over their lifecycle.

# Electrical quality management

The quality of the 8th floor refurbishment will be assured through a structured and comprehensive management process. All works will be carried out in accordance with relevant industry standards, statutory regulations, and the Employer’s design requirements. Quality assurance will begin at the design stage, ensuring that the new UPS system, lighting, and socket outlets are specified to meet performance, safety, and efficiency criteria. During installation, strict inspection and testing procedures will be implemented to verify compliance with design specifications and regulatory standards. This includes routine checks on electrical connections, verification of UPS capacity and functionality, and commissioning of lighting and socket outlets to ensure they align with the new partitioning layout. Any deviations or defects identified will be rectified promptly under a controlled corrective action process.

Documentation such as as built drawings, operating manuals, and maintenance schedules will form part of the quality deliverables, provide a clear record of the completed works and ensure long term reliability. Independent audits and client inspections will be facilitated to confirm that the project meets contractual obligations and quality benchmarks.

# Testing and Inspection

The successful Contractor shall comply with the relevant requirements concerning registration of electricians, registration of the works, testing and inspection.

Prior to handover, a comprehensive program of tests and inspections will be undertaken to verify that all installations meet the Employer’s design requirements, statutory regulations, and industry standards. These procedures are critical to ensuring the safety, reliability, and performance of the new electrical systems. For the UPS system, factory acceptance tests will be conducted to confirm capacity, efficiency, and full back-up functionality. On site commissioning will include load testing, integration with the generator supply, and verification of seamless transfer during power interruptions.

The lighting installation will undergo lux level testing to ensure compliance with workplace standards, alongside functional checks of emergency lighting and controls. Socket outlets and power distribution circuits will be tested for continuity, insulation resistance, polarity, and earth fault loop impedance to guarantee safe operation. All systems will be subject to independent inspections and witnessed testing where required, with results documented in formal test certificates. Quality assurance procedures will ensure that any defects identified during testing are rectified prior to delivery.

The successful Contractor shall ensure that all equipment is installed and tested in full compliance with the requirements of the manufacturers of the equipment so as to ensure that the guarantees offered by the manufacturers are not compromised.  The successful Contractor shall familiarise himself in detail with the manufacturer’s requirements prior to the installation of the equipment, and, where necessary, the installation work shall be carried out under the supervision of the manufacturer/supplier.

The successful Contractor shall carry out continuity, earth leakage, earth loop impedance and insulation tests to ensure that the installation is functional and safe.

A full functional test will be carried out on the installation for a period to determine the satisfactory working thereof after completion of the works and before first delivery is taken.  During this period the installations will be inspected and the successful Contractor shall make good, to the satisfaction of the Engineer, any defects that may arise.

The successful Contractor shall provide all instruments and equipment required for testing and any water, power and fuel required for the commissioning and testing of the installations at completion.

The successful Contractor shall on completion of the tests, submit, in terms of the OHS Act  No.85 of 1993 (as amended), a completed and signed Certificate of Compliance for Electrical Installations to the Clients Representative.

On completion of the Contract Works, the successful Contractor shall remove all dirt and debris arising from the Contract Works from site, paying particular attention to roof spaces.

Only Contractors registered with the Electrical Contracting Board of South Africa in accordance with Regulation 5 of the Occupational Health and Safety Act will be accepted and permitted to do work under this Contract.

The requirements of Regulation 5(2) will be strictly enforced, and are repeated for convenience purposes:

“5(2)	The Electrical Contracting Board of South Africa shall, free of charge, register as an electrical contractor and enter into a register kept for that purpose the name of any person who applies therefore in terms of sub-regulation (1) and who

- has a fixed address and has a telephone listed in his name; and

- employs an accredited person on a full-time basis or is himself an accredited person.”

An “accredited person” is defined in the Regulations as “……a person registered in terms of Regulation (9) (of the Act) as an electrical tester for single phase, an installation electrician or a master installation electrician, as the case may be”.  If, for any reason whatsoever, the successful Contractor fails to comply with these statutory requirements during the Contract period, after having been accepted initially to do work under this Contract, the services of the successful Contractor will be terminated in accordance with Clause 56 of the Conditions of Contract.

# Commissioning of the electrical system

Commissioning will ensure that all electrical installations are fully tested, verified, and operational before handover. The process will include:

- UPS System: Load testing, battery autonomy verification, and seamless transfer checks between mains and generator supply.

- Lighting: Lux level measurements, emergency lighting functionality, and compliance with SANS 10114 standards.

- Socket Outlets & Distribution: Continuity, insulation resistance, polarity, and earth fault loop impedance testing to confirm safety and reliability.

- Integration: Verification of coordination between UPS, generator, and distribution systems to guarantee uninterrupted operation.

- Documentation: Test certificates, commissioning reports, and updated as built drawings will be issued to confirm compliance.

- Training: Building management staff will be briefed on system operation and maintenance procedures.

Only once all commissioning activities are successfully completed and documented will the installation be deemed ready for handover.

On completion, the contractor must provide as built drawings showing the final electrical layout, UPS integration, lighting, and socket outlets. Operating manuals for all systems, including UPS and lighting, must be delivered with clear instructions for use and safety.

A set of maintenance schedules will outline inspection intervals and replacement timelines for critical components. Test certificates and commissioning reports must confirm compliance with design and regulatory standards.

The Contractor shall provide a Quality Control Plan (QCP) indicating Electrical system hold points are enforced to ensure full compliance with applicable standards

# Standards and Code of Practice

Where reference is made to any Code of Practice or Standard Specification, the latest amendment or edition shall apply.  The contractor shall ensure that they are acquainted with the contents of such documents.

Installation work shall be carried out in full compliance with the Codes of Practice mentioned and in accordance with good engineering practice. All materials and equipment shall be new and of high quality which complies with the relevant Specifications.  The contractor shall ensure compliance with these specifications and if requested by the engineer, shall prove compliance at his own cost.

The manufacture of equipment and the complete installation shall be carried out and tested in accordance with the latest issue and/or amendments of the regulations.

The contractor shall issue all notices and pay all the required fees in respect of the installation to the authorities and shall exempt the employer and the engineer from all losses, claims, costs or expenditure which may arise as a result of the contractor’s negligence to comply with the requirements of the regulations.

It shall be assumed that the contractor is conversant with the abovementioned requirements and specifications.  Should any requirements, by-laws or regulation, which contradicts the requirements of this document, apply or become applicable during erection of the installation, such requirement, by-law or regulation shall overrule this document and the contractor shall immediately inform the engineer of such contradiction.  Under no circumstances shall the contractor carry out any variations to the installation in terms of such contradictions without obtaining the written permission to do so from the engineer.

# Employer’s requirements

In line with accepted practice, the Employer has, from time to time, standardised on the supply of various items of equipment.  The Contractor shall undertake, and by the submission of his tender confirms that he has undertaken, to inform himself of the status of such standardisation requirements ruling at the time of tender, and any deviations from such standards shall be corrected by the successful Contractor at his expense.

# Drawings and Documentation

The successful Contractor shall provide four sets of “as built” drawings and operational manuals for all equipment installed in terms of this specification, the drawings and Bill of Quantities.  One set shall be provided to the Clients Representative and three to the Employer.

The maintenance and operational manuals must be complete with an index and be bound in a suitable hard cover binder such as Bantex A4 Ring Binders.  The files must be provided with stiff dividers on which the relevant sections are indicated and are to be in printed or typed format.  Drawings shall be housed in plastic pockets in the file, and only one (1) drawing per pocket will be allowed.

In addition, all “as built” drawings must be stored on CD in .dwg format and must also be submitted with the manuals.

All schematic electrical “as built” drawings of distribution boards must be laminated and attached to the inside of the doors with double sided tape.

The main distribution board/electrical panel schematic diagram in the low voltage plant room or in other plant rooms as well as the schematic site reticulation layout, if applicable, must be suitably framed with Perspex and be mounted in the plant room in a position as indicated on site.

The maintenance and operational manuals must consist of the following sections where applicable to the project:

- Operations section, covering description of the system and functioning thereof, all starting up and stopping procedures, fault-finding procedures, pre-start checks and equipment running checks.

- Comprehensive data log sheets to be kept by the user of the system.

- General system description and general information schedules of plant and equipment, such as description of equipment, model number, capacity, electrical requirements of equipment, name and address of supplier, name of manufacturer.

- Design information:  Design data sheet containing all design and selection parameters, calculations, selection curves, etc. Settings and values recorded during commissioning.

- Manufacturers’ brochures, pamphlets, pump curves, etc. Maintenance data and schedules:  The lapse of time between services and the description of service requirements for each part, piece of equipment or item installed under the Contract.  This section must also include the detailed daily, weekly, monthly, three monthly, six monthly and yearly preventative maintenance instructions and checklists.

- Manufacturers’ literature indication lubrication points, lubricants to be used and other data referred to above.

- Commissioning data of all equipment and systems with all set points listed in table format relating to the specific piece of equipment and/or system.

- All other data relating to other components forming part of the system/reticulation such as valves, diffusers, medical gas outlet points, etc.

- Critical spare parts list for all equipment.

- All test certificates (any certificates required in terms of the installations as pertaining to the project), compliance certificates, lightning protection certificates, certificates of construction of electrical panels.

- Schematic wiring diagrams and equipment ratings of all electrical panels and distribution boards.

- All “As-Built” drawings of mechanical and electrical installations pertaining to the project.  “As-Built” drawings must be the true reflection of the installation as on site and must include the actual particulars of the equipment as installed on site and must be signed and dated by the responsible consultant and must be marked “AS BUILT”.

- All “As-Built” drawings, including wiring diagrams, must be produced in Autocad format and be stored on CD as listed above.

# EXCLUSIONS

None.

# Parts of the works which the Contractor is to design

The scope of work includes assessment, design, procurement, construction, manufacturing, installation, testing, commissioning, 3rd party certification and training for all affected systems.

# Procedure for submission and acceptance of Contractor’s design

All Documents are submitted to the Project Manager for review prior to implementation. All review documentation is submitted with transmittals. Any review information submitted without transmittals are considered rejected automatically.

At the end of each contracted design phase (e.g., Concept, Basic, detailed design phase), the Contractor provides an integrated design report which is reviewed at a Multi-Disciplinary Design Review (MDR) which will allow the project to move into the next design phase or allow for design freeze.

Construction may not begin prior to design freeze.

The following process will be followed during submission of documents:

a) The Contractor submits the documents/drawings to the Employer

b) The Employer’s Document Controller registers the documents.

c) The Employer’s Document Controller will supply the documents/drawings to all relevant parties within the Employer’s project team.

d) The Employer’s project team reviews the documents/drawings and will submit all comments or inputs to the Contractor for consideration.

e) If the Employer finds major deficiencies in the submitted documents/drawings, the Contractor revises the documents/drawings and resubmits to the Employer.

f) The Employer reviews the documents/drawings and if no major deficiencies are found, the Contractor organises a Review session.

g) The Employer and the Contractor conduct a Review.

h) If any fundamental errors were found in the works or further actions are required, the Contractor records all concerns raised and revises the designs.

i) The Contractor organises a review session once all works were revised according to the concerns raised by the Employer.

j) If no fundamental errors were found in the designs during the Design Review session, the Contractor compiles the Review minutes or report and submits it to the Employer

k) The Employer’s Document Controller registers the report.

l) The Employer’s project team reviews the Contractor report/minutes. If the report/minutes are not acceptable, the Contractor revises the report/minutes and resubmits to the Employer’s Agent.

m) The Employer’s Agent will accept the Contractor works once the report/minutes are accepted by the Employer’s project team.

n) Work shall always be subject to full time supervision by a qualified and experienced site agent. This representative must be authorised and competent to receive instructions on behalf of the Contractor.

The following documents are supplied to the Employer by the Contractor as a minimum:

- Detail Design

- Detail design report

- Detail calculations

- Coordination between services

- Design including components data sheets and specification for selected components, distribution, electrical cabling and other associated component

- Dimensioned detailed drawings showing the general arrangement of all plant and component including isometrics and/or P&ID’s where required. Sufficient views must be given to ensure clarity, and the drawing shall have at least a plan and two different elevations or sections giving overall dimensions.

- Detail design drawings. Dimensioned detail drawings showing proposed method of fixing of all the plant and component

- Detailed electrical wiring diagrams including schematic and control circuits.

- Detailed sequencing manner for installation procedure of Works

- Detailed programme for the Works in sufficient detail as to represent the units of work to enable the representative to assess the progress of the Works

- Technical Specifications and Technical literature for all items of component that forms part of the complete installation

- List of recommended spares and technical specifications for the spares

- Detailed structural & civil work for the complete Works

- Detailed maintenance, reliability, control and operating philosophies

- Testing and commissioning procedures

- Plant and material acceptance testing

- Plant Codification Lists for each Section of the Works

# Other requirements of the Contractor’s design

Creation of KKS Coding and cable numbers up to component level.

Allocation of drawing numbers, based on the envisaged quantities of drawings to be produced by the Contractor, a block of drawing numbers will be supplied to the Contractor for allocation to individual drawings.

Labelling of plant to suit KKS and cable numbering.

All the design solutions are developed by the relevant Professional Engineers at all design stages, the associated Professional Engineer will form part of the Contractor’s supervision team and inspect and sign off the various quality documents.

The Contractor is to comply with all legislated safety requirements as well as Eskom’s health and safety standards.

# Use of Contractor’s design

The Contractor grants to the Employer, with effect from the starting date, an irrevocable royalty-free non-exclusive licence to use all of the documents provided to provide the Works (including, but not limited to calculations, drawings, manuals, models and other documents of a technical nature), for any purpose whatsoever, including for the purpose of operating, repairing, maintaining, dismantling, re-assembling and making adjustments to all parts of the Works.

# Design of Equipment

The components are to be designed to facilitate efficient manufacture, inspection, transportation, installation, maintenance, cleaning and repairs.

- The components are to be designed to ensure safe and satisfactory operation for a life expectancy of at least 15 years under the conditions prevailing at Eskom Megawatt Park.

- The components are to be designed to prevent undue stresses being produced by expansion and contraction due to temperature change and other local natural and manmade conditions.

- The components are to be designed to keep maintenance costs to a minimum.

- The components are to be designed to comply with all the legal requirements in respect of safety and the prevention of environmental pollution.

- The components are to be designed to satisfy any specific requirements contained in the relevant statutory codes and standards.

- The components are to be designed for operation of 365 day per annum, 24hrs per day.

- The components are to be designed such that all material from which the components are manufactured from is compatible with the intended duty and service conditions. All components are suitable treated and protected from corrosion.

# Equipment required to be included in the works

As per the Contractor’s approved design to satisfy the requirements stated in this document.

# As-built drawings, operating manuals and maintenance schedules

At Take-over, the Contractor provides two full sets of as-built documentation as hard copies and electronic PDF and native CAD formats (. DGN or .DWG which must be compatible with Bentley MicroStation) to the Employer.

The Operating and Maintenance Manual and Schedules must describe how the plant is to be operated and by whom, as well as the desired level of training and orientation required for the building occupants. The operation and maintenance manuals are to consist of the following as a minimum:

- List of Contents (Index)

- Introduction

- General description of the functions of each of the systems including detailed description of each element of each system, how it functions, how it operates and how to maintain it and what attic stock or tools to carry.

- Full as-built drawings and detailed drawings, brochures and catalogues for each system and each element of each system.

- The format of the O & M documentations is to be A4 and be a specially bound document with hard cover and with metal ring binding. (All drawings and details are to be reduced to A3 format and folded into A4 format.)

- The names, addresses and telephone/fax numbers/email addresses of all responsible persons and manufacturers/suppliers are to be listed in the O& M manual.

- A full list with reference numbers is to be included to enable the O&M staff to order materials and spares.

- Colour diagrams are be provided to illustrate the operation and function of each system with reference to the relevant as-built drawings or brochures of Plant and Materials. These diagrammatic drawings must also indicate the locations of installed equipment with their generated codification.

- Outlines all the required maintenance activities for the complete works as well as the frequency of such activities and by whom.

- Proposed maintenance schedules and activities to complete during maintenance activities.

Shop Drawings

Shop drawings are to indicate all Plant and Materials, distribution systems, testing/inspection/instrumentation positions, access requirements and builder's work requirements.

The Contractor is to review, stamp all shop drawings to confirm that co-ordination with building and services drawings have taken place before submitting to the Employer for Acceptance.

The Contractor’s drawings are to be prepared in accordance with SANS 10111 (Engineering drawing practice) and 240-86973501 (Eskom Engineering Drawing Standard Common Requirements). General arrangement and detailed drawings are to be cross referenced using codification system.

# Procurement

The Contractor provides the following procurement services in performing the Works:

- Preparation of Employer approved supplier and Sub-Contractor’s lists for equipment and contracts to be submitted to the Employer for review and approval.

- Follows the most cost and time saving procurement strategies.

- Contract management services for the selection, appointment, and management of Sub-Contractors, where required to execute the scope.

- Obtains delivery dates from Sub-Contractors and suppliers in order to realize the Completion Date;

- Receiving of invoices, verification thereof in terms of purchase orders and contract provisions, certification of invoices as being correct and payable and supply of correct invoices to the Employer

- Management of and negotiating of all suppliers and Sub-Contractors compensation events and recommendations to the Employer as to the validity, amount and payment of such events.

- Determination of penalties payable by suppliers and Sub-Contractors and recommendation to the Employer as to the enforcement of such penalties prior to any communication to suppliers and Contractors.

- Ensuring that all suppliers and Sub-Contractors, from whom the Contractor procures equipment and materials do not retain, encumber or reserve title to such items.

# People

      - Minimum requirements of people employed on the Site

All the Contractors personnel are subjected to access control conditions as per Eskom requirements.

- All workers employed on site comply with Eskom’s health and safety standards. Workers are not allowed to be transported on the back of vans or bakkies.

- Workers are restricted to the area of activity in close proximity to the construction.

- The Contractor recruits within the immediate District Municipality for general labour/ skills to execute the project.

      - BBBEE and preferencing scheme

The Contractor is required to achieve or maintain BBBEE Level 4 rating in accordance with SD&L requirements.

      - Accelerated Shared Growth Initiative – South Africa (ASGI-SA)

Not applicable for the contract.

# Subcontracting

      - Preferred subcontractors

The Contractor notifies the Project Manager in the event of using any Sub-contractor and provides the Project Manager with a list of all sub-contractors on the project. Subcontractors cannot subcontract work to another subcontractor. The choice of the proposed sub-contractor is subject to the Project Manager’s approval before using the services of such subcontractor. The Subcontractor must be familiar with the required work and should submit CV’s of past experience and have the necessary statutory accreditations.

The Contractor provides the Project Manager with the Health and Safety plans of all the sub-contractors on the project, before commencing the project.

      - Subcontract documentation, and assessment of subcontract tenders

The Contractor uses the NEC subcontractor agreements. All subcontractor quotations for which provisional sums or budgets have been allowed, is first approved by the Employer or his representative with documentary proof. This is done well in advance of the planned scheduling of the work.

      - Limitations on subcontracting

As per Eskom requirements, subcontracting will be limited to 30% as far as possible. The Employer is notified where subcontracting exceeds the 30% threshold prior to commencement of the specific subcontracting works.

      - Attendance on subcontractors

The contractor attends to the activities of all subcontractors including direct subcontractors

# Plant and Materials

      - Quality

The Contractor will not use Plant or Materials which are generally recognised as being unsuitable or otherwise to be avoided for the purpose for which they are intended.

Only components of high reliability will be utilised, with a proven operating history, to enable the Plant to achieve required reliability and availability. Plant and Material design, engineering and manufacture will accord with the best modern practice applicable to high-grade products of the type to be furnished, so as to ensure the efficiency and reliability of the Works and the strength and suitability of the various parts for the Works.

Plant and Materials withstands ambient conditions and the variations of temperature arising under working conditions without distortion, deterioration or undue strains in any part.

All parts are made accurately, and where practicable, to standard gauges so as to facilitate replacement and repairs. Like parts are interchangeable.

No repair of defective Plant and/or Materials will be permitted without the Project Manager’s Acceptance and any such repair, if accepted, will be carried out to the satisfaction of the Employer.

The Project Manager is free to specify hold and witness points during the installation and on-site testing stages of the project. The Contractor issues preliminary notification of such hold and witness points by fifteen working days advance notice to the Project Manager and confirms such hold and witness points at least seven working days prior to the activity.

Typical hold points are listed below:

- Design Review

- Factory Acceptance Test

- Delivery to Site

- Erection and configuration

- Site Acceptance Test

- All manuals and drawings (in the specified format)

- Commissioning

In addition to maintaining appropriate inspection and test records to substantiate conformance to requirements, the following records are safely stored for a minimum period of seven years following the final Completion of the Works:

- Construction, layout and component Acceptances

- Type and routine test certificates

- Construction drawings and Acceptances

After this period, the Contractor offers these records to the Employer (in writing) and obtains a disposal instruction.

Documentation regarding quality procedures is submitted within thirty days of Contract Award. The Employer will review and comment on the acceptability of these documents in a time frame as per the requirements of the contract for contractual correspondence. If controlled copies of these documents have been submitted to the Employer, then the controlled copy numbers may be quoted in the submission.

      - Plant & Materials provided “free issue” by the Employer

None, all Plant and Materials are to be provided by the Contractor.

      - Contractor’s procurement of Plant and Materials

The Contractor is responsible for ensuring that all products are preserved in their appropriate manner as described in their specifications or in Eskom preservation, shipping and transportation procedures as applicable. The Contractor shall submit the preservation, shipping and transportation procedures to the Employer for review and acceptance. The Employer may choose to witness the packaging, loading and offloading of the products depending on their criticality, this will be indicated in the intervention points on the QCP / ITP document. The Contractor shall ensure that all storage requirements for products are properly implemented to preserve the products against adverse conditions, deterioration, damages, etc. Storage and preservation procedures for the different products must be submitted to the Employer for review and acceptance. The Employer may request to inspect the stored products at any given point during the storage period of the product. Requirements for preservation, shipping and transportation are addressed in 240-105658000.

      - Spares and consumables

The Contractor provides as part of the tender proposal, a recommended parts list as well as a proposal for the execution there of:

- The Employer is responsible for purchasing of recommended spares.

- The Contractor is responsible for ensuring that consignment spares are available in time of need.

Each recommended spare part is to be uniquely identified with a part number, which can be cross referenced to a part list and associated drawing. The Employer prefers that support from the OEM is available locally in South Africa.

# Tests and inspections before delivery

The Employer carries out quality inspections at his own discretion. The Employer will inspect and approve stages of manufacture of all Plant and Materials necessary to ensure the correct quality of Plant and Materials as prescribed in the accepted project quality plan.

All inspections and testing are to be performed in accordance with the Quality Control Procedure (QCP) developed by the Contractor after Acceptance by the Employer.

The Contractor must provide facilities for inspection of all items of Plant and Materials at the place of the manufacture and this requirement must extend to all sub-contractors and suppliers if applicable. All material labour or assistance, tools, gauges, articles or apparatus that the Employer may require for the purpose of testing, gauging and inspection, must be provided by the Contractor. The Contractor must provide all such facilities for testing and the contract price must include for this.

The Employer reserves the right to reject items that do not conform to the Employer’s requirements. When the plant has passed the prerequisite tests, the Employer will furnish to the Contractor a certificate or endorse the Contractor’s test certificate to that effect. Examination by the Employer does not relieve the Contractor from the responsibility of carrying out all tests which may be necessary to ensure the required standard of manufacture or from any obligations in terms of the contract.

The achievement of adequate standards during the tests at the place of manufacture, if performed, is only the first requirement. The final criterion will be performance onsite, and any of the requirement which proves defective due to bad workmanship or material must be replaced forthwith by the Contractor at his own cost on the instruction of the Employer.

The following tests are conducted by the Contractor and are to be witnessed by the Employer at the manufacturer’s works or Contractor’s premises as a minimum requirement:

- Visual inspection of the Plant and Materials

- Review of the certification requirements

- Inspection of paint work and corrosion protection.

- Verification that all components are delivered to the Contractor’s premises.

- Verification that all power plugs is correct.

- Verification that components installed is correct.

- Verification that all labels are correct.

# Marking Plant and Materials outside the Working Areas

All Material paid for by the Employer is clearly labelled as being the Employer’s property.

# Contractor’s Equipment (including temporary works).

The Contractor provides the following to complete the Works:

- All scaffolding required

- Any Equipment necessary to complete the Works

- Lifting facilities

The Contractor supplies, installs, maintains and removes all temporary construction facilities and utilities necessary to Provide the Works.

# Cataloguing requirements by the Contractor

Unique Identifier 240-1289988974 to be provided on request.

# Construction

The Contractor is required to:

- Submit a comprehensive method statement of the entire Works to the Project Manager for acceptance prior to the start of the Works

- Submit a project specific safety file to the Employer for comments / acceptance.

- Prepare earthworks for craneage access and working rigging areas if required.

- Manage his activities on site to ensure that no interference takes place between his work and that of others.

- Complete "Contract Activities Daily Reports".

- Liaise with the Project Manager regarding utilities and telephone facilities required for his Site establishment.

- Liaise with the Project Manager regarding the location of waste disposal sites and rubbish dumps,

- Maintain and promotes labour harmony on the Site and in the working environment.

- Immediately report any potential labour disharmony to the Project Manager.

- Not recruit or employ any personnel from the Employer and Others, without prior acceptance of the Project Manager.

- The Contractor submits a fully detailed Quality Control Plan (QCP) for acceptance within one week of the Contract Date.

- The Contractor submits a schedule of unpriced orders to be placed and this is updated regularly.

# Temporary works, Site services & construction constraints

      - Employer’s Site entry and security control, permits, and Site regulations

The site is located in a part of an existing campus, with existing buildings all around, most buildings are currently occupied.

- The Contractor attends the site clarification meeting prearranged by the Employer prior to submitting tender.

- The Contractor ensures that he familiarizes himself with site conditions.

- Contractor’s access is limited to the areas as indicated in the scope and Contractor’s staff is prohibited from roaming in the rest of the facility.

- Eskom Holdings indemnifies themselves from any negligent events by the Contractor relating to the scope of the works within the contract period

- The Contractor, his staff and the Sub-contractors maintain identification at all times e.g. Uniforms etc.

- The Contractor is deemed to execute Safety Procedures to ensure the safety of his staff, Sub-contractors, Eskom staff during the Contract Period.

- Use of power and loud tools to be controlled and/or managed with Eskom office management team.

- The safety of the Contractors Employees, Subcontractors and building’s tenants takes preference over the scope of the Works of this project.

- All site instructions to be approved and authorised in writing by the Project Manager. If this directive is not adhered to it could result in non-payment.

      - Restrictions to access on Site, roads, walkways and barricades

The Employer provides the Contractor with an Access Certificate to formally provide access to the site.

The Contractor ensures that he is familiar with conditions of access to the buildings, which includes constraints to limited parking and no goods lift is available in some of the blocks.

The Contractor adheres to all the requirements which include, but not restricted to:

- Identity cards with photographs

- Cooperation to help Eskom provide the customer with a project schedule reflecting the period during which the construction and commissioning activities will take place.

The Contractor will be responsible for external disputes which may occur regarding the Works.

The Contractor is when necessary or needed, required to make all the necessary arrangements with the Local Authorities via the Building Manager and or Eskom Representative.

      - People restrictions on Site; hours of work, conduct and records

Working after normal working hours and on weekends requires special permission. The Contractor shall give the Employer adequate notice if this is planned.

      - Health and safety facilities on Site

A day clink for medical emergencies is available on site, should the clink not be able to attend to the emergency, the patient will be transported to a hospital at the Contractor’s cost.

      - Environmental controls, fauna & flora, dealing with objects of historical interest

The Contractor shall ensure that all fauna and flora is preserved and protected during his activity on site. All such fauna and flora will be reinstated after completion of the work

      - Title to materials from demolition and excavation

The Contractor has no such title.

      - Cooperating with and obtaining acceptance of Others

Two weeks look-ahead schedule to be developed and submitted to Project Manager on a fortnight basis in order to make timeous arrangements for access into occupied buildings with the occupants concerned.

      - Publicity and progress photographs

The Contractor requests approval from Project Manager for any photography and progress photographs prior to undertaking.

      - Contractor’s Equipment

The Contractor keeps an inventory of equipment brought to site. This is verified and acknowledged by Eskom security to allow removal of such equipment when required by the Contractor

The Contractor provides own security on site and is held liable for excess of insurance in case of theft or loss.

      - Equipment provided by the Employer

The Contractor provides all equipment and tools required to complete the Works.

      - Site services and facilities

The Employer will provide power and water. The Contractor shall make provision of waste disposal and submit proof in a form of Waste Disposal Certificates to the Employer for approval. The Contractor shall provide everything else necessary for providing the Works

      - Facilities provided by the Contractor

A clearly demarcated site establishment area will be provided by the Contractor for the following:

- Suitable facilities for Contractor to store all material and equipment

- Suitable facilities for his employees for changing

- Facilities for the consumption of food

- Site offices

- Toilet/Ablution facilities

- Other temporary facilities required by the Contractor

      - Existing premises, inspection of adjoining properties and checking work of Others

The Contractor is to investigate existence of any services before commencement of work. Care is to be taken when Contractor is doing demolitions so as not to damage the work of Others.

      - Survey control and setting out of the works

It is the Contractor’s responsibility to ensure accuracy when performing setting out of the Works. The Contractor shall provide adequate fastening to existing connection points.

      - Excavations and associated water control

Where excavation is required, the Contractor takes the necessary precautions not to damage any existing services.

      - Underground services, other existing services, cable and pipe trenches and covers

There is no information regarding existing underground services.

Should the need arise for the Contractor to work on underground services, the Contractor is required to conduct scanning to determine the existing/underground services and provides this information as As-Build drawings to the Employer.

      - Control of noise, dust, water and waste

The Contractor takes all precautions necessary to prevent any noise and dust whilst carrying out the work.

      - Sequences of construction or installation

The Contractor sequences execution in order of priority as per the sectional completion schedule and ensures all interfaces are coordinated and carried out without causing any disruptions.

      - Giving notice of work to be covered up

The Contractor to advise at least 4 weeks prior to starting work at that particular section so that proper notification is provided, including relevant authorisation to proceed.

      - Hook ups to existing works

The Contractor stipulates methodology for hooking-up when working in heights and provides notification to the SHE Officer in advance and obtain permission to proceed. The Contractor cannot not hook up for lifting, supporting or for any other reason to any position or existing works in the plant without a written approval by the Project Manager.

# Completion, testing, commissioning and correction of Defects

      - Work to be done by the Completion Date

The contract is deemed complete when the following have been completed in accordance with the scope of work:

- The Plant is erected, and commissioned

- Signed erection and safety clearance certificates have been submitted.

- The final drawings have been submitted.

- All documentation has been submitted including testing reports and the associated certificates received. All Quality Control Plan (QCP) documentation received. Final Draft of the Technical, Operating, Maintenance manuals have been delivered

- The Plant and all documentation / drawings are coded and labelled.

- All special tools / spares have been supplied.

On or before the Completion Date the Contractor shall have done everything required to Provide the Works except for the work listed below which may be done after the Completion Date but in any case, before the dates stated.  The Project Manager cannot certify Completion until all the work except that listed below has been done and is also free of Defects which would have, in his opinion, prevented the Employer from using the Works and Others from doing their work.

|  | Item of work | To be completed by |
| --- | --- | --- |
|  | As built drawings of last commissioned systems | Within 10 days after Completion |

      - Use of the works before Completion has been certified

On completion, commissioning and testing of plant, the Contractor may hand over completed section of the Works for certification and operation.

      - Materials facilities and samples for tests and inspections

The Contractor provides all Materials, facilities and/or samples required for tests and inspections.

The Employer reserves the right to call for samples of the Equipment offered to inspect the workmanship as the work proceeds and to either accept or reject the Equipment or workmanship.

The Employer’s Acceptance of the workmanship or Equipment must in no way reduce the Contractor's liability to provide complete solutions.

The purpose of these inspections is to reduce the risk of non-compliant Equipment and Materials being transported to site. The presence of the Employer at the inspections does not reduce the Contractor’s responsibility to comply with the contract.

The Contractor is to make arrangements that these inspections are carried out within the boundaries of South Africa. Should any tests or inspections be required outside of the Gauteng Area, the Contractor is to allow in his Tender price for all costs (travel, accommodation, subsistence, etc) for two persons to attend such tests or inspections. Accommodation and subsistence arrangements are to be submitted to the Employer for Acceptance in writing.

# Commissioning

When the system is ready for service; commissioning shall take place to check whether the correct quantities of equipment have been delivered, and the installation is in accordance with the specifications. Commissioning shall be performed in co-operation with the Contractor and representatives of the Employer and Supervisor.

Practical Completion certificates will only be issued once the whole of the system installation satisfies the operational performance requirements of the contract and the Supervisor is satisfied that all systems are capable of operating effectively.

Performance and acceptance testing to determine whether the system achieves the required level of performance will only be undertaken after all routine testing, adjusting, commissioning, approvals and building work associated with the contract are complete and the work have been fully tested and commissioned by the Contractor.

Details of the testing required for each system and equipment shall be included in the Contractor’s quality plan.

The Contractor shall supply all labour, materials and equipment required to fully commission and test the installation.

All costs associated in demonstrating that the system performs as required by the contract, shall be borne by the Contractor. Equipment which fails to operate correctly or is found to be installed incorrectly shall be repaired or replaced by the Contractor. Where any test is unsuccessful the defective equipment shall be repaired appropriately and subjected to retesting.

# Start-up procedures required to put the works into operation

In order to put the Works into operation the Contractor demonstrates that the systems comply with all standards and regulations referenced and specified in this document.

# Take over procedures

The Contractor shall do his own complete commissioning tests before the actual first take-over tests are done. This is to satisfy himself that everything is working and is in accordance with the specification.

# Access given by the Employer for correction of Defects

The Project Manager arranges the date and access to site for the Contractor to correct defects. The Contractor updates the site safety file and the records contained inside as per construction regulations. The Contractor will be responsible for ensuring that the area is barricaded before correcting any defects.

# Performance tests after Completion

In accordance with clause X17, performance test will be conducted on completion.

# Training and technology transfer

After Completion of the contract, the Contractor is required to provide training and transfer system knowledge to the building owner/manager by submitting documented Design Intent, As-built drawings, Operational and Maintenance Manual, Commissioning Records, Commissioning Report and by providing training on all the systems to the building management staff to ensure that they have all the information and understanding needed to operate and maintain the features and systems in the building.

The Contractor is to provide on-site training and training material to the Engineers, Operators and Maintenance personnel prior to taking-over of the Works. The training will preferable be offered during the commissioning and testing. The Contractor will, prior to handing over of the Works, satisfy the Employer or authorized representative that maintenance and operational personnel are competent and adequately trained to maintain and operate the Plant and Materials supplied.

Steps for Conducting On-site Training are to include, but not limited to:

- Preparation

- Introduction

- Explanation

- Demonstration

- Practice Under Supervision

- Conclusion

The Contractor shall accordingly take into the Works an agreed number of members of the Employer’s staff for an agreed period. The Contractor shall give the staff workshop hands-on training as fitter-erectors on the plant and shall give instruction in the assembly, adjustment and works testing of main items of plant.

Subsequently the Contractor will have the assistance of Employer’s staff in commissioning of the plant and shall give appropriate instruction during these periods. Whilst the personnel allocated by the Employer can be expected to contribute in some measure to the erection work, the Contractor shall, in the Tender and when determining the programme, take into account that these personnel are involved only for training purposes.

The Contractor shall include attendance of the Employer’s staff during testing and witnessing and for key works inspections.

The Contractor shall provide detailed proposals setting out the key aspects of training which will be provided for the Employer’s personnel, both in the manufacturers’ works and on the Site, including the proposed training programmes.

# Operational maintenance after Completion

The Contractor will be liable for maintenance of the equipment for 52 weeks after the completion date.

# Plant and Materials standards and workmanship

The drawings include final general arrangements. Drawings include sections and details to fully identify design concepts, design loadings and any other special features.

Drawings are fully dimensioned and the dimension figures on the drawing are deemed to be correct, even if the drawings are not to scale. No dimensions are obtained from a drawing by scaling.

All drawings show full endorsement by a Professional Engineer.

    - Investigation, survey and Site clearance

The Employer shall instruct the Contractor to conduct additional investigations of existing facilities within the building if required for interfacing purposes.

# List of Standard

    - Architectural/Planning Layout STANDARDS

- SANS 10400: The Application of the National Building Regulations (Specifically Part T: Fire Protection).

- SANS 1253: Fire Doors and Fire Shutters.

- 240-52599753: Workspace and Furniture Standard for Commercial Properties

- 240-15762340: Universal Access Specifications

- 240-56364535: Architectural Design and Green Building Compliance Manual

- 32-727: Eskom Safety, Health, Environment and Quality (SHEQ) Policy

- SANS/ISO 9001: Quality management systems

- 240-56364535: Architectural Design and Green Building Compliance Manual

- Eskom Universal Access Specifications

    - Fire Protection System STANDARDS

- SANS 10400: 2011 – Part T: Fire Protection

- SANS 10400: 2011 – Part W: Fire Installation

- SANS 10287: Automatic Fire Sprinkler Systems

- SANS 10400: The application of the National Building Regulations Part T: Fire protection

- ASIB 11th Edition Eleventh edition rules for automatic sprinkler installations

- SANS 543: Fire Hose reels

- SANS 1186– 5: Symbolic Safety Signs – Part Five: Photo luminescent signs.

- SANS 10105-1: The use and control of Firefighting equipment – Part One: Portable and wheeled fire extinguishers.

- SANS 10139: Fire detection and alarm systems for buildings – system design, installation and servicing

- 240-54937439: Fire Protection / Detection Assessment

- 240-54937450: Eskom Fire Protection and Life Safety Design Standard

- 240-54937454: Eskom Inspection, Testing and Maintenance of Fire Protection Systems

    - Heating, Ventilation, Airconditioning System STANDARDS

- SANS 10400	National building regulations

- SANS 10400-O Ventilation and Lighting

- ASHRAE   62 American Society of Heating Refrigeration and Air Conditioning Engineers. Ventilation for acceptable indoor air quality

- 240-102547991 Eskom General Technical Specification for HVAC Systems

- 240-143112846 Heating Ventilation and Air Conditioning (HVAC) System Work Instruction

- SANS 10147	Refrigerating systems including plants associated with air conditioning systems

- SANS 10142-1 The wiring of premises Part 1: Low-voltage installations

- SANS 10173	The installation, testing, and balancing of air-conditioning duct work

- SANS 1424	Filters for use in air-conditioning and general ventilation

- SANS 0173	Installation, Testing and Balancing of Air-conditioning Ducting

- SABS 1424	Filters Used in Air Conditioning and General Ventilation

- SANS 10142-1	The wiring of premises Part 1: Low-voltage installations

- SANS 1238	Air-conditioning ductwork

- SANS 10173	The installation, testing, and balancing of air-conditioning duct work

- SANS 1424	Filters for use in air-conditioning and general ventilation

- ASHRAE 52/76 Standard test method for filters

- SANS 0173	Installation, Testing and Balancing of Air-conditioning Ducting

- SABS 1238	Air Conditioning Ductwork

- SABS 1424	Filters Used in Air Conditioning and General Ventilation

- ASHRAE 55	Thermal Environment Condition for Human Occupancy

- ASHRAE 15	Safety Codes for Mechanical Refrigeration

    - Wet Services System STANDARDS

- SANS 10252-1: Water supply and drainage for buildings Part 1: Water supply installations for buildings

- SANS 10252-2: Water supply and drainage for buildings Part 2: Drainage installations for buildings

- SANS 241: Drinking water

    - Electrical and Auxiliary Power System STANDARDS

- SANS Code of Practice 10142-1 for the Wiring of Premises (SABS 0142).

- SANS Code of Practice 10313: Protection of Structures against Lightning.

- SANS Code of Practice 10114-1 Interior Lighting.

- SANS Code of Practice 10114-2 Emergency Lighting.

- SANS Code of Practice 10098 – 1 Public Lighting

- SANS Code of Practice 1507-3 Low Voltage Cables.

- SANS Code of Practice 1473 – 1 & 1765 Distribution Boards.

- All other relevant and applicable IEC/SANS (SABS) Codes.

- The National Building Regulations.

- The local Municipal By-laws and Regulations as well as the Regulations of the local Supply Authority.

- The local Supply Authority Specifications and Regulations

- SANS 10142: The Wiring of Premises - Governs electrical installations in South Africa, ensuring compliance with safety, design, and installation requirements.

- Occupational Health and Safety Act (OHS Act, Act 85 of 1993): Provides the legal framework for workplace safety, including electrical safety, risk management, and safe working practices.

- SANS 1475: Fire Protection Systems - Relevant for ensuring electrical installations do not compromise fire safety and that emergency lighting and systems are compliant.

- SANS 1186 – Symbolic Safety Signs: Ensures proper signage for electrical rooms, UPS systems, and emergency exits.

- SANS 10114 – Interior Lighting: Specifies requirements for lighting design, illumination levels, and energy efficiency.

- ISO 9001 – Quality Management Systems: Often applied to ensure consistent quality assurance and documentation in project delivery.

- Environmental Regulations (NEMA – National Environmental Management Act)	Guides responsible disposal of electrical waste, batteries, and luminaires, ensuring environmental compliance.

    - Public Address (PA) System

- SANS/ISO 7240 Part 19 Design, installation, commissioning and service of sound systems for emergency purposes.

- SANS/EN54 7240 Part 16 Sound system control and indicating equipment.

- EN54 Part 4 (EN54-4) - Voice Alarm Power Supply Equipment.

- EN54 Part 16 (EN54-16) - Voice Alarm and Indicating equipment.

- EN54 Part 24 (EN54-24) - Voice Alarm Loudspeakers.

- 240-64720986 Emergency Preparedness Public Address System Standard.

- Speakers may also conform to ISO 7240-24 and / or BS-5839-8 standards.

- All modems, routers, switches, patch panels, and external media inputs shall be ICASA approved.

    - Fire Detection System (FDS) and Gas Suppression System

- SANS 10139 Code of practice for design, installation, commissioning and maintenance of fire detection and alarm systems n non-domestic premises.

- SANS 14520 Gaseous fire-extinguishing systems – Physical properties and system design

    - Building Management System (BMS)

- ISO/IEC 27001 Information Security (Applicable if IoT connectivity)

- National Building Regulations and Building Standards Act No. 103 of 1977

- SANS 10400 The application of the National Building Regulations. All Parts

    - Digital Addressable Lighting Interface (DALI)

- IEC 62386 Part 101, General Requirements

- IEC 62386 Part 102, Control Gear

- IEC 62386 Part 103, Control Device

- ISO 50001, Energy efficiency targets

    - Other

- 240-129014618 Generation Cyber Security Compliance Guideline

- 32-273 Information Security IT/OT Remote Access Standard

- 240-55410927 Cyber Security Standard for Operational Technology

- 240-79669677 Demilitarised Zone (DMZ) Designs for Operational Technology

- 240-60725641 Specification for Standard (19-inch) Equipment Cabinets

# List of drawings

    - Documentation issued by the Employer

Documentation and drawings pertaining to the building designs will be received from others as the designs for the refurbishment project is forthcoming.

| Document number | Revision | Title |
| --- | --- | --- |
| Architectural/Planning Layout |  |  |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Executive Suite |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Demolition Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Ceiling Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building General Interior Building, Safety, Accessibility, Branding and Informational Signage |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Eighth Floor – As-Built |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Demolition Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Floor Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Furniture Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Floor Finishes Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Ceiling Layout |
| Control and Instrumentation Drawings |  |  |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Fire Detection Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Security and Access Control Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Public Address and Voice Evacuation System Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building CCTV Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Boardroom Audio Visual System Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Telecom/Internet/LAN Layout |
| Mechanical Drawings |  |  |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building HVAC Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building HVAC split units’ Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Fire Protection Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Fire Protection – Gaseous Systems for the server rooms Layout |
| Electrical Drawings |  |  |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Power Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Lighting Layout |
| To be provided during construction phase | 0 | 8th Floor Executive Suite at Thibault Square Building Power Backup Layout |

# C3.2	Contractor’s Works Information

This section of the Works Information will always be contract specific depending on the nature of the works. It is most likely to be required for design and construct contracts where the tendering contractor will have proposed specifications and schedules for items of Plant and Materials and workmanship, which once accepted by the Employer prior to award of contract now become obligations of the Contractor per core clause 20.1. Typical sub headings could be a) Contractor’s design b) Plant and Materials specifications and schedules c) Other

This section could also be compiled as a separate file.

# Part 4: Site Information

| Document reference | Title | No of pages |
| --- | --- | --- |
|  | This cover page | 1 |
| C4 | Site Information |  |
|  | Total number of pages |  |

# Part 4: Site Information

Core clause 11.2(16) states

“Site Information is information which

describes the Site and its surroundings and

is in the documents which the Contract Data states it is in.”

In Contract Data, reference has been made to this Part 4 of the contract for the location of Site Information.

# General description

Thibault Square Building is a prominent high-rise commercial office facility located in the Cape Town Central Business District (CBD), at the intersection of Long Street, Riebeek Street and Hans Strijdom Avenue. The building forms part of the iconic Thibault Square precinct and is one of Cape Town’s landmark commercial developments, providing strategic access to Parliament, government departments, financial institutions and key business centres. The building was originally completed in the early 1970s and remains one of the city’s most recognizable commercial towers.

The facility accommodates a mix of commercial tenants and executive office suites, including Eskom’s Executive Office accommodation on the 8th Floor. The building comprises multiple levels of office space supported by centralized building services and operational infrastructure. The facility includes:

- Executive and administrative office suites accommodating management, operational and support personnel.

- Meeting and boardroom facilities designed to support executive engagements, governance activities and stakeholder interactions.

- Reception and visitor management areas with controlled access arrangements and security monitoring systems.

- Staff support facilities including kitchens, ablutions, printer rooms, storage areas and ancillary service spaces.

- Building service infrastructure supporting power distribution, telecommunications, HVAC systems and life-safety installations.

- Centralized vertical transportation systems, emergency escape routes and shared building common areas serving all tenant floors.

- Dedicated backup power infrastructure connected to building generators and UPS-supported critical loads to improve operational continuity during utility interruptions.

The building design incorporates robust commercial high-rise construction standards and is supported by a range of building services aimed at maintaining tenant comfort, safety and operational resilience. The facility is equipped with:

- A Building Management System (BMS) incorporating Johnson Controls and Alerton field-control infrastructure for monitoring and management of building services.

- Integrated HVAC systems providing environmental control and occupant comfort throughout the facility.

- Fire protection systems including automatic sprinklers, fire hydrants, hose reels, fire extinguishers, smoke detection and alarm systems connected to the building fire infrastructure.

- Public Address and Voice Evacuation systems to support emergency communications and occupant evacuation procedures.

- CCTV surveillance, security monitoring and controlled access arrangements to enhance tenant and visitor safety.

- Emergency and backup electrical systems incorporating generator-supported services and UPS-connected critical equipment.

- Telecommunications and network infrastructure supporting modern business and executive operations.

Thibault Square Building serves as a strategically located corporate and executive office facility within Cape Town’s administrative and business district. For Eskom, the facility provides executive accommodation and support infrastructure in close proximity to Parliament and key governmental stakeholders. The building continues to undergo refurbishment and modernization initiatives to improve accessibility, security, sustainability, operational efficiency and compliance with current occupational health and safety, building, and accessibility standards.

# Subsoil information

No Available information

# Hidden services

As Built information is unavailable therefore the contractor will need to conduct tests / survey for hidden services to prevent clashes where required.

# Other reports and publicly available information

N/A

This total is required by the Employer for budgeting purposes only.  Actual amounts due will be assessed in terms of the conditions of contract.