Eskom Holdings SOC Ltd

Contract No. _________

project or contract title




	[image: image1.jpg]R Eskom






NEC3 Term Service Contract (TSC3)
	Between


	ESKOM HOLDINGS SOC Ltd 

(Reg No. 2002/015527/30)

	and


	[Insert at award stage]

(Reg No. ___________ )

	for


	Provision of Technical Facilities Management Services to Eskom ERIC Estate (ERE) Eskom Research and Innovation Centre (ERIC)
Insert title of the service

	
	

	Contents:


	
	No of pages

	Part C1
	Agreements & Contract Data
	[●]

	Part C2
	Pricing Data
	[●]

	Part C3
	Scope of Work
	[●]

	
	
	

	CONTRACT No.
	[Insert at award stage]

	
	

	
	

	
	


PART C1:
AGREEMENTS & CONTRACT DATA

	Contents:


	
	No of pages

	C1.1
	Form of Offer and Acceptance 

[to be inserted from Returnable Documents at award stage]
	[●]

	C1.2a
	Contract Data provided by the Employer
	[●]

	C1.2b
	Contract Data provided by the Contractor.
[to be inserted from Returnable Documents at award stage]
	[●]

	C1.3
	Proforma Guarantees
	[●]


C1.1 Form of Offer & Acceptance

Offer

The Employer, identified in the Acceptance signature block, has solicited offers to enter into a contract for the procurement of:

Provision of Technical Facilities Management Services to Eskom Eskom Research and Innovation Centre (ERIC). 
The tenderer, identified in the Offer signature block, has examined the documents listed in the Tender Data and addenda thereto and by submitting this Offer has accepted the Conditions of Tender.

By the representative of the tenderer, deemed to be duly authorised, signing this part of this Form of Offer and Acceptance the tenderer offers to perform all of the obligations and liabilities of the Contractor under the contract including compliance with all its terms and conditions according to their true intent and meaning for an amount to be determined in accordance with the conditions of contract identified in the Contract Data. 

Delete the row for the Options which do not apply

	Options A or C
	The offered total of the Prices exclusive of VAT is 
	

	
	Value Added Tax @ 15% is
	

	
	The offered total of the amount due inclusive of VAT is

	

	
	


This Offer may be accepted by the Employer by signing the Acceptance part of this Form of Offer and Acceptance and returning one copy of this document including the Schedule of Deviations (if any) to the tenderer before the end of the period of validity stated in the Tender Data, or other period as agreed, whereupon the tenderer becomes the party named as the Contractor in the conditions of contract identified in the Contract Data.

	Signature(s)


	
	
	

	Name(s)


	
	
	

	Capacity


	
	
	

	For the tenderer:

	

	Name & signature of witness
	(Insert name and address of organisation)
	
	Date
	

	Tenderer’s CIDB registration number: 
	


Acceptance

By signing this part of this Form of Offer and Acceptance, the Employer identified below accepts the tenderer’s Offer.  In consideration thereof, the Employer shall pay the Contractor the amount due in accordance with the conditions of contract identified in the Contract Data.  Acceptance of the tenderer’s Offer shall form an agreement between the Employer and the tenderer upon the terms and conditions contained in this agreement and in the contract that is the subject of this agreement.

The terms of the contract, are contained in: 

Part C1

Agreements and Contract Data, (which includes this Form of Offer and Acceptance)

Part C2

Pricing Data

Part C3

Scope of Work: Service Information

and drawings and documents (or parts thereof), which may be incorporated by reference into the above listed Parts.

Deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Returnable Schedules as well as any changes to the terms of the Offer agreed by the tenderer and the Employer during this process of offer and acceptance, are contained in the Schedule of Deviations attached to and forming part of this Form of Offer and Acceptance.  No amendments to or deviations from said documents are valid unless contained in this Schedule.

The tenderer shall within two weeks of receiving a completed copy of this agreement, including the Schedule of Deviations (if any), contact the Employer’s agent (whose details are given in the Contract Data) to arrange the delivery of any securities, bonds, guarantees, proof of insurance and any other documentation to be provided in terms of the conditions of contract identified in the Contract Data at, or just after, the date this agreement comes into effect.  Failure to fulfil any of these obligations in accordance with those terms shall constitute a repudiation of this agreement.

Notwithstanding anything contained herein, this agreement comes into effect on the date when the tenderer receives one fully completed and signed original copy of this document, including the Schedule of Deviations (if any).  

	Signature(s)


	
	
	

	Name(s)
	
	
	

	Capacity


	
	
	

	for the Employer


	

	Name & signature of witness
	(Insert name and address of organisation)
	
	Date
	


Note: If a tenderer wishes to submit alternative tenders, use another copy of this Form of Offer and Acceptance.

Schedule of Deviations to be completed by the Employer prior to contract award

Note:

1.  This part of the Offer & Acceptance would not be required if the contract has been developed by negotiation between the Parties and is not the result of a process of competitive tendering.
2. The extent of deviations from the tender documents issued by the Employer prior to the tender closing date is limited to those permitted in terms of the Conditions of Tender.

3. A tenderer’s covering letter must not be included in the final contract document.  Should any matter in such letter, which constitutes a deviation as aforesaid be the subject of agreement reached during the process of Offer and Acceptance, the outcome of such agreement shall be recorded here and the final draft of the contract documents shall be revised to incorporate the effect of it.

	No.
	Subject
	Details

	1
	N/A
	

	
	
	


By the duly authorised representatives signing this Schedule of Deviations below, the Employer and the tenderer agree to and accept this Schedule of Deviations as the only deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules, as well as any confirmation, clarification or changes to the terms of the Offer agreed by the tenderer and the Employer during this process of Offer and Acceptance.  

It is expressly agreed that no other matter whether in writing, oral communication or implied during the period between the issue of the tender documents and the receipt by the tenderer of a completed signed copy of this Form shall have any meaning or effect in the contract between the parties arising from this Agreement. 

	
	For the tenderer:


	
	For the Employer



	Signature


	
	
	

	Name
	
	
	

	Capacity


	
	
	

	On behalf of
	(Insert name and address of organisation)


	
	(Insert name and address of organisation)



	Name & signature of witness
	
	
	

	Date
	
	
	


C1.2 TSC3 Contract Data

Part one - Data provided by the Employer.
	`Clause
	Statement
	Data

	1
	General
	

	
	The conditions of contract are the core clauses and the clauses for main Option: 
	

	
	
	A:

Priced contract with price list

	
	dispute resolution Option
	W1:
Dispute resolution procedure

	
	and secondary Options
	

	
	
	X1:

Price adjustment for inflation

	
	
	X2

Changes in the law

	
	
	X17:
Low service damages

	
	
	X18:
Limitation of liability

	
	
	X19:
Task Order

	
	
	Z:

Additional conditions of contract

	
	of the NEC3 Term Service Contract April 2013
 (TSC3)
	If 2005 Edition is to be used delete “April 2013” and replace with “June 2005 with amendments June 2006”. Always delete this note before finalising this Data

	10.1
	The Employer is (name):
	Eskom Holdings SOC Ltd (reg no: 2002/015527/30), a state-owned company incorporated in terms of the company laws of the Republic of South Africa

	
	Address
	Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg

	
	Tel No.
	011 800 800

	10.1
	The Service Manager is (name): 
	Likotsi Matlali

	
	Address
	Lower Germiston Road, Johannesburg

	
	Tel
	011 800 3332

	
	e-mail
	matlalLP@eskom.co.za

	11.2(2)
	The Affected Property is
	Eskom Research and Innovation Centre

	11.2(13)
	The service is 
	Provision of Technical Facilities Management Services to  Eskom Research and Innovation Centre (ERIC).


	11.2(14)
	The following matters will be included in the Risk Register
	Refer to the Risk Register

	11.2(15)
	The Service Information is in 
	Part 3: Scope of Work and all documents and drawings to which it refers.

	12.2
	The law of the contract is the law of 
	the Republic of South Africa

	13.1
	The language of this contract is 
	English

	13.3
	The period for reply is
	1 week

	2
	The Contractor’s main responsibilities
	Data required by this section of the core clauses is also provided by the Contractor in Part 2 and terms in italics used in this section are identified elsewhere in this Contract Data

	21.1
	The Contractor submits a first plan for acceptance within
	2 weeks of the Contract Date

	3
	Time
	

	30.1
	The starting date is.
	01 April 2024

	30.1
	The service period is
	31 March 2029

	4
	Testing and defects
	There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data

	5
	Payment
	

	50.1
	The assessment interval is 
	between the 15th day of each successive month.

	51.1
	The currency of this contract is the 
	South African Rand

	51.2
	The period within which payments are made is
	8 weeks.

	51.4
	The interest rate is 


	the publicly quoted prime rate of interest (calculated on a 365 day year) charged by from time to time by the Standard Bank of South Africa Limited (as certified, in the event of any dispute, by any manager of such bank, whose appointment it shall not be necessary to prove) for amounts due in Rands and 

(ii) the LIBOR rate applicable at the time for amounts due in other currencies.  LIBOR is the 6 month London Interbank Offered Rate quoted under the caption “Money Rates” in The Wall Street Journal for the applicable currency or if no rate is quoted for the currency in question then the rate for United States Dollars, and  if no such rate appears in The Wall Street Journal then the rate as quoted by the Reuters Monitor Money Rates Service (or such service as may replace the Reuters Monitor Money Rates Service) on the due date for the payment in question, adjusted mutatis mutandis every 6 months thereafter (and as certified, in the event of any dispute, by any manager employed in the foreign exchange department of The Standard Bank of South Africa Limited, whose appointment it shall not be necessary to prove.

	6
	Compensation events
	There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data

	7
	Use of Equipment Plant and Materials
	There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data

	8
	Risks and insurance
	

	80.1
	These are additional Employer's risks  
	1. None

	9
	Termination
	There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data.

	10
	Data for main Option clause
	

	A
	Priced contract with price list
	

	20.5
	The Contractor prepares forecasts of the final total of the Prices for the whole of the service at intervals no longer than 
	2 weeks.

	11
	Data for Option W1
	

	W1.1
	The Adjudicator 
	the person selected from the ICE-SA Division (or its successor body) of the South African Institution of Civil Engineering Panel of Adjudicators by the Party intending to refer a dispute to him.  (see www.ice-sa.org.za). If the Parties do not agree on an Adjudicator the Adjudicator will be appointed by the Arbitration Foundation of Southern Africa (AFSA).

	W1.2(3)
	The Adjudicator nominating body is: 
	the Chairman of ICE-SA a joint Division of the South African Institution of Civil Engineering and the Institution of Civil Engineers (London) (see www.ice-sa.org.za ) or its successor body.

	W1.4(2)
	The tribunal is: 
	Arbitration

	W1.4(5)
	The arbitration procedure is 
	the latest edition of Rules for the Conduct of Arbitrations published by The Association of Arbitrators (Southern Africa) or its successor body.

	
	The place where arbitration is to be held is
	South Africa

	
	The person or organisation who will choose an arbitrator. 

· if the Parties cannot agree a choice or
· if the arbitration procedure does not state who selects an arbitrator, is
	the Chairman for the time being or his nominee of the Association of Arbitrators (Southern Africa) or its successor body.

	12
	Data for secondary Option clauses
	

	X1
	Price adjustment for inflation
	

	X1.1
	The base date for indices is 
	[●]. A month after the anniversary of the contract

	
	The proportions used to calculate the Price Adjustment Factor are:
	proportion
	linked to index for
	Index prepared by

	
	
	85%
	Other cost 
	SEIFSA D3

	
	
	15%
	labour
	

	
	
	1.00


	
	

	X2
	Changes in the law
	There is no reference to Contract Data in this Option and terms in italics are identified elsewhere in this Contract Data.

	X18
	Limitation of liability
	

	X18.1
	The Contractor’s liability to the Employer for indirect or consequential loss is limited to
	R0.0 (zero Rand)

	X18.2
	For any one event, the Contractor’s liability to the Employer for loss of or damage to the Employer’s property is limited to
	the amount of the deductibles relevant to the event 

	X18.3
	The Contractor’s liability for Defects due to his design of an item of Equipment is limited to
	The greater of 

· the total of the Prices at the Contract Date

and 

· the amounts excluded and unrecoverable from the Employer’s insurance (other than the resulting physical damage to the Employer’s property which is not excluded) plus the applicable deductibles

	X18.4
	The Contractor’s total liability to the Employer, for all matters arising under or in connection with this contract, other than the excluded matters, is limited to
	the total of the Prices other than for the additional excluded matters.
The Contractor’s total liability for the additional excluded matters is not limited. 

The additional excluded matters are amounts for which the Contractor is liable under this contract for
· Defects due to his design, plan and specification,
· Defects due to manufacture and fabrication outside the Affected Property, 

· loss of or damage to property (other than the Employer’s property, Plant and Materials),

· death of or injury to a person and
· infringement of an intellectual property right.

	X18.5
	The end of liability date is 
	6 months after the end of the service period.

	X19
	Task Order
	

	X19.5
	The Contractor submits a Task Order programme to the Service Manager within 
	2 days of receiving the Task Order

	Z
	The additional conditions of contract are
	Z1 to Z14 always apply.

	
	

	Z1
	Cession delegation and assignment

	Z1.1
	The Contractor does not cede, delegate or assign any of its rights or obligations to any person without the written consent of the Employer.

	Z1.2
	Notwithstanding the above, the Employer may on written notice to the Contractor cede and delegate its rights and obligations under this contract to any of its subsidiaries or any of its present divisions or operations which may be converted into separate legal entities as a result of the restructuring of the Electricity Supply Industry. 

	
	

	Z2
	Joint ventures

	Z2.1
	If the Contractor constitutes a joint venture, consortium or other unincorporated grouping of two or more persons or organisations then these persons or organisations are deemed to be jointly and severally liable to the Employer for the performance of this contract.

	Z2.2
	Unless already notified to the Employer, the persons or organisations notify the Service Manager within two weeks of the Contract Date of the key person who has the authority to bind the Contractor on their behalf.

	Z2.3
	The Contractor does not alter the composition of the joint venture, consortium or other unincorporated grouping of two or more persons without the consent of the Employer having been given to the Contractor in writing.

	
	

	Z3
	Change of Broad Based Black Economic Empowerment (B-BBEE) status

	Z3.1
	Where a change in the Contractor’s legal status, ownership or any other change to his business composition results in a change to the Contractor’s B-BBEE status, the Contractor notifies the Employer within seven days of the change.

	Z3.2
	The Contractor is required to submit an updated verification certificate and necessary supporting documentation confirming the change in his B-BBEE status to the Service Manager within thirty days of the notification or as otherwise instructed by the Service Manager.

	Z3.3
	Where, as a result, the Contractor’s B-BBEE status has decreased since the Contract Date the Employer may either re-negotiate this contract or alternatively, terminate the Contractor’s obligation to Provide the Service.

	Z3.4
	Failure by the Contractor to notify the Employer of a change in its B-BBEE status may constitute a reason for termination. If the Employer terminates in terms of this clause, the procedures on termination are P1, P2 and P4 as stated in clause 92, and the amount due is A1 and A3 as stated in clause 93.


	
	

	Z4
	Confidentiality

	Z4.1
	The Contractor does not disclose or make any information arising from or in connection with this contract available to Others. This undertaking does not, however, apply to information which at the time of disclosure or thereafter, without default on the part of the Contractor, enters the public domain or to information which was already in the possession of the Contractor at the time of disclosure (evidenced by written records in existence at that time).  Should the Contractor disclose information to Others in terms of clause 25.1, the Contractor ensures that the provisions of this clause are complied with by the recipient.

	Z4.2
	If the Contractor is uncertain about whether any such information is confidential, it is to be regarded as such until notified otherwise by the Service Manager.

	Z4.3
	In the event that the Contractor is, at any time, required by law to disclose any such information which is required to be kept confidential, the Contractor, to the extent permitted by law prior to disclosure, notifies the Employer so that an appropriate protection order and/or any other action can be taken if possible, prior to any disclosure.  In the event that such protective order is not, or cannot, be obtained, then the Contractor may disclose that portion of the information which it is required to be disclosed by law and uses reasonable efforts to obtain assurances that confidential treatment will be afforded to the information so disclosed.

	Z4.4
	The taking of images (whether photographs, video footage or otherwise) of the Affected Property or any portion thereof, in the course of Providing the Service and after the end of the service period, requires the prior written consent of the Service Manager.  All rights in and to all such images vests exclusively in the Employer.  

	Z4.5
	The Contractor ensures that all his subcontractors abide by the undertakings in this clause.

	
	

	Z5
	Waiver and estoppel: Add to core clause 12.3:

	Z5.1
	Any extension, concession, waiver or relaxation of any action stated in this contract by the Parties, the Service Manager or the Adjudicator does not constitute a waiver of rights and does not give rise to an estoppel unless the Parties agree otherwise and confirm such agreement in writing.

	
	

	Z6
	Health, safety and the environment:  Add to core clause 27.4

	Z6.1
	The Contractor undertakes to take all reasonable precautions to maintain the health and safety of persons in and about the execution of the service. Without limitation the Contractor:

· accepts that the Employer may appoint him as the “Principal Contractor” (as defined and provided for under the Construction Regulations 2014 (promulgated under the Occupational Health & Safety Act 85 of 1993) (“the Construction Regulations”) for the Affected Property.
· warrants that the total of the Prices as at the Contract Date includes enough for proper compliance with the Construction Regulations, all applicable health & safety laws and regulations and the health and safety rules, guidelines and procedures provided for in this contract and generally for the proper maintenance of health & safety in and about the execution of the service; and

· undertakes, in and about the execution of the service, to comply with the Construction Regulations and with all applicable health & safety laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing.

	Z6.2
	The Contractor, in and about the execution of the service, complies with all applicable environmental laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing.

	
	

	Z7
	Provision of a Tax Invoice and interest.  Add to core clause 51

	Z7.1
	Within one week of receiving a payment certificate from the Service Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice in accordance with the Employer's procedures stated in the Service Information, showing the amount due for payment equal to that stated in the payment certificate.

	Z7.2
	If the Contractor does not provide a tax invoice in the form and by the time required by this contract, the time by when the Employer is to make a payment is extended by a period equal in time to the delayed submission of the correct tax invoice.  Interest due by the Employer in terms of core clause 51.2 is then calculated from the delayed date by when payment is to be made.

	Z7.3
	The Contractor (if registered in South Africa in terms of the companies Act) is required to comply with the requirements of the Value Added Tax Act, no 89 of 1991 (as amended) and to include the Employer’s VAT number 4740101508 on each invoice he submits for payment.

	
	

	Z8
	Notifying compensation events

	Z8.1
	Delete the last paragraph of core clause 61.3 and replace with:

If the Contractor does not notify a compensation event within eight weeks of becoming aware of the event, he is not entitled to a change in the Prices.

	
	

	Z9
	Employer’s limitation of liability

	Z9.1
	The Employer’s liability to the Contractor for the Contractor’s indirect or consequential loss is limited to R0.00 (zero Rand)

	Z9.2
	The Contractor’s entitlement under the indemnity in 82.1 is provided for in 60.1(12) and the Employer’s liability under the indemnity is limited to compensation as provided for in core clause 63 and X19.11 if Option X19 Task Order applies to this contract. 

	
	

	Z10
	Termination: Add to core clause 91.1, at the second main bullet point, fourth sub-bullet point, after the words "against it":  

	Z10.1
	   or had a business rescue order granted against it.

	
	

	Z11
	Ethics

	For the purposes of this Z-clause, the following definitions apply:

	Affected Party
	means, as the context requires, any party, irrespective of whether it is the Contractor or a third party, such party’s employees, agents, or Subcontractors or Subcontractor’s employees, or any one or more of all of these parties’ relatives or friends,

	Coercive Action
	means to harm or threaten to harm, directly or indirectly, an Affected Party or the property of an Affected Party, or to otherwise influence or attempt to influence an Affected Party to act unlawfully or illegally,

	Collusive Action
	means where two or more parties co-operate to achieve an unlawful or illegal purpose, including to influence an Affected Party to act unlawfully or illegally,

	Committing Party
	means, as the context requires, the Contractor, or any member thereof in the case of a joint venture, or its employees, agents, or Subcontractors or the Subcontractor’s employees,

	Corrupt Action
	means the offering, giving, taking, or soliciting, directly or indirectly, of a good or service to influence the actions of an Affected Party unlawfully or illegally,

	Fraudulent Action
	means any unlawfully or illegally intentional act or omission that misleads, or attempts to mislead, an Affected Party, to obtain a financial or other benefit or to avoid an obligation or incurring an obligation,

	Obstructive Action
	means a Committing Party unlawfully or illegally destroying, falsifying, altering or making false statements to materially impede an investigation into allegations of Prohibited Action, and

	Prohibited Action
	means any one or more of a Coercive Action, Collusive Action Corrupt Action, Fraudulent Action, or Obstructive Action.

	Z11.1
	A Committing Party may not take any Prohibited Action during the procurement of this contract or in execution thereof.

	Z11.2
	The Employer may terminate the Contractor’s obligation to Provide the Services if a Committing Party has taken such Prohibited Action and the Contractor did not take timely and appropriate action to prevent or remedy the situation, without limiting any other rights or remedies the Employer has. It is not required that the Committing Party had to have been found guilty, in court or in any other similar process, of such Prohibited Action before the Employer can terminate the Contractor’s obligation to Provide the Services for this reason.

	Z11.3
	If the Employer terminates the Contractor’s obligation to Provide the Services for this reason, the amounts due on termination are those intended in core clauses 92.1 and 92.2.

	Z11.4
	A Committing Party co-operates fully with any investigation pursuant to alleged Prohibited Action. Where the Employer does not have a contractual bond with the Committing Party, the Contractor ensures that the Committing Party co-operates fully with an investigation.


Z12

Insurance
Z _12_.1
Replace core clause 83 with the following:
	Insurance cover
	83
	

	
	83.1
	When requested by a Party, the other Party provides certificates from his insurer or broker stating that the insurances required by this contract are in force.



	
	83.2
	The Contractor provides the insurances stated in the Insurance Table A from the starting date until the earlier of Completion and the date of the termination certificate. 
INSURANCE TABLE A
Insurance against
Minimum amount of cover or minimum limit of indemnity
Loss of or damage caused by the Contractor to the Employer’s property
The replacement cost where not covered by the Employer’s insurance.

The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance.
Loss of or damage to Plant and Materials
The replacement cost where not covered by the Employer’s insurance.

The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance.
Loss of or damage to Equipment
The replacement cost where not covered by the Employer’s insurance.

The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance.
The Contractor’s liability for loss of or damage to property (except the Employer’s property, Plant and Materials and Equipment) and liability for bodily injury to or death of a person (not an employee of the Contractor) arising from or in connection with the Contractor’s Providing the Service
Loss of or damage to property

The replacement cost.
Bodily injury to or death of a person

The amount required by the applicable law.

Liability for death of or bodily injury to employees of the Contractor arising out of and in the course of their employment in connection with this contract
The amount required by the applicable law



	
	
	

	
	
	


Z __12.2
Replace core clause 86 with the following:

	Insurance by the Employer
	86
	

	
	86.1
	The Employer provides the insurances stated in the Insurance Table B

	
	
	

	
	
	INSURANCE TABLE B
Insurance against or name of policy

Minimum amount of cover or minimum limit of indemnity

Assets All Risk

Per the insurance policy document

Contract Works insurance

Per the insurance policy document

Environmental Liability

Per the insurance policy document

General and Public Liability

Per the insurance policy document

Transportation (Marine)

Per the insurance policy document

Motor Fleet and Mobile Plant

Per the insurance policy document

Terrorism

Per the insurance policy document

Cyber Liability

Per the insurance policy document

Nuclear Material Damage and Business Interruption

Per the insurance policy document

Nuclear Material Damage Terrorism

Per the insurance policy document




	Z13
	Nuclear Liability

	Z13.1
	The Employer is the operator of the Koeberg Nuclear Power Station (KNPS), a nuclear installation, as designated by the National Nuclear Regulator of the Republic of South Africa and is the holder of a nuclear licence in respect of the KNPS.

	Z13.2
	The Employer is solely responsible for and indemnifies the Contractor or any other person against any and all liabilities which the Contractor or any person may incur arising out of or resulting from nuclear damage, as defined in Act 47 of 1999, save to the extent that any liabilities are incurred due to the unlawful intent of the Contractor or any other person or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS site, without the permission of the Employer or of a person acting on behalf of the Employer.

	Z13.3
	Subject to clause Z13.4 below, the Employer waives all rights of recourse, arising from the aforesaid, save to the extent that any claims arise or liability is incurred due or attributable to the unlawful intent of the Contractor or any other person, or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS site, without the permission of the Employer or of a person acting on behalf of the Employer.

	Z13.4
	The Employer does not waive its rights provided for in section 30 (7) of Act 47 of 1999, or any replacement section with the same subject matter.

	Z13.5
	The protection afforded by the provisions hereof shall be in effect until the KNPS is decommissioned.

	
	

	Z14.1
	The Employer ensures that the Ambient Air in the area where the Contractor will Provide the Services conforms to the acceptable prescribed South African standard for asbestos, as per the regulations published in GNR 155 of 10 February 2002, under the Occupational health and Safety Act, 1993 (Act 85 of 1993) (“Asbestos Regulations”). The OEL for asbestos is 0.2 regulated asbestos fibres per millilitre of air as a 4-hour TWA, averaged over any continuous period of four hours, and the short-term exposure limit of 0.6 regulated asbestos fibres per millilitre of air as a 10-minute TWA, averaged over any 10 minutes, measured in accordance with HSG248 and monitored according to HSG173 and OESSM.

	Z14.2
	Upon written request by the Contractor, the Employer certifies that these conditions prevail. All measurements and reporting are affected by an independent, competent, and certified occupational hygiene inspection body, i.e., a SANAS accredited, and Department of Employment and Labour approved AAIA. The Contractor may perform Parallel Measurements and related control measures at the Contractor’s expense. For the purposes of compliance, the results generated from Parallel Measurements are evaluated only against South African statutory limits as detailed in clause Z14.1. Control measures conform to the requirements stipulated in the AAIA-approved asbestos work plan.

	Z14.3
	The Employer manages asbestos and ACM according to the Standard.

	Z14.4
	In the event that any asbestos is identified while Providing the Services, a risk assessment is conducted and if so required, with reference to possible exposure to an airborne concentration of above the AL for asbestos, immediate control measures are implemented, and relevant air monitoring conducted in order to declare the area safe.

	Z14.5
	The Contractor’s personnel are entitled to stop working and leave the contaminated area forthwith until such time that the area of concern is declared safe by either Compliance Monitoring or an AAIA approved control measure intervention, for example, per the emergency asbestos work plan, if applicable.

	Z14.6
	The Contractor continues to Provide the Services, without additional control measures presented, on presentation of Safe Levels. The contractually agreed dates to Provide the Services, including the Completion Date, are adjusted accordingly. The contractually agreed dates are extended by the notification periods required by regulations 3 and 21 of the Asbestos Regulations, 2001.

	Z14.7
	Any removal and disposal of asbestos, asbestos containing materials and waste, is done by a registered asbestos contractor, instructed by the Employer at the Employer’s expense, and conducted in line with South African legislation.


SDL&I Penalty and Performance Security

Eskom will apply a penalty of 2.5% of the Contract Value for failure to meet SDL&I obligations. The following shall apply for SDL&I performance security:


For the duration of the contract, Eskom will retain 2.5% of every invoice (excluding VAT) as security for the fulfilment of all SDL&I Obligations. The retained amounts shall only be released to the Contractor upon fulfilment of all SDL&I obligations at the end of the contract.

C1.2 Contract Data

Part two - Data provided by the Contractor.
	Clause
	Statement
	Data

	10.1
	The Contractor is (Name):
	     

	
	Address
	     

	
	Tel No.
	     

	
	Fax No.
	     

	11.2(8)
	The direct fee percentage is
	     %

	
	The subcontracted fee percentage is
	     %

	11.2(14)
	The following matters will be included in the Risk Register
	     

	11.2(15)
	The Service Information for the Contractor’s plan is in:
	     

	21.1
	The plan identified in the Contract Data is contained in:
	     

	24.1
	The key people are:
	

	
	1

Name:
	     

	
	

Job:
	     

	
	

Responsibilities:
	     

	
	

Qualifications:
	     

	
	

Experience:
	     

	
	2

Name:
	     

	
	

Job
	     

	
	

Responsibilities:
	     

	
	

Qualifications:
	     

	
	

Experience:
	     

	
	
	     

	
	
	CV's (and further key person's data including CVs) are in      .

	A
	Priced contract with price list
	

	11.2(12)
	The price list is in
	     

	11.2(19)
	The tendered total of the Prices is
	R     


Part 2: Pricing Data

TSC3 Option A

	Document reference
	Title
	No of pages

	C2.1
	Pricing assumptions: Option A
	2

	C2.2
	The price list 
	[●]


C2.1 Pricing assumptions: Option A

How work is priced and assessed for payment

Clause 11 in NEC3 Term Service Contract (TSC3) core clauses and Option A states:

	Identified and defined terms
	11

11.2
	(12) The Price List is the price list unless later changed in accordance with this contract.



	
	
	(17) The Price for Services Provided to Date is the total of 

· the Price for each lump sum item in the Price List which the Contractor has completed and
· where a quantity is stated for an item in the Price List, an amount calculated by multiplying the quantity which the Contractor has completed by the rate.


	
	
	(19) The Prices are the amounts stated in the Price column of the Price List. Where a quantity is stated for an item in the Price List, the Price is calculated by multiplying the quantity by the rate.




This confirms that Option A is a priced contract where the Prices are derived from a list of items of service which can be priced as lump sums or as expected quantities of service multiplied by a rate or a mix of both.

Function of the Price List

Clause 54.1 in Option A states: “Information in the Price List is not Service Information”.  This confirms that instructions to do work or how it is to be done are not included in the Price List but in the Service Information.  This is further confirmed by Clause 20.1 which states, “The Contractor Provides the Service in accordance with the Service Information”. Hence the Contractor does not Provide the Service in accordance with the Price List.   The Price List is only a pricing document.  

Link to the Contractor’s plan

Clause 21.4 states “The Contractor provides information which shows how each item description on the Price List relates to the operations on each plan which he submits for acceptance”.  Hence when compiling the price list, the tendering contractor needs to develop his first clause 21.2 plan in such a way that operations shown on it can be priced in the price list and result in a satisfactory cash flow in terms of clause 11.2(17). 

Preparing the price list
Before preparing the price list, both the Employer and tendering contractors should read the TSC3 Guidance Notes pages 14 and 15.  In an Option A contract, either Party may have entered items into the price list either as a process of offer and acceptance (tendering) or by negotiation depending on the nature of the service to be provided.  Alternatively, the Employer, in his Instructions to Tenderers or in a Tender Schedule, may have listed some items that he requires the Contractor to include in the price list to be prepared and priced by him. 

It is assumed that in preparing or finalising the price list the Contractor:
· Has taken account of the guidance given in the TSC3 Guidance Notes relevant to Option A.
· Understands the function of the Price List and how work is priced and paid for.
· Is aware of the need to link operations shown in his plan to items shown in the Price List.
· Has listed and priced items in the price list which are inclusive of everything necessary and incidental to Providing the Service in accordance with the Service Information, as it was at the time of tender, as well as correct any Defects not caused by an Employer’s risk.
· Has priced work he decides not to show as a separate item within the Prices or rates of other listed items in order to fulfil the obligation to complete the service for the tendered total of the Prices. 
· Understands there is no adjustment to items priced as lump sums if the amount, or quantity, of work within that item later turns out to be different to that which the Contractor estimated at time of tender. The only basis for a change to the (lump sum) Prices is as a result of a compensation event. 
Format of the price list
(From the example given in an Appendix within the TSC3 Guidance Notes)

Entries in the first four columns in the price list in section C2.2 are made either by the Employer or the tendering contractor. 

If the Contractor is to be paid an amount for the item which is not adjusted if the quantity of work in the item changes, the tendering contractor enters the amount in the Price column only, the Unit, Expected Quantity and Rate columns being left blank.

If the Contractor is to be paid an amount for an item of work which is the rate for the work multiplied by the quantity completed, the tendering contractor enters the rate which is then multiplied by the Expected Quantity to produce the Price, which is also entered.

If the Contractor is to be paid a Price for an item proportional to the length of time for which a service is provided, a unit of time is stated in the Unit column and the expected length of time (as a quantity of the stated units of time) is stated in the Expected Quantity column.

C2.2 the price list
Refer to the Bill of Quantities Attached.
	The total of the Prices
	


Part 3: Scope of Work

	Document reference
	Title
	No of pages

	
	This cover page
	1

	C3.1
	Employer’s Service Information
	36

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	Total number of pages
	37


Contents

1Part 3: Scope of Work







1
Description of the service




3
2
Management strategy and start up.



28
3
HERICth and safety, the environment and quality assurance
30
4
Procurement






31
5
Working on the Affected Property



33
6
List of drawings






35


Part 3: Scope of Work

	Document reference
	Title
	No of pages

	
	This cover page
	1

	C3.1
	Employer’s Service Information
	39

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	Total number of pages
	40


Contents

Part 3: Scope of Work

1
Description of the service

2
Management strategy and start up.

3
Health and safety, the environment and quality assurance

4
Procurement

5
Working on the Affected Property

6
List of drawings



1 Description of the service
1.1 Executive overview 
The purpose of this contract is to appoint a suitable qualified Contractor for the Provision of Facilities Management (Technical) Services to Eskom Real Estate (ERE) Eskom Research and Innovation centre (ERIC) located at Lower Germiston Road, Rosherville. Eskom Research and Innovation Centre buildings adds up to a total size of approximately 59651 m².
1.2  Scope of Work
The scope of work includes the provision of the following technical services:

	· HVAC and Mechanical Services

	· Cold Rooms, Canteen, Office Fridges repairs and microwaves repair.

	· Water Reticulation Systems

	· Sprinkler System

	· Water Treatment Services

	· Building Management System Services 

	· Civil and Plumbing Services

	· Electrical services (MV, LV equipment, Standby Power System)

· Canteen equipment repairs

	· Portable Fire Equipment 

	· Fire Protection and Gas Suppression Systems services

	· Fire Sprinkler Services

	· Audio Visual Services
· Lifting Equipment Services
· Carpentry 


The Contractor shall provide all labour, supervision, administration and management, equipment, tools, supplies and material required to perform the facilities management services specified herein.
1.3 Detailed description of the service
	1. Item
	2. Description
	3. Frequency

	1.3.1.
	Heating and Ventilation Air Conditioning System

Operations
General plant operation, BMS monitoring, temperature adjustments and minor repairs and or switching between pumps and chillers etc.
	Weekly/Monthly 

	1.3.2.
	Domestic air conditioning units (window-, console-, split units)

The basic requirement listed below must be carried out as and when required Consisting of:-

Minor service:

Check and clean filter – replace if torn or damaged 

Check and clear condensate drains to prevent internal leaks

Clean equipment in general, blow out dust from condenser with blower and observe air-conditioner operation in all its functions.
Check amperage readings on cooling/heating and fan only operation and compare to nameplate ratings

Major Service: Once per annum

Check and clean filter – replace if torn or damaged 

Check condition of evaporator coil and clean/wash. Straighten fins with fin comb where necessary

Check condition of condenser coil and clean/wash. Straighten fins with fin comb where necessary

Check condensate drip trays and treat for corrosion if necessary

Check condensate drains and clear if necessary to prevent internal leaks

Check condensate drain pumps are in order

Check fan blades to ensure they are secured to fan shafts, aligned/balanced and not damaged

Check fan motors to ensure they are running freely, bearings are fine and oil where applicable. Ensure baffle plates are secured between in and outlet air

Check compressor is operating correctly, that klixon is operating correctly and that compressor is suspended freely.

Check and eliminate vibrations

Check thermostats, switches, contactors, capacitors and wiring to ensure that all electrical connections are secure and clean(blow out dust with blower) - no burnt or hot connections and no insulation damage – repair where necessary

Check refrigerant system for leaks and repair where necessary

Clean equipment in general and observe its operation in all its functions

Check amperage readings on cooling/heating and fan only operation and compare to nameplate ratings

For split units: do the above points plus:

Check and tighten/repair all refrigerant pipe fittings

Check head and suction pressures to ensure it is according to specifications, otherwise adjust gas to required pressures

Take corrective action for all above points where necessary


	Quarterly

Annual

	1.3.3.
	Central air conditioning system
Chillers - check the following basic requirements. Services to be done by OEM.
Chillers X 3: Type: Trane Screw Chillers, Size:160KW. 

Compressor X 6 Type: Trane Screw, Size: 110 KW.
Service: Check, repair and record the following:

Safety valves and devices for correct operation and those valves are not blocked or leaking.

Ensure Chiller installations conform to all the manufacturer’s requirements.

All parameters to be checked to ensure that the installation is in a good condition.

That there is no oil, frost or humidity under insulating materials and repair insulating materials where necessary.

Check that there are no vibrations or unusual noises.



Operating temperatures and pressures on evaporators and condensers, to ensure permissible limits are not exceeded.

Evaporator pressure drop

Line and control voltages

Motor Amperages and Electrical connections.

Compressor motor windings’ resistances, between windings and to earth.

Open and check all contactors and all wiring for loose and burned connections.

Operation of all temperature safety controls (sensors).

Operation of all pressure safety controls (HP, LP and Oil differential).

Operation of all electrical safety controls (Overloads, CT’s).

Operation of the control circuitry.

Operation of the Microprocessors and programmed parameters.

Evaluate fouling conditions in the evaporators and condensers.

Oil flow and level, pressure drop across oil filter and refrigerant charge.

Check for tell-tale refrigerant leaks and test all piping and components for refrigerant leaks.

Loading and unloading of systems for correct operation.

All solenoid valves for condition (cracks, leaks, etc.) and operation.

Condition and positions of oil shut off valves.

Evaluate fouling of the oil and refrigerant filters and drier cores.

Correct chilled water flow against pressure drop chart.

Correct condensed water flow, pressure drop and control valve operation.

Correct condensed water entering and leaving temperatures.

Correct operation of chilled and condensed water flow switches.

Discharge superheat, liquid sub cooling and evaluate refrigerant charge.

Refrigerant approach temperatures in the evaporators and condensers.

Entering and leaving chilled water temperatures.

Operation of expansion valves.

Compressors start and run hours.

On completion, supply full maintenance report and log sheet for each chiller.
Service Check, repair and record the following: 

Safety valves and devices for correct operation and those valves are not blocked or leaking.

Ensure Chiller installations conform to all the manufacturer’s requirements.

All parameters to ensure that the installation is in a good condition.

Check that there is no oil, frost or humidity under insulating materials and repair insulating materials where necessary.

Check that there are no vibrations or unusual noises.


Operating temperatures and pressures on evaporators and condensers, to ensure permissible limits are not exceeded.

Evaporator pressure drop.

Line and control voltages.

Motor Amperages and Electrical connections.

Compressor motor windings’ resistances, between windings and to earth.

Open and check all contactors and all wiring for loose and burned connections.

Operation of all temperature safety controls (sensors).

Operation of all pressure safety controls (HP, LP and Oil differential).

Operation of all electrical safety controls (Overloads, CT’s).

Operation of the control circuitry.

Operation of the Microprocessors and programmed parameters.

Evaluate fouling conditions in the evaporators and condensers.

Oil flow and level, pressure drop across the oil filter and refrigerant charge.

Check for tell-tale refrigerant leaks and test all piping and components for refrigerant leaks.

Compressor loading and unloading mechanisms for correct system operation.

Compressor discharge check valve.

All solenoid valves for condition (cracks, leaks, etc.) and operation.

Condition and positions of oil shut off valves.

Evaluate fouling of the oil and refrigerant filters and drier cores.

Correct chilled water flow against pressure drop chart.

Correct condensed water flow, pressure drop and control valve operation.

Correct condensed water entering and leaving temperatures.

Correct operation of chilled and condensed water flow switches.

Discharge superheat, liquid sub cooling and evaluate refrigerant charge.

Refrigerant approach temperatures in the evaporators and condensers.

Entering and leaving chilled water temperatures.

Operation of expansion valves.

Compressors start and run hours.

Do oil analysis with spectrograph by a qualified laboratory.

Change oil if necessary, depending on report.

Change oil filters.

Change refrigerant drier cores.

Clean condenser (Chemical clean and brush.)

Clean evaporator if necessary.

Clean chilled and condensed water strainers.

Clean and repaint any areas that show signs of corrosion. 

On completion, supply full maintenance report and log sheet for each chiller.


	Monthly

Annual

	1.3.4.
	Chilled water makes up and expansion tank Plantroom 1 – size 0.8 x 0.8 x 1m.
Bi-annual Service

Check general condition of tank and pipe work for any leaks.

Check all gate valves and ball valve and repair where necessary.

Chilled water makes up and expansion tank Plantroom – size 1.2 x 1.2 x 1.2 m.
Bi-annual Service 

Check general condition of tank and pipe work for any leaks.

Check all gate valves and ball valve and repair where necessary.


	Bi-annual

	1.3.5.
	Air Handling Units 

Monthly service

Check drains and unblock. 

Cleaning of plant rooms – floors an equipment.

Motor and fan holding down bolts and spring mountings, check for tightness and security. 

Heating and cooling coils, check for physical damage and comb fins where necessary. 

Quarterly Service

Heating and cooling coils, pressure clean with approved chemical agent. 

Check and clean condensate drain pans and pipe work. 

Check and lubricate damper and vortex damper mechanisms. 
Pressure clean secondary filters. 
Annual Service

Pressure wash inside of entire unit 

Check doors ERICs and repair/replace.  

Check for corrosion and treat. 

Check all main- and re-heater-/ diffuser heater banks (approximately 200).
	Monthly/

Quarterly/

Annual

	1.3.7.
	Control Panels, (Main electrical boards in the chiller plant) 
Quarterly Service

Clean interior of enclosures

Check access doors ERICs and fittings

Bi-annual Service

Check cable ways and secure cabling, covers, etc

Check cable loops to doors for scuffing

Check contactors

Annual Service

Check all connections for tightness and repair hot connections

Check labels and terminal numbers according to drawings 

Calibrate Volt- and Ammeters

Check all CT’s and VT’s

Check overload operation and set points

Check equipment amperages

Check insulation resistance

Clean equipment

Check earth impedance

Take infrared photographs on all major panels and take corrective action

Check all circuit breakers, isolators, fuses and fuse holders, pilot lights and electrical wiring from main isolator


	Quarterly/Bi-annual/Annual

	1.3.8.
	Heat Exchangers 

6 Monthly

Check general condition for leaks

Check pressure gauges and thermometers and replace where necessary

Check, operate and grease manual valves

3 Yearly

Pressure vessel testing for statutory compliance - By Accredited Supplier


	Bi-annual/

Annual

	1.3.9.
	Pumps 

· Chiller: Primary pumps x 3. Make: Unistream SPP. 

· Chiller: Secondary pumps x 3. Make: Unistream SPP. 

· Hot water pumps x 2. Make: Unistream SPP.  

· Pressurisation chill water pumps x 2. Make: Wilo.  
· Pressurisation hot water pumps x 2. Make: Wilo.  
Check the following: By accredited pump supplier/OEM

Monthly

Noise and vibration levels, leaks and general condition

Pump and motor alignment and flexible coupling conditions

Bearing temperatures on pumps and motors and lubrication

Check all temperature and pressure gauges and replace where necessary

From above inspections advice on corrective action for bearing, shafts or flexible coupling replacements, etc.

Annually

Check, repair and grease all mechanical valves and non-return valves

Clean all pump strainers


	Monthly/Annual

	1.3.10.
	Electric motors 
Quarterly Service

Check that earthing of motor through conduit or cable armouring is secure

Check that motor terminal cover is secure

Check bearings while running and report on condition

Bi-annual Service

Blow out motor

Grease motor bearings if grease nipples are fitted

Blow out starter panel

Check motor and starter terminals for tightness and condition

Operate and check overloads where possible and check overload setting for correctness.

	Quarterly/Bi-annual

	1.3.11.
	Air-Compressors  

Monthly Service

Check compressor oil level

V-Belt wear and tension

Air-filters

Noise and vibration

Compressor cycling controls

Receiver tank relief valve operation

Drain receiver tank

Clean components

Check that earthing of motor through conduit or cable armouring is secure

Check that motor terminal cover is secure

Check bearings while running and report on condition

Bi-annual Service

Blow out motor

Grease motor bearings if grease nipples are fitted

Blow out starter panel

Check motor and starter terminals for tightness and condition

Operate and check overloads where possible and check overload setting for correctness

3 Yearly 

Pressure vessel testing for statutory compliancy – By Accredited Supplier


	Monthly/Bi-annual

	1.3.12.
	Water treatment 

Weekly: Inspections

Bi-annual – Legionella tests

The scope would include but will not be limited to the following specifications:

Responsibilities of the Water Treatment Supplier:

Take control of all the aspects of the HVAC water treatment program and supply all the water treatment chemicals in order to prevent Scale, Corrosion Deposits, Biofouling and diseases, as follows:

Weekly site visits are required to monitor systems and take corrective action and to do dosage on all the systems as required.

Do full analytical tests on each system with a detailed report on action taken to be submitted to ERIC’s Eskom Representative on a weekly basis. Reports to state: Parameters and current values for all areas regarding pH, Alkalinity, Calcium, TDS and chemical concentration factors, action taken and general conditions.

Legionella analysis to be carried out twice per year (October and April) on all air handling units and cooling towers and certification on findings observed to be sent to ERIC’s Eskom Representative. All positive results must be managed by the Water Treatment Supplier until the systems are tested negative.

Ensure client is kept up to date on system conditions and report any deviations immediately to ERIC’s Eskom Representative.

Supply all necessary chemicals required to prevent scale, corrosion, biofouling and diseases in the specified systems.

Ensure all chemical supply containers have sufficient chemicals.

Ensure all dosage units are in working order.

Ensure all bleeding systems are controlled at the correct total dissolved solids values.

Ensure dosage of all closed systems.

Setting of all control equipment according to water analysis results.

Ensure all analysis ratios are correct, with corrective action, if required.

Abide by the guidelines as detailed in risk management.

Safety Data Sheets to be provided for all Chemicals used on site and should be displayed at all dosing points/containers.

Systems to be treated.
Closed Chiller Units

Closed Hot water systems.
Chiller plant systems. 

Air-Handling Units - Sumps for Air-Washers in:

Chemical specifications and parameters

Air Handling Units - Chemicals to prevent scale and corrosion must have the ability to remove old scale deposits with constant use over extended periods. No chromates to be used in corrosion control. Bacterial control to prevent Legionella growth: No oxidising biocides to be used in the control of biological proliferation. Care has to be taken that all chemicals used will not react and release smells or gasses in the air ducts.

Chiller Systems - Chemicals to prevent corrosion and biofouling in closed chiller systems. No chromates or heavy metals to be used in the systems.

Closed Hot Water Systems - Chemicals to prevent scale and corrosion. No chromates to be used. Chemical must ensure adequate oxygen absorption surface coating and alkalinity control.


	Weekly/Bi-annual

	1.3.13.
	Filtration by OEM (Patent holder)
Monthly

Clean-Air Filter services at ERIC
The scope would include but will not be limited to the following specifications:

The filters of the Central plants (ducted systems) need to be maintained monthly by       means of a good quality “clean air” program to ensure that Safety and Environment standards are maintained. 

The filters and surrounding areas (filter mounting panels and floors) must be cleaned at least monthly but as frequently as necessary to always ensure clean air, taking in consideration winter and summer conditions, etc. 

The filter Supplier will keep filter bank areas clean, including the floors in the immediate filter areas, to always ensure cleanliness.

Mounting frames and ERICs need to be kept in a good condition to ensure that no filter by-pass occurs.

The manometers and related equipment, measuring the pressure drop across the filters, must be maintained. (Repaired or replaced when necessary.)

Any damaged filters must be replaced immediately, on an as and when required basis.

The replacing and repairing of faulty filters and manometers (including their ink/oil), filter banks ERICs, cleaning materials and all other labour, material and travelling costs should be included in the fixed monthly costs. 

An efficiency level of 95% and above needs to be always maintained and filters need to be replaced when efficiency drops below 95% @ 5um.

Certification of efficiency levels for all the filters needs to be supplied to Eskom on request.

No storage facilities will be provided by ERIC.

Dirty filters must be removed from ERIC’s site for cleaning.

Cleaning of filters to be done off site under controlled conditions.

The filters for ERIC should be marked and used at ERIC only and filters should be replaced with new ones after the fifth wash to ensure that filters stay rigid and efficient.

Records of number of washes to be kept at supplier and ERIC. 

Filters to be labelled for identification and tracking purposes.

Proof of identification of filters must be produced before installation.

No other site’s filters will be accepted at ERIC.

Monthly feedback/inspection sessions to be scheduled by the filter Supplier with the Eskom Representative.

The filter Supplier to submit a Monthly Report to Eskom, stating: 

1. The filter status in all areas, the velocity as well as the initial and final pressure drops on the manometers, before and after installation of clean filters, at all the air-handling units in the Main and Simulator buildings and LDC.

2. Particle counts before and after all the filters banks must be done every month, before and after the filters are replaced. The results of the particle counts must be plotted on a graph in the monthly report.

Filter requirements:

· Supply Clean Air, using Conical Cell Venturi filters in Main and Simulator buildings, Colenso and LDC and Service Exchange Panel systems in other areas.

· Efficient air quality and sufficient airflow is extremely important.

· The filter medium for CCV’s should consist of nonwoven fibres and have at least 380grams of fibres per square meter, which ensures a filtration efficiency of 95-98% @ 5um. 

· The filter medium for Service Exchange Panel systems should consist of nonwoven fibres, with at least 250 grams of fibre per square meter, which ensures a filtration efficiency of 80% @ 5um.

· The filters and the filter framework should be rigid to ensure that the movement of Air flow that causes a considerable amount of vibration on the filtration products, shaking holding frames and filters, will not cause the filters to offload dust particles (passing through filters) in the air supply. 

· The filters must be able to absorb a great amount of dust and keep the dust in the catchment area, without bursting its breaking apart.
· Proper servicing of filters in holding frames is required to prevent by-pass of unfiltered air.

· A low average pressure drop is required to save energy. 

· All material to be tested according to SABS1424-1987 test standards (Ashrae 52-76).

Note: The supplier needs to provide and change the filters once a year. The supplier needs to supply the same specification quality with the current one on site. Approval to be done by ERE supervisor on site. 

	Monthly

	1.3.14
	BMS/CONTROLS.  
BMS and Controls – Services to be done By OEM accredited agent

Monthly Service

· Advise on software upgrades to ensure communication to latest technology controllers and to prevent system from becoming outdated. 

· Do system back-ups monthly of database

· Update graphics and do modifications to database when required

· Check alarm and failure reports from controls workstation and resolve problems if any and pick up sequential problems from alarm counts.

· Check BMS system workstation for correct operation and do necessary adjustments/programming

· Give problem areas/defects first priority

· Check step controllers (heaters, boilers, air-handling units) for correct operation and adjust where necessary

· Check all switching and monitoring points(pumps, fans, chillers, flow switches, etc.)

· Control loops to be checked and adjusted where necessary(e.g. sensor, damper, actuator cycle)

· Check and ensure flow switches, static pressure sensors and timers are in order

· Checking  and repairing of fire damper operation and control

· Checking of MEC controller and PB controllers for correct operation for system communication and there battery back-ups.

· Supply SMS Alarm service and ensure correct operation thereof

· Investigate problem areas for better control, experimenting with supply air, return air, enthalpy or averaging control

· Check and repair server where necessary

· Supply report after every service

· System improvement and energy management to form part of service

· Check and repair UPS’s

· Physically check damper operations that control return-, outside- and exhaust air and enthalpy to confirm correct operation as per BMS settings and to ensure economy cycles are functioning efficiently 

· Physically check actuator operation for dampers, vortex dampers, cooling towers to confirm correct position as per BMS settings – make sure bolts are properly secured to prevent slipping on damper shafts. 

· Examine, clean and test all control devices

· Check and ensure all sensors – for air temperature:  supply-, return- and fresh/outside air, humidity, enthalpy and room temperatures are functioning properly.

· Also check  all automatic temperature set points and adjust where necessary, including re-heater set points and sensors to switch on and off at the correct temperatures

· Check boiler temperature and pressure sensors and overheat stats for correct operation

· Physically check heating- and cooling coil valves positions are correct as per BMS Settings

· Check that Chiller by-pass valves are operating correctly to prevent chillers from starting and stopping too frequently- do adjustments where necessary

· All minor repairs where material is not required must be done as part of service

· Check that water differential pressure controllers are operating correctly

· Check all control interlocks on control panels and interaction with other controls are functioning correctly

· Check that level switches on hot water and Chilled water make up and expansion tanks and on open hot water expansion tanks in Plantrooms P1A and P6 are functional

· Ensure safety interlocks between  boilers and chillers are operating correctly to prevent current overload

· Source and supply and install necessary replacement parts.

· Provide emergency call-out service – 2hour response time – report on site within 4 hours 

Annual Service

· Calibration of sensors,  thermostats, humidity controls, temperature controls and pressure controls

· Stroke dampers and valve actuators

· Check status of all panel point addresses to ensure all is in order

Note: Lead times for any emergency call out shall be 2 hours from call out. Failure to respond with such time will result in NCR 

Generic list of Eskom Equipment for guidance purposes only

· Central Plants

· Chillers
· Heat-exchangers

· Air-handling units

· Heaters – Main and re-heaters

· Filtration

· Water treatment(Cooling towers/condensed water, chilled water)

· Heat pumps for water heating

· Window Units

· Console Units

· Split Units

· Ducted Splits Units

· Data Room Aircons 

· Extraction systems – transformer rooms, toilets, etc

· Fresh air systems

· Domestic Fridges

· Commercial Cold Rooms and Freezer rooms

· Kitchen Extraction and Supply systems

· Ice machines

· Under counter fridges

· Upright fridges and freezers

Scope of work for new air-conditioners at ERIC
· Heat load calculations to be submitted with quotes as well as proof of qualifications of installer on site. (See competency section)

· Successful contractor must supply operating and installation manuals as well as a complete set of trouble shooting and service manuals or CD’s with all the relevant electrical diagrams for the indoor units, outdoor units, controller cards, remote controls, etc. for all types of units installed as part of the contract or installation.

· Where existing equipment are replaced, the quotes should include the removal of old air-conditioners, including the old piping and wiring, etc. but it stays the property of Eskom and none of it shall be used for the new installations. 

Installation

· If a split type of air-conditioner is fitted, where the main plant used to supply air-conditioning, the supply air must be blanked of properly with galvanized endcaps on the ducting itself. 

· The pneumatics must be blanked off with the correct fittings as well.

· The sensors in the room must stay in the room, in working order. 

· Where the removal of old air conditioners influences existing air conditioners the contractor must make good. E.g., servicing of holes where drains used to tap in existing installations, etc.

Installations to be done as per manufacturer specifications.
In Addition:

· Each air-conditioner indoor unit to be installed, level, in the best possible position to obtain optimal function of the air-conditioner, regarding air-flow, or as instructed by the project officer but at least 100mm from the ceiling to allow for maintenance on the indoor unit.

· Indoor unit back plate to be fixed to the wall with at least 6x55mm anchor nails or bigger. 

· The refrigerant pipes to be installed in separate Armaflex as required by manufacturer’s specifications. Armaflex joints to be serviced with 50mm pvc tape.

· No joints allowed on cabling, for electrical connections, between indoor and outdoor units. (Evaporators and condensers)

· The refrigerant piping, drainpipes and indoor/outdoor electrical connections to be installed in a 50mm x 75mm white PVC enclosure (trunking) with a solid cover on the inside of the building. (When working in straight lines, joints on the trunking and its covers are allowed at 3-meter intervals only.) 

· The supply cable to the isolator to be installed in 25mm x 15mm white PVC trunking. (When working in straight lines, joints on the trunking and its covers are allowed at 3-meter intervals only.) 

· Blue PVC condensation drainpipes and elbows, couplings, etc. to be used. (Proper joints with PVC glue are allowed where necessary. Drains to stop at 100 mm from ground level and must be covered with trunking.)

· Drains running horizontally, to be in a straight line and level or slightly downwards to ensure proper draining.

· When the installation is done through a brick or concrete wall.

· A 10mm pilot hole to be drilled from inside the room to the outside.

· A 65mm hole to be drilled from the inside, halfway through the wall towards the outside. From the outside a 65mm hole to be drilled towards the inside of the room by lining the hole up via the drilled pilot hole. This is to prevent the damaging of bricks or concrete on the outside of the building. 

When the installation is done through metal sheeting, drywall etc. 

· A 65mm hole to be drilled with a hole saw.

· The holes through the walls should be serviced with foam to make good and prevent insects and reptiles entering the building from outside.
· Each air-conditioner outdoor unit to be mounted at the end of a hot dipped cantilever bracket (white powder coated) against the outside wall. 450 mm brackets to be used on condensing units up to 12000 Btu and 650mm brackets for 18000 Btu condensing units. The bracket to be at least 1meter above ground level at a comfortable height, to enable the servicing of the unit, without making use of a stepladder. The outdoor units should not obstruct any windows, doors, walkways, etc. 

· These brackets to be secured with raw bolts against the walls. 

· The refrigerant piping and indoor/outdoor electrical connections to be installed inside a 75mmx75mm hot dipped galvanized enclosure with a solid cover on the outside of the building. This should cover the hole and extend right to the ground.  (When working in straight lines, joints on the trunking and its covers are allowed at 3 meter intervals only.) 

· All trunking and remotes to be secured with fisher plugs/hammering nails to the walls but pop rivets or self-tapping screws to be used on sheeting after neatly drilling the correct size of holes.  

· All open ends of trunking to be covered with end caps and all of the steel enclosure ends should be painted with a cold galvanizing compound on cut joints to prevent rust.

· Holes through the sheeting on the outside of the building to be serviced off with bitumen and its cloth, matching the colour of the existing sheeting.

· All open armerflex on the outside of the building to be painted with roof paint or bitumen to protect it against UV rays and weather conditions, matching the colour of the existing walls/sheeting.

· Any accidental damage to be repaired. E.g., If holes on the inside of the building are exposed it should be filled with Polyfilla and sanded down neatly.

· The refrigerant system shall be pressure tested to 2800Kpa with dry Nitrogen and pressure shall be maintained for two hours to proof the refrigerant system leak free. Vacuum shall be drawn to below 200 Microns. Purging the refrigerant system with refrigerant, will not be acceptable. Refrigerant recyclers should be used if necessary and no refrigerant should be released to the atmosphere. Oxygen free Nitrogen to be purged through the refrigerant pipes when welding the joints.

· A COC must be issued for all the electrical installations.

Typical materials that will be used. (All SABS approved and as per manufacturer specifications)

· 50mm x 75mm white PVC enclosure.

· 75mm x 75mm hot dipped galvanized enclosure.

· Refrigerant piping of the correct type and size.

· Armerflex.

· 7 core cable. 

· 20mm blue PVC condensation drain pipes. 

· White powder coated cantilever brackets.

· Hammering nails/fisher plugs.

· Raw bolts.

· 50mm PVC tape.

· Cable straps.

· Pop rivets.

· Self-tapping screws.


	

	1.3.15.
	Cold Rooms 

Service

· Check Operation of Unit

· Clean Condenser Coils (Hose)

· Check System Gas Charge and refill the gas when necessary.
· Leak Test Refrigeration System

· Check Compressor Oil Level and refill when necessary.
· Check Operating Pressures and Record

· Check Safety Cut-Outs and Record Discharge & Suction

· Check for Signs of Oil Leaks

· Check for any Signs of Vibration


	Monthly

	1.3.16.
	4. Refrigeration Equipment

Monthly Service

· Check Operation of Unit

· Clean Condenser Coil

· Check System Gas Charge and refill the gas when necessary.
· Leak Test Refrigerant System

· Check Compressor Oil Levels

· Check Operating Pressures. Record Discharge and Suction

· Check Safety Cut-Outs. Record Discharge, Suction & O/P/S

· Record Time Delay of Oil Pressure Safety Switch

· Check for Signs of Oil Leaks

· Check for Signs of Vibrations

· Clean Condenser Coils (Hose)

	

	1.3.17.
	Counter Fridges 

Quarterly Service

· Check Operation of Unit

· Clean Condenser Coils (Hose)

· Check System Gas Charge and refill the gas when necessary.
· Leak Test Refrigeration System

· Check Compressor Oil Level

· Check Operating Pressures and Record

· Check Safety Cut-Outs and Record Discharge & Suction

· Check for Signs of Oil Leaks

· Check for any Signs of Vibration


	

	1.3.18.
	5. Bar Fridges

As and when required Service

· Pressure Test Refrigeration System

· Check All Door seals and replace when necessary.
· Check General Condition of Fridge.

· Record temperature.


	


	1.3.2
	Plumbing and Drainage
Service

· Repair and replacement of leaking taps and cisterns

· Replacement of copper and PVC pipes

· Repairs and replacement of urinals, basins, sinks, tubs, troughs, runnel, shower trays, shower heads, tanks toilet.

· Water connection to hydro boilers, water tanks sewer system and buildings

· Unblocking of drainage structures, pumps including manholes

· Grease or replace gullies.
· Replace aluminium glass shower door, manholes lids

· Replacement of threaded tubing and valve

· Installation of water tanks, hydro boilers

· Pressure jetting-ad hoc maintenance 

· Wash bay sumps maintenance and issue disposal certificate –this is for major offices only.
· Attend to water leaks /blockages call outs.
· Keep basic spares on site to address leaking taps and pipes (copper and PVC)

· Water tank repair and replacement

· Septic /conservancy tank repair and maintenance.

· Annual testing of boreholes

· Storage tanks

· Supply and installation of geysers and other hot water systems
	


	1.3.3
	Civil Works and Mechanical
	

	1.3.3.1
	Civil Works

Service

· Breaking down and removing brickwork, reinforced concrete including cutting off and removing reinforcement.

· Break out and from opening through brick wall for window including necessary precast or concrete lintels, making good plaster or facings on one or both sides, into reverse.

· Taking out and removing doors, windows, including thresholds and sills from brickwork to remain (build up or altering openings elsewhere measured)

· Fixing of existing doors, windows, and fanlights.

· Paving 

· Painting 

· Tiling and glazing 

· Carpentry, masonry, joinery, and ironmongery

· Plastering 

· Bricklaying

· Taking up and removing vinyl floor coverings, carpeting and suspended floor.

· Maintenance of drainage structures.

· Repairs to existing structural steelworks including various types of fencing. 

· Galvanising of existing steelworks
· Maintenance of existing roadworks and markings including cut, fill, compact, primer and tarmac on existing worn-out roads

· Repair, replace and clean kerbing. 

· Repair clean and maintain storm water catch pits and piping.

	


	Item
	Description
	Frequency

	1.3.4
	Electrical and UPS System 

Service

· The checking of the mechanical soundness of all parts.

· The checking of the semi-conductor power devices, transformers, filter elements and the like

· The checking and, if necessary, adjusting of the voltage of the DC circuitry.

· The checking and, if necessary, adjusting of the output voltage of the AC circuitry.

· The checking and adjusting of all electronic regulating circuits.

· The cleaning of the UPS system

· The checking of the DC caps.

· The checking of the AC filters caps.

· The checking of all Fan operations.

· Visual checking for Hot Spots (Hot Spots are discolouring of power wires and main bus bars)

· The checking of batteries for loose connections, hot spots, and terminal corrosion.

· The checking of load currents and voltages.

· The checking of environmental temperature and ensuring that it is within the UPS operational specifications.

· The checking and recording on a log sheet of the voltage of each battery block.

· The cleaning of the batteries.

· Conduct a battery discharge test using the s existing load connected to the Equipment to determine the capacity of the battery. 

· The checking of sufficient lighting. 

· Should the Technician find any problem during the inspection.
· Submit the detailed service report will be handed to site personnel directly after completion of the service.
· Where after arrangements to correct these faults can be made


	

	1.3.4.1
	Main and Sub Electrical Distribution Boards All Blocks

Service

· The Contractor shall be responsible for the cleaning, service, maintenance, and repairs to all Main and Sub Electrical Distribution Boards and Control Equipment. 


	Quarterly 

	1.3.4.2
	Switches, Changeovers, etc.

Service 

· Main incoming supply, main switches, change-over systems, bus bars and the supply ups to each of the local isolators for each individual piece of equipment. 


	Monthly

	1.3.4.2
	Charger and Batteries 

Battery Tripping Unit

Service

· Clean off any acid from battery terminals

· Check water levels on all cells

· Check all connections

· Check load circuits on battery

· Check supply voltage

· Check battery voltage

· Test all single cell internal battery resistance (Test conducted per battery)

· Test all single cell battery voltage(Test conducted per battery)

· Check all indication functional

· Compile test report according to Charger specifications

Battery Testing 

Service

· Check hydrometer

· Check casing condition

· Check the water

· Check terminals

· Note Volts

· Note Amps

· Compile battery report

· Checking of input and output terminations 

· Installation of batteries in battery cabinets or onto stands. 

· Checking of battery connections 

· Complete mechanical check of the UPS system. 

· Electrical and calibration check of the UPS system 

· Testing of all UPS alarm functions including Remote Alarm Panel (RAP) if supplied 

· Mains failure test, using existing load, to prove correct operation of UPS system 

· Explanation of UPS operation and alarms to customer 

· Hand-over acceptances. 


	

	1.3.4.3
	Certificate of Compliance 

Service

· Issue the certificate of compliance as electrical regulation.  


	When necessary.

	1.3.4.4
	PA System
Service and test the PA System including a written report.

	Bi-annual

	1.3.4.5
	Earthing and Bonding

Service 

· Must be done as per earthing and bonding regulation.

	Annual

	1.3.4.6
	Infra-Red Scanning 

Service

· Must be done on the tested, balanced and commissioned complete electrical installation.
· Conduct an Infra-Red Scan survey on all the above-mentioned distribution boards under full load condition.

· On completion of the survey, a detailed written report including photographs shall be handed to the Employer.
	Quarterly


	1.3.5
	Fire Protection &Sprinkler System

Fire and Smoke Detection 

Service 

· All the equipment as specified above shall be serviced and maintained in strict accordance with the manufacturer’s specifications and recommendations.  

· Manuals are available on the Site and shall not be removed from the Site.


	Quarterly 

	1.3.5.1
	Fire Detection System and Alarm Systems

Service

· Each smoke detector shall be activated and checked for operating correctly including all remote indication associated with the relevant smoke detector.

· Each smoke detector shall be inspected during the service to be in a good condition and not damaged.

· Each smoke detector shall be wiped clean during the service.

· Ensure that during the service of each smoke detector is recorded as per its number on the service report sheet and checked accordingly.

· The relevant fire panels shall be checked to ensure that all visual and audible alarm signals as per zone are correctly received.


	Quarterly

	1.3.5.2
	Fire Panel

Service

· All visual and audible alarms associated with the zones being tested are to be checked for correctness of operation. All control signals on fire panel and within the building to be tested and verified correct.

· Check power supply unites and ensure satisfactory operation.

· Check on condition of batteries and report any defects.

· Check all cable terminations and ensure tightness.


	Quarterly

	1.3.5.3
	Test Fire Signal to Fire Brigade

Service

· A test shall be carried out to ensure that a fire signal from the Eskom Building ERIC is correctly received at the Emergency and Disaster Management Centre.


	Monthly

	1.3.5.4
	CO2 Gas Fire Suppression System

Service

· Before the Contractor proceeds to provide the Works, a risk assessment shall be conducted, and all the relevant safety measures shall be put in place and be recorded in writing.

· Test the operation of the entire system and record all the steps and the findings on the service report sheet.

· Trigger test each one of the detectors and record all the steps and the findings on the service report sheet.

· Visually inspect all gas cylinders, record all the findings. And the pressure on the service report sheet

· Pressures test the gas cylinders when required by regulation or law.


	Annual


	1.3.5
	Wastewater Treatment and Sewage System

Operations

Plant needs to be operated on a 24-hour basis.
Daily checks

· Start raw water pumps

· Check pH and chlorine levels and keep a record

· Check pH/flow readings and record

· Check water flocculation and record pH

· Check stirring chemicals in makeup tanks

· Make up chemicals in tanks, if required

· Backwash filter as required

· Check that dosing pumps are pumping and that dosing rate is correct

· Check the chlorine dosing rate and record

· Start high lift pumps

Weekly checks

· Do all daily checks

· Backwash filters

· Flush the dosing line with acid

Monthly checks

· Do daily and weekly checks

· Check pumps, glands, etc.

· Clean items as required further in plant

· Allow the HTH chemical makeup tank to empty and clean out sludge from HTH/Alum make up tank

Bi-annual checks

· Check sand in filters, and replace or replenish if necessary

Yearly Checks

· Do daily, weekly and monthly checks

· Check all electrical connections

· Check functioning of all pumps

Monthly Maintenance

· Check pumps

· Check float switches

· Check sand filters

· Check all valves

· Flush the reservoirs with Chlorine

· Check all electrical connections 

· Check the structural integrity of the site including steel and concrete work


	Monthly/Bi-annual/

Annual


	1.3.6
	Diesel Generator and Storage Tanks
	

	
	
	

	1.3.6.1
	Diesel Generator

Inspection and service

Weekly Inspection (Visual inspection of the following)

•
General condition of prime mover/generator

•
Condition of belts & hoses

•
Engine oil level

•
Lube oil heater

•
Coolant level

•
Water pump

•
Jacket water heater

•
Radiator

•
Electrical/Generator breaker closed

•
Battery Electrolyte level

•
Battery Charger

•
Exhaust system

•
Fuel supply level

•
Tank vent(s)

Monthly Inspection

•
Check Fan belt, condition, and tension

•
Check radiator passages is clean

•
Check radiator hoses and clamps

•
Check service faces of elements, air cleaner, hoses, and clamps for dust ingress

•
Check thermos heater operation and temperature

•
Check all guards in position and secure

•
Check battery charger

•
Check batteries, lugs, clean and tighten

•
Battery test:


-Check hydrometer


-Check casing condition


-Check terminals


-Note Volts


-Note Amps


-Compile battery report

•
Start engine

•
Check for any leaks

•
Check charge alternator operation

•
Take oil pressure gauge reading

•
Take engine temperature gauge reading

•
Check low radiator level

•
Check low fuel level

•
When engine has stopped, top up with oil

•
Check alternator coupling

•
Check air vents on alternator

•
Check fuel system

•
Drain water trap

•
Check all pipes and fittings

•
Check exhaust, manifold, silencer, and pipes

•
Check base and anti-vibration mounts

•
Run plant off load

•
Clean plant and equipment
Quarterly Inspection and Minor service

•
Check Fan belt, condition, and tension

•
Check radiator passages is clean

•
Check radiator hoses and clamps

•
Add water conditioner

•
Drain radiator/system and refill

•
Drain oil and refill

•
Change fuel filters

•
Change oil filters

•
Change water conditioner filters

•
Change air filters (if required)

•
Check service faces of elements, air cleaner, hoses and clamps for dust

•
Check thermos heater operation and temperature

•
Check all guards in position and secure

•
Check battery charger

•
Check batteries, lugs, clean and tighten

•
Battery test:


-Check hydrometer

      -Check casing condition


-Check terminals


-Note Volts


-Note Amps


-Compile battery report

•
Start engine

•
Check for any leaks

•
Check charge alternator operation

•
Take oil pressure gauge reading

•
Take engine temperature gauge reading

•
Check low radiator level

•
Check low fuel level

•
When engine has stopped, top up with oil

•
Check alternator coupling

•
Check air vents on alternator

•
Check fuel system

•
Drain water trap

•
Check all pipes and fittings

•
Check exhaust, manifold, silencer, and pipes

•
Check base and anti-vibration mounts

•
Run plant on load

•
Clean plant and equipment

Annual Service

All the above items are to be attended to in addition to the following items:

•
Drain radiator

•
Refill with new water conditioner

•
Drain oil

•
Supply and fit new oil filters

•
Refill with new oil

•
Remove and replace fuel filters

•
Remove and replace air filter

•
Run the set up to temperature and top up all levels afterwards.

•
Check entire panel operation

	Monthly/

Quarterly/Annual

	1.3.6.2
	Diesel Storage 

Annual Service Pressure tanks 

· Pressure test of diesel tank.

· Test for loss and leaks including a written report.
Service Diesel tank & Diesel fuel testing 

· Visual inspection of the fuel system.

· Checking the filters, tanks, fillers, and site tubes.

Bi-annual Service Conidia Bioscience test

· Conidia Bioscience Fuel-stat test and written report.

Annual Service Filtration & Additives 

· The diesel in both tanks will be filtered and polished if no filtration system is installed including additives added. 

· The “Fuel Right” method to be utilised.
Service Fuel supply

· Supply of 50ppm diesel to fill up tank.

·  Proof of purchase to be submitted.


	


	1.3.7
	Help Desk Services

The functions of the Helpdesk include but not limited to the following:

· Providing a single point of contact for receiving all maintenance services calls, requests, and complaints.

· Preparing and issuing of work orders to the Employer for approval prior to any work been executed.

· Closing of all the calls, requests, and complaints once work is completed and verified by the Employer.

· Preparing of monthly reports for corrective and planned maintenance work executed.

· Executing ad-hoc services as and when requested by the Employer.

· Contractor to ensure that there’s a reliever for the help desk personnel.  

The Employer will provide the necessary training on the work planning system.

	Monthly


	1.3.8
	Water Analysis

CHEMICAL AND BACTERIAL ANALYSIS All tests conducted must include for the following:
•
pH at 25ºC: Electrometric (Based on SANS 5011)

•
Electrical conductivity at 25ºC Conductimetric (Based on SANS7888)

•
Suspended solids at 105ºC Gravimetric (Based on SANS 6049)

· Total Solids at 105ºC: Gravimetric (Based on Standard Methods for the Examination of Water and Wastewater (APHA, AWWA, WEF), 21st Edition)

•
Dissolved solids at 180ºC: Gravimetric (Based on SANS 5203)

•
Turbidity: Nephelometric (Based on Standard Methods for the Examination of Water and Wastewater (APHA, AWWA, WEF), 21st Edition)

•
Chemical Oxygen demand: Titrimetric (Dichromate reflux). (Based on government Gazette 2512)

•
Oxygen absorbed: Titrimetric (Based on SANS 5220)

•
Chloride: Titrimetric (Argentometric) (Based on Standard Methods for the Examination of Water and Wastewater (APHA, AWWA, WEF), 21st Edition)

•
Alkalinity: Titrimetric (Based on Standard Methods for the Examination of Water and Wastewater (APHA, AWWA, WEF), 21st Edition)

•
Sodium (Based on Standard Methods for the Examination of Water and Wastewater (APHA, AWWA, WEF), 21st Edition)

•
Potassium (Based on Standard Methods for the Examination of Water and Wastewater (APHA, AWWA, WEF), 21st Edition)

•
Calcium (Based on SANS 216)

•
Magnesium (Based on SANS 1071)

•
Copper (Based on SANS 5203)

•
Zinc (Based on SANS 5214)

•
Iron (Based on SANS 5207)

•
Manganese (Based on SANS 5209)

•
Nickel (Based on SANS 6171)

•
Chromium (Based on SANS 6054)

•
Aluminium (Based on SANS 6169)

•
Lead (Based on SANS 5208)

•
Fluoride (Based on Standard Methods for the Examination of Water and Wastewater (APHA, AWWA, WEF), 21st Edition)

•
Ammonia (Quickchem method 10-107-06-2-J)

•
Nitrate (Quickchem method 10-107-04-1-A)

•
Orthophosphate (Quickchem method 10-115-01-1-O)

•
Sulphate (Quickchem method 10-116-10-1-A)

•
Hexavalent Chromium (Quickchem method 10-124-13-1-A)

•
Microbiology:

•
Enumeration of Total Coliforms, Faecal Coliforms and E.Coli.

•
Standard Plate Count.


	Monthly


1.3.2 Uniforms
· All staff to be issued with minimum uniform as follows: 

	Items
	Sets per year to issue per worker

	Appropriate work suits.
	4

	Safety boots (SABS approved)
	2

	Socks
	4

	Winter Jacket, contractor name branded
	1

	
	

	Safety goggles
	2

	Safety gloves preferable fire gloves
	4

	Hard Hat with chin straps 
	1


· All staff to be clearly identified.
1.3.2.1.1 Customer survey
Customer surveys to be done by Contractor every month with full feedback report, to enable Eskom to evaluate Service quality, Consumption report and Client Satisfaction.  Meetings with minutes must be held monthly with Contract Manager to evaluate, report, and formulate action plans.
Performance and quality of service will be evaluated monthly; penalty will apply for poor service as per agreed expectations.
1.3.2.1.2 Working time
Core working times: Shift working will apply between 07:00 and 16:00 Monday - Friday and as and when required by the Employer.
Weekend (Saturday and Sunday) and Public Holidays not working days. 
Overtime work will be required on as and when required basis and working times will be stipulated in the task order.

2 Management strategy and start up.

2.3 The Contractor’s plan for the service
During the execution of the Service, the Contractor shall maintain a suitable office in the area allocated for that purpose by the Employer, which shall be the headquarters of the Contractor’s Representative and authorised to receive instructions or other communications or notices under the Contract. The Contractor shall maintain, at the office, up-to-date copy of the Contract and all Contract related documents (including correspondence and documents issued by and to the Contractor, Compensation Events, Progress Reports, correspondence, non-conformance reports etc.). These documents shall be always available to the Employer.
2.4 Management meetings

Regular meetings of a general nature may be convened and chaired by the Supply Manager as follows:

	Title and purpose
	Approximate interval
	Location
	Attendance by:

	Progress / feedback meeting
	Monthly
	Eskom Research and Innovation Centre
	Eskom Research and Innovation Centre

	Risk management meeting
	Monthly 
	Eskom Research and Innovation Centre
	Eskom Research and Innovation Centre

	Overall contract progress meeting
	Monthly 
	Eskom Research and Innovation Centre
	Eskom Research and Innovation Centre

	Safety, health, environmental and quality meeting
	Monthly
	Eskom Research and Innovation Centre
	Eskom Research and Innovation Centre


Meetings of a specialist nature may be convened as specified elsewhere in this Service Information or if not so specified by persons and at times and locations to suit the Parties, the nature and the progress of the service.  Records of these meetings shall be submitted to the Service Manager by the person convening the meeting within five days of the meeting.  

All meetings shall be recorded using minutes or a register prepared and circulated by the person who convened the meeting.   Such minutes or register shall not be used for the purpose of confirming actions or instructions under the contract as these shall be done separately by the person identified in the conditions of contract to carry out such actions or instructions.  
2.5 Contractor’s management, supervision, and key people

The Contractor shall provide the Employer with a detailed organogram of all staff and management on the contract. This must be revised quarterly and must reflect any changes to the staff and management structure. The Employer reserves the right to audit and verify the structure.
2.6 Provision of bonds and guarantees.
N/A
2.7 Documentation control

The Contractor will submit the following documents to the Employer for review, the Employer will review the documents for acceptance and inform the Contractor if the documents have been accepted or if it is not accepted and stating the reasons of not the accepting the documentation. The Employer will give the Contractor reasonable time which will be agreed to between the Contractor and the Employer to respond or re-submit the documents. 

2.8 Invoicing and payment

Within one week of receiving a payment certificate from the Service Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice showing the amount due for payment equal to that stated in the Service Manager’s payment certificate.  

The Contractor shall address the tax invoice to: 
Eskom Holdings SOC Ltd

Group Capital Division

Eskom RERIC Estate 

Megawatt Park Maxwell Drive Sunninghill Sandton

PO Box 1091 Johannesburg 2000, SA
and include on each invoice the following information:

Name and address of the Contractor and the Service Manager. 

The contract number and title.
Contractor’s VAT registration number.
The Employer’s VAT registration number 4740101508.
Description of service provided for each item invoiced based on the Price List.
Total amount invoiced excluding VAT, the VAT and the invoiced amount including VAT.
2.9 Contract change management. 

The Employer may instruct changes to the scope at any time, each instruction shall set out the change and the date on which it becomes effective; and must be issued to the Contractor in writing to be valid.
2.10 Records of Defined Cost to be kept by the Contractor.
The Contractor must keep all documentation related to the compensation events, quotes and instructions from the Employer for the period of 5 years after contract completion for audit purposes.
2.11 Insurance provided by the Employer.
The insurance policy provided by the Employer will be direct with as specified in Clause 86.1 TSC.
2.12 Training workshops and technology transfer
N/A

2.13 Design and supply of Equipment

N/A.

2.14 Things provided at the end of the service period for the Employer’s use.
2.14.2 Equipment
N/A

2.14.3 Information and other things

At the end of the service period the Contractor will be required to provide the Employer with the Contractor’s Safety file
2.15 Management of work done by Task Order

All work will be done in terms of Task Order (refer to attached Annexure A).
3 Health and safety, the environment and quality assurance

3.3  Health and safety risk management

The Contractor shall comply with the health and safety requirements contained in the Eskom Real Estate SHE specification (as applicable).

3.4 Environmental constraints and management

The Contractor shall comply with the environmental criteria and constraints stated in Eskom Real Estate SHE specification (As applicable).

3.5 Quality assurance requirements

The Contractor shall comply with the quality requirements as stated in QM-58 (As applicable).

4 Procurement
The Contractor provides the following procurement services in performing the scope:

· Sub-Contractor’s lists for to be submitted to the Employer for review and approval.
· Follows the least cost and time procurement strategies.
· Obtains the Employers’ approval prior to committing any contracts or orders.
4.3 People

4.3.2 Minimum requirements of people employed.
In some instances, the Contractor may be required to recruit staff from the local to site communities.
4.3.3 B-BBEE 

The Contractor shall maintain the Required B-BBEE Recognition Level for the duration of the Agreement. The Contractor shall provide Eskom with a valid Verification Certificate and such other information as Eskom may reasonably request, in respect of which the Contractor claims maintenance for the duration of the Agreement of the Required B-BBEE Recognition Level. For the purpose of this clause “verification Certificate’ means a verification certificate and the accompanying documentary proof confirming the B-BBEE Status of a particular entity as issued by an accredited verification agency.

4.3.4 Supplier development and localisation
The Contractor complies with and fulfils the Contractor’s obligations in respect of the supplier, development and localisation matrix.

The Contractor shall keep accurate records and provide the Service Manager with reports on the Contractor’s actual delivery against the above stated supplier development and localisation matrix
The Contractor’s failure to comply with his supplier development and localisation obligations constitutes substantial failure on the part of the Contractor to comply with his obligations under this contract.
4.4 Subcontracting

4.4.2 Preferred subcontractors

N/A
4.4.3 Subcontract documentation, and assessment of subcontract tenders

Prior to appointment of a sub-contractor, the Contractor shall submit to Eskom all detail of the contractor, including B-BBEE details, for verification.
4.4.4 Limitations on subcontracting

The Contractor shall not sub-contract more than 30% (rand value) of the whole of the services to the local to site companies but shall, subject to Eskom’s consent (which consent shall only be valid if given in writing and signed by the Eskom Representative), be entitled to sub-contract selected parts of its obligations in terms of this Agreement to any other person/s, provided that such sub-contracting shall not relieve the Contractor of its obligations and the Contractor shall remain liable for all and any acts or omissions of such person/s as though they were acts or omissions of the Contractor. 

The Contractor shall not be entitled to cede, delegate, assign or otherwise transfer any of its rights and/or obligations without the prior written consent of Eskom, which consent shall not be unreasonably withheld.
4.4.5 Attendance on subcontractors

N/A

4.5 Plant and Materials

4.5.2 Specifications

N/A
4.5.3 Correction of defects

The Contractor shall provide maintenance and repair of all the equipment necessary to provide the services. All defects to the works shall be rectified as specified in QM 58.
4.5.4 Contractor’s procurement of Plant and Materials

The Contractor may be required to provide the Employer with a technical data sheet of the equipment or material supplied to the Employer. A guarantee and warrantees’ certificate may also be required for any plant and material supplied by the Contractor to the Employer.
4.5.5 Tests and inspections before delivery

.  The employer representative will conduct inspection if deemed necessary to do so.
4.5.6 Plant & Materials provided “free issue” by the Employer.
N/A
5 Working on the Affected Property

5.3 Employer’s site entry and security control, permits, and site regulations.
The Employer will provide access control for the Site. Strict access control shall be implemented 24 hours a day at all entrances to the Project Site.  All persons and vehicles entering or exiting the Project Site may be subjected to searches and the Employer reserves the right to refuse entrance to Site to any person not meeting security and/or access requirements.

From time to time, and as required, the Employer will issue policies and procedures regarding Project Site security and access control. These policies and procedures shall be strictly adhered to by the Contractor. The Employer shall be entitled, at his discretion, to amend or relax the Project Site security and/or access requirements to ERIC with emergencies or other circumstances justifying such amendment or relaxation.

Where the contractor is allocated a construction yard, security will be contractor’s responsibility and must comply with the employer’s requirements. 

Any breach of security must be reported to the Employer immediately.
5.4 People restrictions, hours of work, conduct and records.
Core working hours shall be from 07:00 to 16:00, Monday to Friday or as directed by the Employer. Shift work is required. Overtime will be approved by an Employer prior to the Contractor working overtime.

The Contractor shall keep records of his people working on the Affected Property, including those of his Subcontractors.  The Employer shall have access to records at any time.  
5.5  Health and safety facilities on the Affected Property

The Contractor shall ensure that alternative arrangements are made for possible incidents occurring after normal working hours. Where services are not available from the Eskom Medical Centre, the Contractor shall make alternative arrangements for any medical assistance.  Proof of this must be made available in the principal contractors SHE Plan.
5.6 Environmental controls, fauna & flora

The Contractor shall comply with the safety, health and environmental requirements stated in the ERE SHE Specification.
5.7 Cooperating with and obtaining acceptance of Others

Except as directed by the Employer, the Contractor shall in no way interfere with, remove, adjust, or operate plant, materials and/or equipment of or being supplied or operated by Other Contractors.
5.8 Records of Contractor’s Equipment

The Contractor is responsible for maintaining the asset register equipment on site and shall be audited by the Employer from time to time.

5.9 Equipment provided by the Employer
N/A

5.10 Site services and facilities

5.10.2 Provided by the Employer
The Employer will, at his expense, arrange for, develop, and maintain the various facilities and services at or near the Site, as applicable. The services and facilities provided by the Employer are listed below:

· Electricity.
· Water supply; and

· Sanitary Services.

5.10.3 Provided by the Contractor
The Contractor shall provide all other services and facilities.
5.11 Control of noise, dust, water and waste 

The Contractor shall comply with the safety, health and environmental requirements stated in the project SHE Specification.

5.12 Hook ups to existing works

The performance of the Works which affects the Employer's operations, or the systems of Other Contractors shall be scheduled to be performed only at times approved by the Employer. The procedure for carrying out work which of necessity interrupts the Employer's operations, or the systems of Other Contractors, or imposes abnormal operating conditions on their systems, is subject to approval of the Employer. (Applicable to pre-arranged window cleaning).
5.13 Tests and inspections

5.13.2 Description of tests and inspections

The Contractor is responsible for providing quality inspections as per the scope requirements and rectifies all defects within agreed time. The Contractor shall supply the end of job documentation associated with the services. The end of job documentation consists of the signed off (where applicable) completion forms of acceptance by the Employer.

5.13.3 Materials facilities and samples for tests and inspections 

In some instances, the Employer representative may request samples for testing/ inspection.
6 List of drawings

6.3 Drawings issued by the Employer.
The site drawings shall be issued by the Employer on request. 

ANNEXURE A: TASK ORDER

Task Order

	Task Order form for use when work within the service is instructed to be carried out within a stated period on a Task-by-Task basis

	

	Task Order No.
	[●]
	Service
	.[●]

	To: [●].......................................................................................................................................................

.......................................................................................................................... (Contractor)

	

	I propose to instruct you to carry out the following task:

	Description
	[●]

	
	

	
	

	Starting date
	[●]

	Completion Date
	[●]

	Delay damages per week
	[●]

	
	

	Please submit your price and programme proposals below.

	Signed:


	Date

	(for Employer)
	

	
	

	Total of Prices for items of work on the Price List (details attached)
	R.___________________________________

	Total of Prices for items of work not on the Price List (details attached).
	R.___________________________________

	Total of the Prices for this Task Order
	R ___________________________________

	
	

	The programme for the Task is 
	 ........................................... [ref] (attached)

	Signed:


	Date

	(for Contractor)
	

	
	

	

	I accept the above price and programme and instruct you to carry out the Task

	Signed:


	Date:

	(for Employer)
	


ANNEXURE B: X 17 – LOW PERFORMANCE DAMAGES
	Item No.
	Key Performance Area
	Key Performance Indicator
	Key Performance Targets
	Penalties

	1


	Service Performance Management 
	React within 1 hour to diagnose the root cause
	100% Compliance
	3 consecutive non-conformance will result in    R 2 500 penalty, amount payable the following month

	
	
	Critical work to be completed within 4 hours (blocked toilets,  leaking urinals, earth leakage trips, lights out, faulty plugs, power supply, refuelling of generators, temperature control, UPS system, Dali lights system, Water treatment ,etc)
	100% Compliance 
	3 consecutive non-conformance will result in    R 2 500 penalty, amount payable the following month per discipline.

	
	
	Maintain 80% for closure of defects vs logged defects 
	80% Compliance – measured monthly 
	2 consecutive non-conformance will result in    R 50 000 penalty, amount payable the following month

	2
	Statutory Inspection Compliance 
	Maintain statutory compliance
	100% Compliance
	2 consecutive non-conformance will result in    R 50000 penalty, amount payable the following month

3 consecutive non-conformance will result in termination of the contract

	3
	Safety, Health, and Environmental Contravention 
	Safety, health, and environment standards are regularly monitored, reviewed and maintained in accordance with all legal and regulatory requirements on quarterly basis
	0 contravention 
	3 consecutive non-conformance will result in termination of the contract

	4
	Availability of Cleaning Equipment 
	Provide well maintained equipment
	100% availability during any random inspection/audit
	3 consecutive non-conformance will result in    R 50 000 penalty, amount payable the following month

	5
	Employee Compensation and Benefits
	Payment of Employee salaries/wages, Provident Fund, UIF, COIDA, etc. as per the agreed date
	100% Compliance
	2 consecutive non-conformance will result in    R 50 000 penalty, amount payable the following month 

3 consecutive non-conformance will result in termination of the contract


� This total is required by the Employer for budgeting purposes only.  Actual amounts due will be assessed in terms of the conditions of contract.


� Available from Engineering Contract Strategies Tel 011 803 3008 Fax 086 539 1902 � HYPERLINK "http://www.ecs.co.za" �www.ecs.co.za� 







DOCUMENT C2.1
PAGE lxvi
PRICING DATA




Part C2: Pricing Data
PAGE 1
C2 TSC3 Cover

