|  | FBC Free State OU and Northern Cape OU INVESTIGATION REPORT | Template Identifier | 240-43921804 | Rev | 6 |
| --- | --- | --- | --- | --- | --- |
|  |  | Document Identifier | 240-136349448 | Rev | 2 |
|  |  | Review Date | 10 April 2018 |  |  |
|  |  | Effective Date | 01 March 2022 |  |  |

| INFORMATION SUPPLIED BY THE CUSTOMER AND POPULATED BY INSURANCE DEPARTMENT |  |  |  |
| --- | --- | --- | --- |
| Incident location (Town) | Dewetsdorp | Sector | Bloemfontein Sector |
| Date of incident | 19 Junie 2021 | Time of Incident | 22h47 |
| Date reported (fault) | 20 Junie 2021 | Reference number | Not stated |
| Date reported (claim) | 01 November 2023 | Reference number | Summons Received |
| Pole No. | DDW 331A-56-62 | Works order No. |  |
| Name of claimant | AJ Kingsley C Van Gend Jacobs Van Aswegen Trust | Contact number | 082 567 0523 – Kingsley 051-505 6600 – Leon Strating - Attorney |
| Stand Number/Address | Farm Oorlogspruit, Farm Willowvale, Farm Blydschap, Dewetsdorp | Claim No. | 438204 |
| Summary of incident |  |  |  |
|  | AJ Kingsley – Natural Pasture - R314 834.85 Lick Supplement - R90 634.27 Fence – R45 363.29 TOTAL R 450 832.41 C van Gend Jacobs - Natural Pasture – R83 199.60 Lick Supplement – R23 951.40 Fence – R22 965.18 TOTAL R 130 116.18 G Van Aswegen(TRUST) - Natural Pasture – R96 435.90 Lick Supplement – R27 761.85 Fence – R16 101.30 TOTAL R140 299.05 |  |  |
| Insurance remarks |  |  |  |
| Date to PCC | 14.02.2024,21.02.2024 |  |  |

| INVESTIGATION MAINTENANCE AND OPERATIONS DEPARTMENT |  |  |  |
| --- | --- | --- | --- |
| Complied by | Jaco Weldhagen | Designation | Sector Engineer |
| Authorised by | Korone Moea | Designation | Sector Manager |
| Claimant’s allegations for claim: |  |  |  |
| Date and Time of Incident | 19/06/2021 22:47 | Date and Time supply Restored | 20/06/2021 14:23 |
| Time Dispatched | 09:01 | Work Order Number | 501- 27091662 |
| Number of Interruptions | 1 | Duration of Interruptions | 14 Hrs |
| Network or Customers Affected | Both | Planned Outage? (Yes/No) | No |
| Approximate MVA hours lost | NA | Network or Customers still at risk (Yes/No) | Yes |
| Weather Conditions | Windy | Protection Details |  |
| Proposed Contingency Plans | Install vibration dampers Page 15 of 28 Table B.2: To determine the number of dampers required Arrangement of dampers per conductor 115m to 250m Number of dampers per span per conductor = 2 & 1 damper at each end |  |  |
| Root Cause of the Incident | Vibration. Line on uphill, severe wind cause vibration. |  |  |
| Summary of the Incident | At DDW 331A/56/62,Fox armrodding and conductor strands broke on red phase at suspension clamp, which caused steel wire to burn off and conductor fell to ground, load side, and caused veld fire on 19/06/2021. On 20/06/2021 10:12 Brkr at DDW 331A/1 was opened via Telecontrol. At DDW 331A/56/74 conductor broke and caused a veld fire on 01/11/2022. |  |  |
| Summary of Switching and Actions taken after the Incident | An employee was dispatched to a fault at Dridorp Dewetsdorp 22KV line (DDW331A/56/169/8 (WO 501-27091662 and the Ref Num: 35945) On arrival on site the employee discovered that the Red phase conductor was broken and lying on the ground which cause a veld fire. The operator took instruction to open isolate and earth and repair the fault and restore the supply to the customers affected. |  |  |
| Voltage Regulation within NRS048 | NA |  |  |
| Findings | Note 3: Ensure that only one joint is made in a span and no joints are made within a distance of 20 metres (240-75883906) from either side of the structure. Page 10 TM Conductor was repaired with splice at structure. No other joints between /61 & /62 and /62 & /63. Joints on all phases between /63 & /64 – Red phase repair sleeve/splice, White phase crimped sleeve , Blue phase Quick joint. Splice on White phase between /68 & /69. Wind blew from N -S. Span length between /62 & /63 = 124m. Poles 65,66,67,69 was replaced previously. Pole nameplate year 2013. |  |  |
| Line Maintenance / Pole Inspection Reports attached (In case of veld fires) |  |  |  |
| Proposed Recommendations to prevent recurrence | Install vibration dampers |  |  |
| I hereby Acknowledge that the Above Information provided by me is correct and to the Best of my Ability | Jaco Weldhagen |  |  |

| Approval of Investigation by Sector Manager | Comments and Action by Sector manager: Vibration dampers to be installed. Name: Korone Moea Date: 05/02/2024 Signature: …………………………………….. |
| --- | --- |

PHOTOS AND ANY OTHER SUBSTANTIATED DOCUMENTATION

| PROVINCIAL CLAIMS COMMITTEE USE ONLY |  |  |
| --- | --- | --- |
| Notes for consistency: - A note log to be kept of discussions regarding steps to be taken to prevent future incidents. - Eskom only responsible up to meter point, therefore the Customer is responsible for his own installation beyond this meter point. - Claims caused by stormy weather arising in December must be paid due to inconvenience caused to customers. - Ex Gratia payment: a minimum of 50% direct damage will be considered and based on the circumstances an amount higher than 50% will be considered based on consensus reached by the committee. - Veld Fire claims: Direct losses will be paid as per advice from the Agricultural extension officer of the Area. - Airdac in townships should be at a height of 4.7 meter as per EMR 15. - Staff needs to be sensitized as to the wording for root causes for normal deterioration. - Position where the LV neutral is broken will determine whether Eskom is liable. - Guiding principles for negligence: a) Deviation from the procedures, standards and legal requirements b) Reasonable steps not taken where it was required (Excluding major works & failure of major equipment) c) Omission or failure to act. - Damage due to strong winds causing poles to break (veldt set alight) will not be considered as a claim.- |  |  |
| QUESTIONS - Is Eskom liable? - Was fault attended to in a reasonable time? | Yes Yes | REMARKS: Equipment failure |

| PROVINCIAL CLAIMS COMMITTEE DECISION |  |
| --- | --- |
| PCC Decision:14.02.2024 Claim supported by PCC. PCC Decision 21.02.2024 The claim to be referred to legal for them to decide on behalf of the OU REASON: |  |
| POLICY | REASONS FOR REJECTION |
| There must be damage to Eskom property | No conclusive evidence could be detected on Eskom network linking the damage to an Eskom event. |
| Must be one sudden, unforeseen, specific or identifiable event | - Incident could not have caused the damage - Eskom not responsible for the cause of the fire |
| Proximate cause should not be due to parties external to Eskom | - Proximate cause due to persons external to Eskom |
| Power fluctuations/power failures are specifically excluded unless Eskom contributed to the fault. | - Phases incorrectly connected - Neutral burnt - Refer clause 6. 3 - Lack of maintenance - Fault repaired within a reasonable time. - Voltage Regulation was within the NRS048 |
| Act of God | - Eskom could not have foreseen - Customer could not have taken reasonable standard |
| Must be direct damage | - Consequential loss - Incorrectly disconnected - Cable damaged due to excavation activities in the area by non-Eskom contractor and highly unlikely that damaged cable could have caused damage to Customers equipment. - Fault on customer side |

6.3	Customers are cautioned that they should ascertain from ESKOM the nature of the protection 			provided on the supply and should provide adequate means for the protection of their own 			equipment.  Inter alia,

6.3.1	It is not practicable for ESKOM to install protective equipment on its system which will ensure in all 		cases that motors and/or other equipment on the CUSTOMER's side will be protected in the event 		of low voltage or over voltage or single-phasing. It is therefore necessary for the CUSTOMER to 		take adequate measures to protect his motors and/or equipment against damage that may arise 		under low voltage or over voltage conditions or from single-phasing;

6.3.2	Where a voluntary or involuntary outage of supply may cause damage to the CUSTOMER's plant or 		business, he should take measures to protect himself against such possible damage. (i.e. standby 		generator & personal Insurance (Especially a sensitive business) Should the CUSTOMER have, or 		decide to install, his own standby generating plant for use during such outages, the equipment for 		connecting such plant to his electrical installation shall be subject to ESKOM's approval.  Such 			standby plant shall be operated only during such outages and furthermore the use and operation 		thereof by the CUSTOMER shall be subject to such terms and conditions as ESKOM may lay down 		to ensure the safety and protection of its personnel and equipment.

20.	CONTINUITY, REDUCTION OR VARIATION OF SUPPLY

20.1	ESKOM shall take all reasonable precautions to procure and maintain suitable plant for the 			generation and distribution of electricity calculated to secure to its consumers a constant supply of 		electricity and shall procure efficient technical staff to control such plant, but ESKOM does not 			guarantee that the same will always be maintained, and ESKOM shall not be liable for damages, 		expenses or costs caused to the CUSTOMER from any interruption in the supply, variation of 			voltage, variation of frequency, any failure to supply a balanced three-phase current or failure to 			supply electricity unless the said interruption or failure is due to the negligence of ESKOM in failing 		to carry out its obligations aforesaid.  In the event that ESKOM should be liable for damage caused 		to the CUSTOMER as a result of any such reduction in load or any interruption in the supply, or any 		variation of voltage or frequency or any failure to supply electricity, such liability shall be limited to 		direct damage only.

20.2	For purposes of the efficient operation and extension of ESKOM's distribution system, or if ESKOM 		should experience any shortage of generating capacity, ESKOM shall have the right to interrupt the 		supply to the CUSTOMER