REQUEST FOR SUPPLY AND DELIVER OMICRON CMC356 IN SALT RIVER DEPOT

PROJECT DESCRIPTION: SUPPLY AND DELIVER OMICRON CMC356 IN SALT RIVER DEPOT

TRANSACTION: Request for Quotations

END USER: Infrastructure

(REGION / DEPARTMENT):   Western Cape

# Introduction

Omicron CMC 256-6 and CMC356 are the testing equipment that are used for testing all generations and types of protection relays. Its powerful current sources for testing are high-burden electromechanical relay. In Prasa we are using Omicron CMC256-6 with no failures but now it’s time to upgrade as the supplier will no longer be able to update the software hence it’s advised for Prasa to upgrade to the latest Omicron CMC 356 version.

- Scope of Works

The Contractor shall be responsible for the supply and delivery of material to Salt River depot, off-loading, installation, connecting, testing, and guarantees of the equipment, materials and labour on the following aspects of the works.

## 2.1 Description of the works

The Contractor shall be responsible for the supply, delivery, and handover of the CM356 Omicron. The scope of work will include the existing Omicron CMC 256-6 and to be traded in to the supplier.

The scope of work for this project shall entail the following activities:

- Supply and deliver Omicron CMC 356 including the following accessories:

- CMC 356 test hardware (4x300V and 6x32A)

- Ethernet patch cable 3 m  X 2

- USB connection cable 2 m  X 2

- ELT- DC analogue inputs, 10 analogue measuring inputs.

- Test Universe test modules: Quick CMC, State sequencer, ramping.

- Test Universe Control Centre software.

- Omicaddy mobile workstation with wheels.

- Supply Hardcover transport case with wheels.

- Supply: Manual, carry bag, power lead, connection lead to controller.

- Supply: Mini wireless USB adapter 2m generator lead, test lead and connecting accessories.

- Flexible test lead adapters with retractable sleeve (6 x red, 6 x black)

- Leads with 4 mm safety plugs (6 x red, 6 x black) 2 m

- Jumper flexible (4 x black) 6 cm / 2.4 in

- Grounding cable with battery clamp and M6 cable lug 6 m / 19.7

- Supply and deliver Test Universe Advanced Differential Relay test module (VESM1160)

- Supply and deliver Test universe Distance Relay test mode (VESM1111)

- Supply and deliver Test Universe Overcurrent Relay test module (VESM113)

# Specification:

### Technical requirements:

- Auxiliary DC Supply 0 – 264 V

- 4 x Binary outputs.

- Voltage outputs: 4 x 300 V or 2 x 600 V

- Current outputs:

6 x 32 A / 6 x 430 VA

3 x 64 A / 3 x 860 VA

1 x 128 A / 1x 1000 VA

- Generator combination socket : 3 x 300 V and 3 x 32 A

- DC measuring inputs: 0 ... 10 V and 0 ... 20 mA

- 10 x multifunctional inputs: binary (dry/wet)

- CMC 356 test hardware (4x300V and 6x32A)

## Local Content

| No | Some equipment against which the local content must be discharged |  |  |
| --- | --- | --- | --- |
|  | Equipment | Quantity | % Local Content |
| 1 | 3m Ethernet patch cable | 2 | 90 |
| 2 | 2m USB connection cable | 2 | 90 |
| 3 | Flexible test lead adapters with retractable red sleeve | 6 | 90 |
| 4 | Flexible test lead adapters with retractable black sleeve | 6 | 90 |
| 5 | 2m Leads with 4 mm safety plugs red. | 6 | 90 |
| 6 | 2m Leads with 4 mm safety plugs black. | 6 | 90 |
| 7 | 6cm Jumper flexible black. | 4 | 90 |
| 8 | Grounding cable with battery clamp | 1 | 90 |
| 9 | M6 cable lug 6 m | 1 | 90 |
| 10 | Soft carrying Bag | 1 | 100 |

NB: 90% that is on page 37 of the RFQ refers only to the cable not to the Omicron (the component)

| PRASA WESTERN CAPE SUPPLY AND DELIVER OMICRON CMC356 IN SALT RIVER |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Bill of Quantities- SUPPLY AND DELIVER OMICRON CMC356 IN SALT RIVER |  |  |  |  |  |
| Item | Bill Description | Unit | QTY | Total Rate | Amount |
| 1 | Material cost |  |  |  |  |
| 1.1 | Supply and deliver omicron CMC356 in Salt River with accessories | Sum | 1 |  |  |
| 1.2 | Test Universe Advanced Differential Relay test module (VESM1160) | Sum | 1 |  |  |
| 1.3 | Test universe Distance Relay test mode (VESM1111) | Sum | 1 |  |  |
| 1.4 | Test Universe Overcurrent Relay test module (VESM1130) | Sum | 1 |  |  |
| 1.5 | TOTAL |  |  |  |  |
| 1.6 | Software Discount for trading in of CMC 256-6 | Sum | 1 |  |  |
| 1.7 | Test Universe Differential test module | Sum | 1 |  |  |
| 1.8 | Test Universe Distance Relay test module | Sum | 1 |  |  |
| 1.9 | Test Universe Overcurrent Relay test | Sum | 1 |  |  |
| 1.10 | TOTAL |  |  |  |  |
|  | Subtract total 1.10 from total 1.5 |  |  |  |  |
|  | WORKS SUB-TOTAL (EXCLUDING VAT) |  |  |  |  |
|  | VAT (15%) |  |  |  |  |
|  | CONTRACT TOTAL (INCLUDING VAT AND PROVISIONAL SUM) |  |  |  |  |