BID SPECIFICATION: RFB 3183/2025 REQUEST FOR BID FOR THE APPOINTMENT OF A SERVICE PROVIDER TO SUPPLY AND INSTALL LOW VOLTAGE DISTRIBUTION BOARDS AND CABLING AT SITA CENTURION FOR A PERIOD OF 30 MONTHS.

TECHNICAL, PRICING AND PREFERENCE POINTS REQUIREMENTS

# Contents

1.	Introduction and background	4

1.1.	Purpose	4

1.2.	Background	4

2.	Scope of Bid	4

2.1.	Scope of Work	4

2.2.	Delivery address	4

3.	Requirements	5

3.1.	Solution Requirements	5

4.	Bid Evaluation Stages	6

4.1.	Mandatory Administrative Responsiveness (Stage 1)	6

4.1.1.	Attendance of briefing session	6

4.1.2.	Registered Bidder	6

4.1.3.	Bid Submission Instructions	6

4.2.	Technical Returnable Documents	7

4.2.1.	Instruction and evaluation criteria	7

4.2.2.	Technical Mandatory Requirements (Stage 2)	8

4.3.	Special Conditions of Contract Verification (Stage 3)	11

4.3.1.	Special Conditions of Contract	12

4.3.2.	Declaration of compliance and acceptance SCC	23

4.4.	Costing and Preference Points Evaluation (Stage 4)	23

Annex A: Bidder Substantiating Evidence	36

5.	Technical Mandatory Requirement Evidence	36

5.1.	Bidder Certification / Affiliation Requirements	36

5.2.	Bidder Experience and Capability Requirements	36

5.3.	CIDB Registration Requirements	37

5.4.	Key Personnel Qualification: Project Manager	37

5.5.	Electrical Distribution Boards Data Sheet	37

5.6.	Electrical Distribution Boards General Arrangement Drawings	38

5.7.	Third Party Risk Management Assessment	38

5.8.	Special Conditions of Contract Acceptance	38

5.9.	Preference Points Preferential Goals Evidence	38

Annex B: CIDB Registration Requirement	41

Annex C: Technical Information	42

6.	Technical Information	42

Annex D: Local Content Requirements	43

7.	Local Content Requirements:	43

7.1.	The bidder must confirm compliance to the Local Content requirements.	43

7.2.	The following documents are attached to guide guidance in completing the Local Content requirements:	43

7.3.	The Bidder must complete, sign and submit the following documents at bid closure:	43

Annex E: Third-Party Risk Management (TPRM) Assessment	44

8.	Instructions	44

8.1	44

8.1.1.	Company risk	44

8.1.2.	All questions for all other risk elements:	45

8.2.	Third Party Risk Assessment	45

8.3.	Third Party Risk Management Declaration	48

8.3.1.	Declaration of Acceptance	48

Annex F: CIDB Basic Guide General Conditions of Contract for Construction Works (GCC 2004)	50

# Introduction and background

## Purpose

The purpose of this RFB is to invite Suppliers (hereinafter referred to as “bidders”) to submit bids for “Request for Bid for the Appointment of a Service Provider to Supply and Install low voltage distribution boards and cabling at Sita Centurion for a period of 30 months. (18 Months construction period and 12 months warranty period).

## Background

The electrical infrastructure at the data centre is close to the end of life, which leads to several challenges regarding availability, short to medium-term maintenance planning, and medium to long-term growth planning. The low voltage distribution boards upgrades will make the SITA Centurion facility to have a higher- level reliability and availability of the electrical infrastructure for the mission critical environments.

# Scope of Bid

## Scope of Work

The scope of work by the bidders is for the supply, installation and commissioning of low voltage electrical distribution boards and cabling at SITA Centurion which includes:

- Preliminary and Site establishment enabling works at SITA Centurion Data Centre, ensuring readiness for project execution.

- Supply, installation, and commissioning of Distribution Boards, including the provision of suitable mounting frames as per Single Line Drawings in Annex C section 6 The distribution boards shall be Schneider PrismaSet Active.

- Supply, installation, and commissioning of low voltage interconnections, including necessary modifications to existing busbar trunking systems to accommodate the newly installed distribution boards.

- Modification and extension of existing indoor generator synchronization boards, including the reprogramming of indoor generators to align with the updated configuration and ensure seamless integration.

- Supply and installation of cabling, including all terminations required to complete the system integration in line with project specifications and safety standards.

- Dismantling and removal of obsolete cabling and associated busbar trunking systems to make way for the new installation.

- Integration of the new equipment to the power monitoring system. Existing system is Power Monitoring Expert.

- General electrical works to complete the installation.

- Safe removal and disposal of the existing distribution boards as part of the upgrade and modernization of the electrical infrastructure.

## Delivery address

Table 1: Delivery address

| No | Site Name | Physical Address |
| --- | --- | --- |
| 1 | SITA Centurion | 1108 John Vorster Drive, Centurion, Pretoria |

# Requirements

## Solution Requirements

The supply, delivery and installation of the electrical distribution boards. This will include but not be limited to the following:

  - Preliminary and general site establishment activities.

  - Manufacturing and factory acceptance testing of electrical distribution boards, including integrated protection and control schemes.

  - Delivery and offloading of electrical distribution boards to the site.

  - Installation of new electrical distribution boards.

  - Testing and commissioning of the newly installed electrical distribution boards.

  - Removal and disposal of old electrical distribution boards from the LV room.

  - Removal of redundant electrical cabling and busbar trunking.

  - Modifications to the existing low voltage connections for the generator supplies in the main LV room and UPS room, and extension of the HVAC main supply busbar trunking to Generators 3 and 4 room.

  - Termination of existing electrical cabling into the new LV distribution boards.

  - Supply and installation of low voltage connections, including terminations and earthing, from the new main LV distribution boards in the main LV room to the input side of the UPS units located in the UPS rooms.

  - Supply and installation of low voltage connections from the existing electrical transformers in the main transformer room to the existing main LV distribution board in the main LV room.

  - Supply and installation of low voltage connections, including terminations and earthing, from the new main LV distribution boards in the main LV room to the new mechanical LV distribution boards located in Block E plant rooms for HVAC systems and chillers.

  - Supply and installation of low voltage connections, including terminations and earthing, from the new mechanical LV distribution boards in Block E to HVAC mechanical equipment such as chillers and pumps.

  - Disconnection, modification, and termination of existing LV cables from the outside container generator G5 to the new G5 LV distribution board.

  - Supply and installation of low voltage connections from the existing main LV distribution board to new LV distribution boards within the main LV room.

  - Modifications and reconfiguration of the existing synchronisation panels of Generators G1 to G4 to suit the new electrical reticulation configuration.

  - Supply and installation of low voltage connections from the new G5 LV distribution board to new LV distribution boards within the main LV room.

  - Supply and installation of low voltage connections from the SP3-4 LV distribution board in the indoor generator room to the LV DB3&4 in the main LV room.

  - Provision of all operating manuals and participation in the final handover process.

  - Provision of 12 months of warranty on the new distribution boards.

  - Builder’s works, including creation of openings in walls for cable or busbar routing, installation of heavy-duty epoxy flooring, wall plastering, and painting.

  - General electrical works to complete the installation

  - Provision and installation of a complete fire protection system, including detection, alarm, and suppression, suitable for indoor electrical installations.

# Bid Evaluation Stages

The bid evaluation process consists of several stages, according to the nature of the bid. A bidder must qualify for each stage to be eligible to proceed to the next stage of the evaluation.

The stages are:

Table 2: Bid Evaluation Stages

| Stage | Description | Applicable for this bid YES/NO |
| --- | --- | --- |
| Stage 1 | Mandatory Administrative Responsiveness | YES |
| Stage 2 | Technical Mandatory Requirements | YES |
| Stage 3 | Special Conditions of Contract Verification | YES |
| Stage 4 | Costing and Preference Points Evaluation | YES |

## Mandatory Administrative Responsiveness (Stage 1)

### Attendance of briefing session

- A Compulsory Virtual Briefing session will be held. The bidder has to sign the briefing session attendance register using the same information (bidder company name, bidder representative person name and contact details) as submitted in the bidder’s response document.

Note (1):	Bidder who wishes to attend the Compulsory Virtual Briefing Session needs to notify the responsible Specialist indicated in the Bid Document of attending the session. The link to the Compulsory Virtual Briefing Session will then be sent to those Bidders.

Note (2):	Any bidder who fails to attend the compulsory briefing session will be disqualified.

Note (3):	A non-compulsory site visit will be arranged on request by the bidders.

### Registered Bidder

- Only responses from bidders who are registered as a Bidder on National Treasury’s Central Bidder Database (CSD) in terms of National Treasury’s Instruction Note 4A of 2016/17 will be considered for award on this RFB.

- In the case of joint ventures or consortiums the bidder must demonstrate that at least one of the parties to the bid response attended the briefing session.

- Bidders need to complete all the SBD documents which needs to be submitted as stated in the Invitation to Bid Document.

### Bid Submission Instructions

Note that a Two Envelope process will be followed and therefore bidders must submit as follows:

- Envelope 1: RFB Document and Technical / Functionality Response

# The following must be included and submitted in a in a separate envelope:

  - One (1) original file excluding pricing; and

  - One (1) hard copy excluding pricing; and

  - One (1) electronic copy on USB memory stick/ flash drive in Portable Document Format (PDF) of the RFB Document and Technical / Functionality Response.

- Envelope 2: Price Response

# The following must be included and submitted in a in a separate envelope:

  - One (1) original file excluding Technical / Functionality Response; and

  - One (1) hard copy excluding Technical / Functionality Response; and

  - One (1) electronic copy on USB memory stick/ flash drive in Portable Document Format (PDF) of pricing only.

- It is the Bidder’s responsibility to ensure that the information and contents on the electronic copies is the same as in the hard copies.

- To ensure that the electronic copies are not damaged, the bidder must submit the USB’s (memory stick/ flash drive) in a sealed padded envelope and be clearly marked.

- Bidders shall submit Bid responses in accordance with the prescribed manner of submission as specified above. Failure to comply with the above instructions on submitting a proposal will lead to disqualification.

- The RFB Responses (hard and electronic copies) must be clearly marked as follows: Bidder’s Name & Contact Details, RFB Number, RFB Description, and Closing Date.

- All Bids in this regard shall only be accepted if they have been placed in the tender box before or on the closing date and stipulated time.

- Late bids shall not be considered.

- The Bid response must be signed by an authorised employee, agent or representative of the bidder. The Bid response Bid must bear the initials of the signatory at the bottom of every page as an indication that the bidder has familiarised itself with the terms and conditions of this RFB document.

- Faxed or e-mailed bids will not be accepted.

- Bidders shall submit Bid responses in accordance with the prescribed manner of submission as specified in this document. Failure to comply with the bid submission requirements will lead to disqualification.

- Bidders are required to submit all returnable documents/information together with their Bids/proposals on or before the closing time and date of the Bids/proposals.

- All services supplied in accordance with the bidder’s proposal must be in accordance with all applicable legal requirements in terms of South African law, policies and regulations.

## Technical Returnable Documents

### Instruction and evaluation criteria

- The Bidder must comply with ALL the requirements as per the Technical Mandatory Requirements below by providing substantiating evidence in the form of documentation or information, failing which it will be regarded as “NOT COMPLY”.

- The Bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response.

- The Bidder must comply with ALL the TECHNICAL MANDATORY REQUIREMENTS in order for the bid response to proceed to the next stage of the evaluation.

### Technical Mandatory Requirements (Stage 2)

Table 3: Technical Mandatory Requirements

| Mandatory Requirements | Substantiating evidence of compliance (used to evaluate bid) | Evidence reference (to be completed by bidder) |
| --- | --- | --- |
| 1. Bidder Certification/ Affiliation Requirements |  |  |
| The Bidder must be registered as an Electrical Contractor with the Department of Labour. | Attach to ANNEX A copy of valid of Letter from the Department of Labour as evidence that the bidder is registered as an Electrical Contractor. NOTE (1): SITA reserves the right to verify the information provided. | <provide a unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.1> |
| 2. Bidder Experience and Capability Requirements |  |  |
| The bidder must have executed the Low Voltage Electrical Installations involving Distribution Boards or Busbar Trunking Systems of a minimum size of 1600A at a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Manufacturing Facility) to at least two (2) customers/projects in the last five (5) years from the publication date of this Bid. | The Bidder must complete table 10 by providing reference details from two (2) customers/projects to whom Low Voltage Electrical Installations involving Distribution Boards or Busbar Trunking Systems of a minimum size of 1600A at a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Manufacturing Facility) to at least two (2) customers/projects in the last five (5) years from the publication date of this bid. - Company name; and - Reference Person Name, Tel and/or email; and - Project Scope of Work; and - Project Start and end date. NOTE (1): The Bidder must provide all of the following information when completing table 10. NOTE (2): Failure to comply fully with the abovementioned requirements will result in disqualification. NOTE (3): SITA reserves the right to verify the information provided. | <provide a unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.2, table 10> |
| 3. CIDB Registration Requirement |  |  |
| The Bidder must be registered with the Construction Industry Development Board (CIDB) and have a minimum rating of 8EB or 8EP or higher. | The Bidder must complete and sign ANNEX B as evidence that the Bidder, is registered with the CIDB with a minimum rating 8EB, or 8EP or higher. NOTE (1): SITA reserves the right to verify the information provided. | <provide a unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.3 and Annex B> |
| 4. Key Personnel Qualification: Project Manager |  |  |
| The Bidder must provide a qualified Project Manager with a minimum of five (5) years’ post professional registration. The professional registration be either one (1) of the following: - ECSA, Professional Engineer (Pr Eng), or - ECSA, Professional Certificated Engineer, or - ECSA, Professional Engineering Technologist, or - ECSA, Professional Engineering Technician, or - PMI, Project Management Professional (PMP), or - SACPCMP, Professional Construction Project Managers. | Attach to Annex A copy of a valid Registration Certificate indicating that the Project Manager has been registered as a professional for a minimum of five (5) years post professional registration. The professional registration be either one (1) of the following: - ECSA, Professional Engineer (Pr Eng), or - ECSA, Professional Certificated Engineer Technician, or - ECSA, Professional Engineering Technologist, or - ECSA, Professional Engineering Technician, or - PMI, Project Management Professional (PMP), or - SACPCMP, Professional Construction Project Managers. NOTE (1): SITA reserves the right to verify the information provided. NOTE (2): SITA reserves the right to verify the consent from the registered person. NOTE (3): The Bidder must also provide registered person contact details by completing table 10. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.4 par table 11> |
| 5. Electrical Distribution Boards Data Sheet |  |  |
| The Bidder must comply with the specifications by completing and submitting signed equipment data sheets listed in Annex C. - SITA Centurion LV BOARDS Data Sheets - SITA Centurion DB-G5 Data Sheets | Attach to Annex A completed and signed Data Sheets: - SITA Centurion LV BOARDS Data Sheets - SITA Centurion DB-G5 Data Sheets Note (1): Total two (2) data sheets are to be submitted. Note (2): SITA reserves the right to verify the information provided. Note (3): The data sheet information will be applicable with all other distribution boards. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.5 and Annex C> |
| 6. Electrical Distribution Boards General Arrangement Drawings |  |  |
| The Bidder must comply with the specifications by submitting General Arrangement Drawings of Distribution Boards for the following Single Line Diagrams: - 1001547-DRG-EL-100-LV-A - 1001547-DRG-EL-700-DB-G5 - 1001547-0000-DRG-EL-900-T0-MECH DB-A | Attach to Annex A copies of General Arrangement drawings of the following Single Line Diagrams: and signed Data Sheets: - 1001547-DRG-EL-100-LV-A - 1001547-DRG-EL-700-DB-G5 - 1001547-0000-DRG-EL-900-T0-MECH DB-A Note (1): Total three (3) GA drawings that are to be submitted. Note (2): SITA reserves the right to verify the information provided. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.6 |
| 7. Third Party Risk Assessment |  |  |
| The Bidder must confirm compliance to Third-Party Risk Management Assessment. | The Bidder must comply to the Third-Party Risk Management Assessment requirement by completing All the questions in Annex E. Note (1): SITA reserves the right to verify information provided. Note (2): Failing to complete all the questions, or not Accepting the Declaration of Acceptance above will result in disqualification. | <Provide unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.7 and Annex E> |
| 8. Special Conditions of Contract Acceptance |  |  |
| Bidder must accept ALL the Special Conditions of Contract (SCC) as stated in section 4.3. | The Bidder must accept ALL the Special Conditions of Contract (SCC) as stated in section 4.3, by signing in the declaration of compliance and acceptance of SCC in section 4.3.2 Note (1): Failure to accept ALL the Special Conditions of Contract will result in disqualification. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.8 |

## Special Conditions of Contract Verification (Stage 3)

- The successful Bidder will be bound by Government Procurement: General Conditions of Contract (GCC) as well as this Special Conditions of Contract (SCC), which will form part of the signed contract with the successful Bidder. However, SITA reserves the right to include or waive the condition in the signed contract.

- SITA reserves the right to:

  - Negotiate the conditions; or

  - Automatically disqualify a bidder for not accepting these conditions; or

  - Award to multiple bidders; or

  - Not to award; or

  - To do a partial award.

- In the event that the bidder qualifies the proposal with own conditions and does not specifically withdraw such own conditions when called upon to do so, SITA will invoke the rights reserved in accordance with subsection 4.3. (b) above.

### Special Conditions of Contract

#### Contracting Conditions

- Formal Contract - The Bidder must enter into a formal written contract (agreement) with SITA.

- Right of Award - SITA reserves the right to award the contract for required goods or services to multiple Bidders.

- Right to Audit - SITA reserves the right, before entering into a contract, to conduct or commission an external service provider to conduct a financial audit or probity to ascertain whether a qualifying bidder has the financial wherewithal or technical capability to provide the goods and services as required by this tender.

#### Delivery Address

- The Bidder must deliver the required products or services at as indicated in Section 2.2, Delivery Address

#### Delivery Schedule

  - The scope of work (Section 2.1) and Section 3 (Requirements) must be completed within 18 months after the contract has been awarded for decommission, supply, install and commissioning of the new equipment.

  - Construction period will be limited to a period 18 months. The 12 months warranty period that will commence immediately after handover and commissioning of the distribution boards. Total contract period will be 30 Months.

  - The Bidder is responsible for performing the work as outlined in the following Work Breakdown Structure (WBS):

Table 4: Work Breakdown Structure (WBS)

| WBS | Statement of Work | Delivery Timeframe |
| --- | --- | --- |
|  | Preliminary, General and Site Establishment; | TBC with Successful Bidder and limited to maximum 18months |
|  | Manufacturing and Factory Acceptance Testing of electrical distribution boards complete with integrated protection and control schemes; |  |
|  | Delivery and Off Loading of electrical distribution boards; |  |
|  | Supply and Delivery Cabling and terminations; |  |
|  | Installation of new electrical distribution boards; cabling and terminations |  |
|  | Testing and Commissioning of new electrical distribution boards. |  |
|  | Modification and extension of the existing indoor generator synchronization |  |
|  | Removal of old cabling and connections |  |
|  | Removal of old distribution boards |  |
|  | 12 Months warranty on the new installed equipment |  |

#### Penalties

- A penalty of 15% of the monthly contract value or any specific deliverable may be imposed if it is found that the Service Provider failed to meet agreed deliverables, and such failure was not caused by a failure of the client to comply with its obligations.

- Where penalties are imposed, the relevant monthly invoice will be reduced by the penalty amount or a credit note for the penalty amount will be submitted to SITA within 2 (two) months of the target not being met.

SITA reserves the right to enforce these penalties, or not, depending on the merit of each case.

#### Services and Performance Metrics

  - During Warranty and Maintenance periods the Bidder is responsible to provide the following services as specified in the Service Breakdown Structure (SBS):

Table 5: Service Breakdown Structure

| SBS | Service Element | Service Level |
| --- | --- | --- |
|  | Emergency Contact during warranty period | 24h x 7days x 52weeks |
|  | Incident Response during warranty period | Maximum 90-minutes |

#### Bidder Performance Reporting

- The Bidder will report to SITA monthly during the design and manufacturing phase of the project; monthly written reports will be presented to SITA on the progress until delivery of the equipment.

- The Bidder will report to SITA/Client on a bi-weekly basis during the installation and implementation phase of the project; bi-weekly written reports will be presented to the SITA/Client on the progress of the preceding week until the installation process has been completed.

- The Bidder is required to generate regular reports as outputs during the maintenance and support cycle within the following service levels (the report type will drive the service level agreement; definition of the content of each report type will be finalised at the time of concluding the contracted service level agreement).

#### Certification, Expertise and Qualification

  - The Bidder must be registered at the Department of Labour as an Electrical Contractor

  - The bidder must have executed the Low Voltage Electrical Installations involving Distribution Boards or Busbar Trunking Systems of a minimum size of 1600A at a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Manufacturing Facility) to at least two (2) customers/projects in the past five (5) years.

  - The Bidder or subcontractor must be registered with the Construction Industry Development Board (CIDB) with a minimum rating of 8EB or 8EP.

  - The Bidder must provide a qualified Project Manager with a minimum of five (5) years’ post professional registration. The professional registration be either one (1) of the following:

    - ECSA, Professional Engineer (Pr Eng), or

    - ECSA, Professional Certificated Engineer Technician, or

    - ECSA, Professional Engineering Technologist, or

    - ECSA, Professional Engineering Technician, or

    - PMI, Project Management Professional (PMP), or

    - SACPCMP, Professional Construction Project Managers.

  - The Bidder must confirm the manufacturing and assembly of the distribution boards compliance with IEC 61439 for Low-voltage switchgear and control-gear assembly.

  - The Bidder must comply with the specifications by completing and submitting signed equipment data sheets listed in Annex C:

    - SITA Centurion LV BOARDS Data Sheets

    - SITA Centurion DB-G5 Data Sheets

  - The Bidder must comply with the specifications by submitting General Arrangement Drawings of Distribution Boards for the following Single Line Diagrams:

    - 1001547-DRG-EL-100-LV-A

    - 1001547-DRG-EL-700-DB-G5

    - 1001547-0000-DRG-EL-900-T0-MECH DB-A

  - The Bidder represents that,

    - it has the necessary expertise, skill, qualifications and ability to undertake the work required in terms of the Statement of Work or Service Definition and;

    - it is committed to provide the Products or Services; and

    - perform all obligations detailed herein without any interruption to the Customer.

  - The Bidder must provide the service in a good and workmanlike manner and in accordance with the practices and high professional standards used in well-managed operations performing services similar to the Services;

  - The Bidder must perform the Services in the most cost-effective manner consistent with the level of quality and performance as defined in Statement of Work or Service Definition;

  - Original Equipment Manufacturer (OEM).

    - The Bidder must ensure that work or service for the commissioning of the new equipment is performed by a person who is certified by Original Equipment Manufacturer and the certification will be included in the commissioning reports and handover documents.

    - The Bidder shall provide copy of OEM letter of verification of the electrical distribution boards.

#### Logistical Conditions

  - Hours of work, 08h00 – 16h00.

  - Provision to be made for work which will be Saturday and Sunday.

  - Provision for the installation and commissioning of the equipment to be made during scheduled downtime, which will be from Friday midnight to Sunday morning for a maximum of one weekend. The Supplier must make sure all the resources, tools, and equipment are available to work continuously during that period to complete all the scheduled tasks.

  - Centurion Data Centre is a live site, and downtimes are limited. All site services must be restored at the end of the scheduled downtime.

  - The installation and commissioning that does not require downtime can be completed during hours 7(a) and 7(b).

  - In the event that SITA grants the Supplier permission to access SITA's Environment including hardware, software, internet facilities, data, telecommunication facilities and/or network facilities remotely, the Supplier must adhere to SITA's relevant policies and procedures (which policy and procedures are available to the Supplier on request) or in the absence of such policy and procedures, in terms of, best industry practice.

  - Tools of Trade. The Supplier must bring their necessary tools of trade to perform their duties adequately.

  - On-site and Remote Support. The Bidder must provide both on-site and remote support, and only when off-site support is not sufficient will on-site support be required upon approval by the SITA representative.

  - Support and Help Desk. After-hours helpdesk support is required for the first three months per site during weekdays, including weekends and public holidays.

  - Scheduled Maintenance: This includes site travel, labour, materials, tools, consumables, and the specified service pack.

  - Designs and Approvals. Detail design drawings shall be submitted for approval before manufacturing may start.

  - Manufacture and Supply: Manufacture and delivery to Site is included in the SOW. The Bidder shall be responsible for all transport risks and arranging for the necessary site access permits.

  - IEC 61439 Compliance: The Bidder must confirm the manufacturing and assembly of the distribution boards in compliance with IEC 61439 for Low-voltage switchgear and control-gear assembly by providing a copy of a certificate of conformity to IEC 61439 for Low-voltage. The bidder to provide copy of OEM letter of verification of the electrical distribution boards.

  - Factory Acceptance Testing. On completion and approval of all pre-FAT documentation, the switchgear supplier will commence with the functional testing of protection schemes. The employer will be notified at least 2 weeks in advance before FAT commences to allow the employer or their representative to witness these tests. Once these tests are completed, the Employer will verify the test results and request to witness specific items.

    - Panels are undamaged

    - The distribution boards are square and level

    - Connections are labelled in accordance with single line diagrams

    - Doors and access panels open freely.

    - Minimum clearance requirements have been provided around cabinets

    - Inspect input & output switchboards to confirm the following:

    - Correct labelling of circuit breakers & Switchboards

    - Correct labelling of power, signal and control cables

    - Correct settings have been applied to circuit breaker protection relay

  - Installation and Pre-Commissioning: The tests shall include, but not be limited to the following:

    - Final positions of equipment shall be agreed with the Engineer on site, prior to installation.

    - All equipment shall be securely mounted using propriety (i.e., suited to and manufactured for such use) fixtures and fittings.

    - The method of equipment installation shall not adversely affect the function or structural integrity of the structure to which the equipment is attached.

    - Equipment terminals and covers shall be readily and safely accessible after installation.

    - The method of equipment installation shall not adversely affect the IP rating of the equipment.

    - Installation and commissioning of the equipment under this scope that require electrical power shutdown will be limited to approved change periods.

    - Installation of the Switchboard, power cables, control cables, auxiliary cables and earthing is included. Any Civil work required to do the installation is included

    - A Detailed SAT plan, detailing the various role players, SAT process, commissioning schedule and check sheets shall be submitted for approval 4 weeks before the actual SAT.

    - On completion of installation (after all the equipment have been installed and set up on site), Site Acceptance Testing (SAT) shall be carried out by the Bidder and witnessed by the Employer and the Project Manager. The SAT shall include cold and hot Commissioning.

    - Perform a visual inspection of the installation.

    - Record the Serial Number of the unit and any ancillary cabinets under test. Cross check against Serial Number recorded during Factory Acceptance Testing

    - Distribution Boards are undamaged.

    - Distribution Boards are square and level.

    - Connections are labelled in accordance with single line diagrams.

    - Doors and access panels open freely.

    - Minimum clearance requirements have been provided around cabinets

    - Connected cables have been terminated and shrouded correctly with adequate bending radii provided and suitable support brackets provided.

    - Inspect input & output switchboards to confirm the following:

    - Correct labelling of circuit breakers & Switchboards.

    - Correct labelling of power, signal and control cables.

    - Correct settings have been applied to circuit breaker protection relays.

    - Commissioning Requirements. The Bidder shall provide experienced test personnel as well as an experienced and competent test Engineer to undertake and supervise all the commissioning tests.  The test Engineer shall work in conjunction with the Employer’s representatives on site and shall always co-operate with these representatives.

    - Check list for cleaning of panels.

    - All operational tests will be verified by the SITA representatives to ensure that the tests have been performed, and the results were acceptable.

    - Final energisation authority and outage co-ordination will be the responsibility of SITA. If applicable, the Bidder shall submit a request for outage at least 14 days in advance for any further de-energised testing.

    - Infra-Red scan on all the connections.

  - Commissioning Requirements. The Bidder shall provide experienced test personnel and an experienced and competent test Engineer to undertake and supervise all the commissioning tests. The test Engineer shall work in conjunction with the Employer’s representatives on site and shall always cooperate with these representatives.

    - Check list for cleaning of cabinets.

    - All operational tests will be verified by the SITA representatives to ensure that the tests have been performed, and the results were acceptable.

    - Infra-Red scan on all the connections.

    - SANS 10142 COC by Master Electrician

#### Skills Transfer and Training

  - The Bidder must provide training on the proposed solution to technical staff and operators to enable SITA to operate and support the product or solution after implementation. The training would be informal.

  - The Bidder to submit all the necessary documentation such as COCs, commissioning sheets, record drawings (as built), operation and maintenance manuals for all the equipment.

#### Regulatory, Quality and Standards

- The Bidder must for the duration of the contract ensure compliance with ISO/IEC General Quality Standards, and Protection of Personal Information Act (POPIA).

- The Bidder must for the duration of the contract ensure compliance with General Quality Standards, ISO 9001.

- The Bidder must for the duration of the contract ensure compliance with the project specification and listed standards:

- IEC 62040-1:	Uninterruptible power systems (UPS) – Part 1: General and safety requirements for UPS

- IEC 62040-2:	Uninterruptible power systems (UPS) – Part 2: Electromagnetic compatibility (EMC) requirements

- IEC 62040-3:	Uninterruptible power systems (UPS) – Part 3: Method of specifying the performance and test requirements.

- IEC 60204:		Safety of machinery. Electrical equipment of machines.

- IEC 60269:		Low-voltage fuses.

- IEC 60529:		Degrees of protection provided by enclosures (IP Code)

- IEC 61558:		Isolating transformers and safety isolating transformers.

- IEC 61000:		Electromagnetic compatibility (EMC)

- IEC 61643-1:	Low-voltage surge protective devices Part 1: Surge protective devices

connected to low-voltage power distribution systems

- The Bidder must for the duration of the contract ensure compliance with the project specification and listed standards:

  - SITA Electrical Technical Specification

#### Company and Personnel Security Clearance Requirements

  - Company security screening: The supplier may be required to undergo a company security screening conducted by the State Security Agency (SSA). Should the SSA find the supplier not suitable after the conduct of the security screening, the business relationship will be terminated. The following documentation will be required for the company security screening process to be conducted:

    - Copy of company registration documentation;

    - Copy(ies) of identity documentation of Director(s), Member(s) or Trustee(s);

    - Copy of valid tax clearance certificate.

  - Security suitability check for individuals: SITA may, at its own discretion and in line with its policies and procedures, require employees of the supplier to be subjected to a security suitability check before commencement of a project or delivering of a service. The security suitability check is conducted by SITA in order to ensure that individuals meet the minimum security requirements and also to verify personal information. The supplier will be required to replace any employee(s) who is found to be not suitable after the conduct of the security screening. The following documentation will be required for the security suitability check:

    - Copy of identity document;

    - Copy(ies) of qualification(s) if SITA requires verification thereof;

    - Fingerprints – will be taken electronically;

    - Signed consent form for the conduct of background checks.

  - Security clearance: A security clearance, issued by either the SSA or Defence Intelligence (DI) is required if any employee of the supplier will have or may gain access to classified information throughout the duration of the project or in the process of delivering a service. The level of security clearance required – Confidential, Secret or Top Secret, will be determined at the sole discretion of SITA. The supplier will have to replace any employee who do not qualify for a security clearance or is found not suitable by the SSA or DI. The following documentation will be required for the security clearance process:

    - Completed Z204 or DD1057 security clearance application form;

    - Fingerprints;

    - Personal documentation of the applicant, including but not limited to, identity document, passport, marriage certificate (if applicable), divorce order (if applicable), qualifications, salary advice and bank statements.

#### Confidentiality and non -disclosure conditions

- The Bidder, including its management and staff, must before commencement of the Contract, sign a non-disclosure agreement regarding Confidential Information

- Confidential Information means any information or data, irrespective of the form or medium in which it may be stored, which is not in the public domain and which becomes available or accessible to a Party as a consequence of this Contract, including information or data which is prohibited from disclosure by virtue of:

  - the Promotion of Access to Information Act, 2000 (Act no. 2 of 2000);

  - being clearly marked "Confidential" and which is provided by one Party to another Party in terms of this Contract;

  - being information or data, which one Party provides to another Party or to which a Party has access because of Services provided in terms of this Contract and in which a Party would have a reasonable expectation of confidentiality;

  - being information provided by one Party to another Party in the course of contractual or other negotiations, which could reasonably be expected to prejudice the right of the non-disclosing Party;

  - being information, the disclosure of which could reasonably be expected to endanger a life or physical security of a person;

  - being technical, scientific, commercial, financial and market-related information, know-how and trade secrets of a Party;

  - being financial, commercial, scientific or technical information, other than trade secrets, of a Party, the disclosure of which would be likely to cause harm to the commercial or financial interests of a non-disclosing Party; and

  - being information supplied by a Party in confidence, the disclosure of which could reasonably be expected either to put the Party at a disadvantage in contractual or other negotiations or to prejudice the Party in commercial competition; or

  - information the disclosure of which would be likely to prejudice or impair the safety and security of a building, structure or system, including, but not limited to, a computer or communication system; a means of transport; or any other property; or a person; methods, systems, plans or procedures for the protection of an individual in accordance with a witness protection scheme; the safety of the public or any part of the public; or the security of property; information the disclosure of which could reasonably be expected to cause prejudice to the defence of the Republic; security of the Republic; or international relations of the Republic; or plans, designs, drawings, functional and technical requirements and specifications of a Party, but must not include information which has been made automatically available, in terms of the Promotion of Access to Information Act, 2000; and information which a Party has a statutory or common law duty to disclose or in respect of which there is no reasonable expectation of privacy or confidentiality;

- Notwithstanding the provisions of this Contract, no Party is entitled to disclose Confidential Information, except where required to do so in terms of a law, without the prior written consent of any other Party having an interest in the disclosure;

- Where a Party discloses Confidential Information which materially damages or could materially damage another Party, the disclosing Party must submit all facts related to the disclosure in writing to the other Party, who must submit information related to such actual or potential material damage to be resolved as a dispute;

- Parties may not, except to the extent that a Party is legally required to make a public statement, make any public statement or issue a press release which could affect another Party, without first submitting a written copy of the proposed public statement or press release to the other Party and obtaining the other Party's prior written approval for such public statement or press release, which consent must not unreasonably be withheld.

#### Guarantee and Warranties

The Bidder warrants that:

- as at Commencement Date, it has the rights, title and interest in and to the Product or Services to deliver such Product or Services in terms of the Contract and that such rights are free from any encumbrances whatsoever;

- the Product is in good working order, free from Defects in material and workmanship, and substantially conforms to the Specifications, for the duration of the Warranty period;

- during the Warranty period and Extended Warranty periods any defective item or part component of the Product be repaired or replaced within 3 (three) days after receiving a written notice from SITA;

- the Products is maintained during its Warranty Period and Extended Warranty periods at no additional expense to SITA;

- the Product possesses all material functions and features required for SITA’s Operational Requirements;

- the Product remains connected or Service is continued during the term of the Contract;

- all third-party warranties that the Bidder receives in connection with the Products including the corresponding software and the benefits of all such warranties are ceded to SITA without reducing or limiting the Bidder’s obligations under the Contract;

- no actions, suits, or proceedings, pending or threatened against it or any of its third-party Bidders or sub-contractors that have a material adverse effect on the Bidder’s ability to fulfil its obligations under the Contract exist;

- SITA is notified immediately if it becomes aware of any action, suit, or proceeding, pending or threatened to have a material adverse effect on the Bidder’s ability to fulfil the obligations under the Contract;

- any Product sold to SITA after the Commencement Date of the Contract remains free from any lien, pledge, encumbrance or security interest;

- SITA’s use of the Product and Manuals supplied in connection with the Contract does not infringe any Intellectual Property Rights of any third party;

- the information disclosed to SITA does not contain any trade secrets of any third party, unless disclosure is permitted by such third party;

- it is financially capable of fulfilling all requirements of the Contract and that the Bidder is a validly organized entity that has the authority to enter into the Contract;

- it is not prohibited by any loan, contract, financing arrangement, trade covenant, or similar restriction from entering into the Contract;

- the prices, charges and fees to SITA as contained in the Contract are at least as favourable as those offered by the Bidder to any of its other customers that are of the same or similar standing and situation as SITA; and any misrepresentation by the Bidder amounts to a breach of Contract

#### Intellectual Property Rights

  - SITA retains all Intellectual Property Rights in and to SITA's Intellectual Property. As of the Effective Date, the Bidder is granted a non-exclusive license, for the continued duration of this Contract, to perform any lawful act including the right to use, copy, maintain, modify, enhance and create derivative works of SITA's Intellectual Property for the sole purpose of providing the Products or Services to SITA pursuant to this Contract; provided that the Bidder must not be permitted to use SITA's Intellectual Property for the benefit of any entities other than SITA without the written consent of SITA, which consent may be withheld in SITA's sole and absolute discretion. Except as otherwise requested or approved by SITA, which approval is in SITA's sole and absolute discretion, the Bidder must cease all use of SITA's Intellectual Property, at of the earliest of:

    - termination or expiration date of this Contract;

    - the date of completion of the Services; and

  - the date of rendering of the last of the Deliverables.

  - If so required by SITA, the Bidder must certify in writing to SITA that it has either returned all SITA Intellectual Property to SITA or destroyed or deleted all other SITA Intellectual Property in its possession or under its control.

  - SITA, at all times, owns all Intellectual Property Rights in and to all Bespoke Intellectual Property.

  - Save for the license granted in terms of this Contract, the Bidder retains all Intellectual Property Rights in and to the Bidder’s pre-existing Intellectual Property that is used or supplied in connection with the Products or Services.

  - Provide SITA with the compliant safety file.

#### General

- The parties in this Agreement agree that the offer price of all the equipment shall be at the wholesale price or below wholesale price as agreed with the OEM. Should, at any time during the existence of the agreement that the offered price which is higher than the wholesale price or as agreed with the OEM, SITA client shall be entitled to such wholesale price with the exclusion of the mark-up which the reseller may have charged”.

NOTE: These conditions will form part of the contract obligations and Bidders are expected to comply in order for SITA to conclude an agreement with the potential Bidders. Failure to comply during finalisation of a contract may result to disqualification.

#### Counter Conditions

- Bidders’ attention is drawn to the fact that amendments to any of the Bid Conditions or setting of counter conditions by bidders may result in the invalidation of such bids.

#### Fronting

- The SITA supports the spirit of Broad Based Black Economic Empowerment and recognizes that real empowerment can only be achieved through individuals and businesses conducting themselves in accordance with the Constitution and in an honest, fair, equitable, transparent and legally compliant manner. Against this background the SITA will not condone any form of fronting.

- The SITA, in ensuring that bidders conduct themselves in an honest manner will, as part of the bid evaluation processes, conduct or initiate the necessary enquiries/investigations to determine the accuracy of the representation made in bid documents. Should any of the fronting indicators as contained in the Guidelines on Complex Structures and Transactions and Fronting, issued by the Department of Trade and Industry, be established during such enquiry/investigation, the onus will be on the bidder / contractor to prove that fronting does not exist. Failure to do so within a period of 14 days from date of notification may invalidate the bid / contract and may also result in the restriction of the bidder/contractor to conduct business with the public sector for a period not exceeding ten (10) years, in addition to any other remedies SITA may have against the bidder/contractor concerned.

#### Business Continuity and Disaster Recovery Plans

- The bidder confirms that they have written business continuity and disaster recovery plans that define the roles, responsibilities and procedures necessary to ensure that the required services under this bid specification is in place and will be maintained continuously in the event of a disruption to the bidder’s operations, regardless of the cause of the disruption.

#### Bidder Due Diligence

- SITA reserves the right to conduct Bidder due diligence prior to final award or at any time during the Contract period and this may include pre-announced / non-announced site visits. During the due diligence process the information submitted by the bidder will be verified and any misrepresentation thereof may disqualify the bid or Contract in whole or parts thereof.

#### Sub-Contracting as a condition of tender

- SITA, in terms of the SITA Preferential Policy (PPP), has an obligation to advance designated groups which includes black SMMEs (i.e. Exempted Micro Enterprises (EME) and Qualifying Small Enterprises (QSE) for the supply of certain ICT goods or services where feasible to subcontract for a contract above R50m, an organ of state must apply sub-contracting to advance designated groups.

# Note  (1): The feasibly of subcontracting as well as the exact percentage subcontracting will be agreed by the parties during the contracting stage.

#### Preference Goal Requirements conditions

- The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

- The Bidder must sustain, or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

- Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report indicating progress against the Bidder’s Preferential commitments within 30 days of the yearly anniversary of the contract.

- Bidders need to keep auditable substantive records / evidence and upon request by SITA/Department must be made available for audit and, or due diligence purposes.

- SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

- SITA reserves the right to verify information / evidence provided by the Bidder.

- SITA/Department reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA/Department for the prior year if the Bidder fails to comply to paragraphs (a), (b) and (c) above.

### Declaration of compliance and acceptance SCC

I (we), the bidder hereby declare that I (we) accept ALL the Special Conditions of Contract as specified in par 4.3. above and shall comply with all stated obligations:

Name of Bidder: _____________________________	Signature: _________________________

Date: ______________

## Costing and Preference Points Evaluation (Stage 4)

    - 4.4.1 Costing and Preference Evaluation

- In terms of the SITA Preferential Procurement Policy (PPP), the following preference point system is applicable for this Bid:

  - the 80/20 system (80 Price, 20 Specific Goals) for requirements with a Rand value of up to R50 000 000 (all applicable taxes included); or

  - the 90/10 system (90 Price and 10 Specific Goals) for requirements with a Rand value above R50 000 000 (all applicable taxes included).

- The Bidder must complete either the 80/20 or 90/10 preference point system based on the offer submitted by the Bidder and submit proof of documentation required in terms of this tender.

- SITA reserve the right to apply either the 80/20, or 90/10 preference point system based on the following conditions:

  - If the lowest acceptable bid price is up to and including R50 000 000 (all applicable taxes included) then the 80/20 preferential point system will apply to all acceptable bids; or

  - If the lowest acceptable bid price is above R50 000 000 (all applicable taxes included) then the 90/10 preferential point system will apply to all acceptable bids;

- Points will be allocated for each of the Preferential Goal Requirements for this tender as indicated in table 6.

- Points for this tender shall be awarded for:

  - Price; and

  - Preference points for specific goals.

Table 6: Points allocation

| Description | Points | Points |
| --- | --- | --- |
| Price | 80 | 90 |
| Preference points for specific goals | 20 | 10 |
| Total points for Price and preference points for specific goals | 100 | 100 |

    - 4.4.2 Costing and Pricing Conditions

- South African Pricing

# The total price must be VAT inclusive and be quoted in South African Rand (ZAR).

- Total Price

  - All quoted prices are the total price for the entire scope of required services and deliverables to be provided by the bidder.

  - All additional costs as well as cost of delivery, labour, S&T, overtime, etc. must be included in this bid.

  - All services, accessories, upgrades and options required by the solution or specified by the client must be included in the quoted price. If not included, Bidders will be required to supply these accessories at no cost to the client.

  - The total bid price is based on estimated quantities; however, payments shall be made based on actual measured quantities supplied, used, or installed on site.

  - Any additional items not included in the original schedule of quantities shall be subject to prior written approval and rate agreement before execution. Payment shall be based on approved rates and measured quantities.

  - SITA reserves the right to negotiate pricing with the successful bidder prior to the award as well as envisaged quantities

- These conditions will form part of the Contract between SITA and the bidder. However, SITA reserves the right to include or waive the condition in the Contract.

- The bidder must complete the declaration of acceptance as per par 4.5 below by marking with an “X” either “ACCEPT ALL”, or “DO NOT ACCEPT ALL”, failing which the declaration will be regarded as “DO NOT ACCEPT ALL” and the bid will be disqualified.

    - 4.4.3 Bid Pricing Schedule

- Bidders must complete the bid pricing schedule in the Excel spreadsheet format provided and include this as part their submission.

Note:

Bidders must complete and submit bid pricing in the provided Excel spreadsheet format, and any pricing schedule submitted in a different format will not be considered.

  - Declaration of Acceptance

|  | ACCEPT ALL | DO NOT ACCEPT ALL |
| --- | --- | --- |
| - The bidder declares to ACCEPT ALL the Costing and Pricing conditions as specified in par 4.4.2 above by indicating with an “X” in the “ACCEPT ALL” column, or - The bidder declares to NOT ACCEPT ALL the Costing and Pricing Conditions as specified in par 4.4.2 above by - - Indicating with an “X” in the “DO NOT ACCEPT ALL” column, and; - Provide reason and proposal for each of the condition not accepted. |  |  |
| Comments by bidder: Provide the condition reference, the reasons for not accepting the condition. |  |  |

  - Preference Requirements

- The bidder must complete in full all the PREFERENCE requirements.

- Allocation of points per requirements: The points allocation of bidders’ responses to the requirements will be determined by the completeness, relevance and accuracy of substantiating evidence.

- Points will be allocated for each PREFERENCE requirement as per the criteria set in table 9A or table 9B  based on the offer submitted by the Bidder.

- The bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response. During evaluation, SITA reserves the right to treat substantiation evidence that cannot be located in the bid response, as “NOT COMPLY”. The evidence needs to be attached to Annex A.

- Preference Goal Requirements

  - The Bidder must complete either the 90/10 or 80/20 preference point system based on the offer submitted by the Bidder and submit proof or documentation required in terms of this tender.

  - The specific Preferential Goal Requirements for this tender is indicated in table 7 or table 8 below.

  - The Bidder must indicate their commitment to claim points for each of the preference points by signing at par 4.5 in the Invitation to Bid document.

  - The Bidder must indicate how they claim points for each of the preference points.

  - Failure on the part of a bidder to submit proof or documentation required in terms of this tender to claim preference points for the Preference Goal Requirements for this tender, will be interpreted to mean that preference points are not claimed.

  - The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

  - The Bidder must sustain, or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

  - Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report indicating progress against the Bidder’s Preferential commitments within 30 days of the yearly anniversary of the contract.

  - Bidders need to keep auditable substantive records / evidence and upon request by SITA must be made available for audit and, or due diligence purposes.

  - SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

  - SITA reserves the right to verify information / evidence provided by the Bidder.

  - SITA reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA for the prior year if the Bidder fails to comply to paragraphs (g), (h) and (i) above.

Table 7: Preference Goal Requirements (Specific Goals for (80/20) system)

| Preference Goal Requirement # | Preferential Goal Requirements (Specific Goals) (80/20) system |  |  |  |
| --- | --- | --- | --- | --- |
|  | Preferential Goal Requirements allocated for this tender | Point allocation for 80/20 system | Substantiating evidence and evidence reference to be completed by bidder. Evaluation per requirement: Each requirement indicated in the table below must be completed and points will be allocated based on the evidence required below for the (80/20) system | Evidence reference |
|  | B-BBEE Requirements |  |  |  |
| 1) | B-BBEE Requirements: Promotion of Transformational Objectives. | 10,0 | Evidence: The Bidder must provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for: - Columns A, B, C and D in table 9A # Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act: - B-BBEE certificate (from a SANAS Accredited Agency/thedtic); # or # Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only; - Column D in table 9A # Copy of South African Identification Document (ID); and/ or - Column E in table 9A # Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act. Note: The CIPC (Companies and Intellectual Property Commission) registration documents will also be used as evidence to confirm compliance to the Preferential procurement requirements as part of the evaluation process. Points allocation: Points will be allocated for bidders that meets the requirements as indicated in table 9A in section 4.6. | <provide unique reference to locate (80/20) system substantiating evidence in the bid response – Annex A, section 5.9> |
|  | Specific Goals: | 10,0 |  |  |
| 2) | The promotion of Local Products in line with the PPP. In line with the promotion of Local Products SITA will allocate Preference Points to Bidders whose products contain Local Content and production for Electrical and Telecom cables. | 10,0 | Evidence: Bidder must complete, sign and submit the Local Content Requirements as indicated in Annex D. Points allocation: 0 points = Zero % Local Content; 10 points = 90 % or greater Local Content. | <provide unique reference to locate (80/20) system substantiating evidence in the bid response – Annex A, section 5.9> |
|  | Total Point Allocation: | 20,0 |  |  |

Table 8: Preference Goal Requirements (Specific Goals for (90/10) system)

| Preference Goal Requirement # | Preferential Goal Requirements (Specific Goals) (90/10) system |  |  |  |
| --- | --- | --- | --- | --- |
|  | Preferential Goal Requirements allocated for this tender | Point allocation for 90/10 system | Substantiating evidence and evidence reference to be completed by bidder. Evaluation per requirement: Each requirement indicated in the table below must be completed and points will be allocated based on the evidence required below for the (90/10) system | Evidence reference for the substantiating evidence |
|  | B-BBEE Requirements |  |  |  |
| 1) | B-BBEE Requirements: Promotion of Transformational Objectives. | 5,0 | Evidence: The Bidder must provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for: - Columns A, B, C and D in table 9B # Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act: - B-BBEE certificate (from a SANAS Accredited Agency/thedtic); # or # Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only; - Column D in table 9B # Copy of South African Identification Document (ID); and/ or - Column E in table 9B # Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act. Note: The CIPC (Companies and Intellectual Property Commission) registration documents will also be used as evidence to confirm compliance to the Preferential procurement requirements as part of the evaluation process. Points allocation: Points will be allocated for bidders that meets the requirements as indicated in table 9B in section 4.6. | <provide unique reference to locate (90/10) system substantiating evidence in the bid response – Annex A, section 5.9> |
|  | Specific Goals: | 5,0 |  |  |
| 2) | The promotion of Local Products in line with the PPP. In line with the promotion of Local Products SITA will allocate Preference Points to Bidders whose products contain Local Content and production for Electrical and Telecom cables. | 5,0 | Evidence: Bidder must complete, sign and submit the Local Content Requirements as indicated in Annex D. Points allocation: 0 points = Zero % Local Content; 10 points = 90 % or greater Local Content. | <provide unique reference to locate (90/10) system substantiating evidence in the bid response – Annex A, section 5.9> |
|  | Total Point Allocation: | 10,0 |  |  |

Table 9A: B-BBEE Points as part of the Preference Goal requirements (Preferential Goal Requirements for (80/20) system)

Note: Bidder to select the section for points they wish to claim (Mark as Y=Yes) in the table below.

|  |  |  |  | Ownership of at least 51% of People who are: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Reference # | Contributor Level as defined in the Broad-Based Black Economic Empowerment Act | Local Entity | EME/QSEs | Woman Owned | Youth Owned | Owned by People living with disabilities | Score | Bidder to select the section for points they wish to claim (Mark as Y= Yes) |
|  | (A) | (B) | (C) | (D) | (E) | (F) | (G) |  |
| 1 | Level 1 | 0 | 2 | 4 | 3 | 1 | 10 |  |
| 2 | Level 1 | 0 | 2 | 4 | 3 | 0 | 9 |  |
| 3 | Level 1 | 0 | 2 | 4 | 0 | 0 | 6 |  |
| 4 | Level 2 and 3 | 0 | 1 | 2 | 1 | 1 | 5 |  |
| 5 | Level 2 and 3 | 0 | 1 | 2 | 1 | 0 | 4 |  |
| 6 | Level 2 and 3 | 0 | 1 | 2 | 0 | 0 | 3 |  |
| 7 | Level 4 and 5 | 0 | 0.,5 | 1 | 0,5 | 0,5 | 2,5 |  |
| 8 | Level 4 and 5 | 0 | 0,5 | 1 | 0.5 | 0 | 2 |  |
| 9 | Level 4 and 5 | 0 | 0,5 | 1 | 0 | 0 | 1.5 |  |
| 10 | Level 6 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 11 | Level 7 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 12 | Level 8 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 13 | Non-Contributor | 0 | 0 | 0 | 0 | 0 | 0 |  |
| Total Maximum Score Allocation: |  |  | 10 |  |  |  |  |  |
| G= A+B+C+D+E+F |  |  |  |  |  |  |  |  |

Table 9B: B-BBEE Points as part of the Preference Goal requirements (Preferential Goal Requirements for (90/10) system)

Note: Bidder to select the section for points they wish to claim (Mark as Y=Yes) in the table below.

|  |  |  |  | Ownership |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Reference # | Contributor Level as defined in the Broad-Based Black Economic Empowerment Act | EME/QSEs | Black Owned | Black Woman Owned | Youth Owned | Owned by People living with disabilities | Score | Bidder to select the section for points they wish to claim |
|  |  |  |  | (BO) | (BWO) |  |  |  | (Mark as Y= Yes) |
|  |  |  |  | (51% or more) | (More than 30%) |  |  |  |  |
|  |  |  | (A) | (B) | (C) | (D) | (E) | (F) |  |
|  | 1 | Level 1 | 0,75 | 1,5 | 1,25 | 1 | 0,5 | 5 |  |
|  | 2 | Level 1 | 0,75 | 1,5 | 1,25 | 1 | 0 | 4,5 |  |
|  | 3 | Level 1 | 0,75 | 1,5 | 1,25 | 0 | 0 | 3,5 |  |
|  | 4 | Level 1 | 0,75 | 1,5 | 0 | 0 | 0 | 2,25 |  |
|  | 5 | Level 2 and 3 | 0,5 | 1 | 0,5 | 0,25 | 0,25 | 2.5 |  |
|  | 6 | Level 2 and 3 | 0,5 | 1 | 0,5 | 0,25 | 0 | 2,25 |  |
|  | 7 | Level 2 and 3 | 0,5 | 1 | 0,5 | 0 | 0 | 2 |  |
|  | 8 | Level 2 and 3 | 0,5 | 1 | 0 | 0 | 0 | 1,5 |  |
|  | 9 | Level 4 and 5 | 0,25 | 0,5 | 0,25 | 0,125 | 0,125 | 1,25 |  |
|  | 10 | Level 4 and 5 | 0,25 | 0,5 | 0,25 | 0,125 | 0 | 1.125 |  |
|  | 11 | Level 4 and 5 | 0,25 | 0,5 | 0,25 | 0 | 0 | 1 |  |
|  | 12 | Level 4 and 5 | 0,25 | 0,5 | 0 | 0 | 0 | 0.75 |  |
|  | 13 | Level 6 | 0 |  | 0 | 0 | 0 | 0 |  |
|  | 14 | Level 7 | 0 |  | 0 | 0 | 0 | 0 |  |
|  | 15 | Level 8 | 0 |  | 0 | 0 | 0 | 0 |  |
|  | 16 | Non-Contributor | 0 |  | 0 | 0 | 0 | 0 |  |
|  | Total Maximum Score Allocation: |  | 5 |  |  |  |  |  |  |

|  | F= A+B+C+D+E |  |  |
| --- | --- | --- | --- |

Bidder Substantiating Evidence

# Technical Mandatory Requirement Evidence

## Bidder Certification / Affiliation Requirements

Attach a copy of valid letter from the Department of Labour as evidence that the bidder is registered as an Electrical Contractor here.

NOTE (1):

SITA reserves the right to verify information provided.

## Bidder Experience and Capability Requirements

Complete table below, noting that:

The Bidder must complete table 10 by providing reference details from two (2) customers/projects to whom Low Voltage Electrical Installations involving Distribution Boards or Busbar Trunking Systems of a minimum size of 1600A at a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Manufacturing Facility) to at least two (2) customers/projects in the past five (5) years from the publication date of this bid.

The Bidder must provide all of the following information when completing table 10:

- Company name

  - Company name; and

  - Reference Person Name, Tel and/or email; and

  - Project Scope of Work; and

  - Project Start and End-date.

- Project end-date must be current or not older than five (5) years from the publication date of this bid.

- Scope of work must be related.

Table 10: References

| No | Company Name | Contact person, telephone and e-mail address | Project Scope of Work | Project start and end date |
| --- | --- | --- | --- | --- |
| 1 | <Company name> | <Person Name> <Tel> <email> | < Provide scope detail that was executed including the equipment sizes> | Start Date: End Date: |
| 2 | <Company name> | <Person Name> <Tel> <email> | < Provide scope detail that was executed including the equipment sizes> | Start Date: End Date: |

NOTE (1):

The Bidder must provide all of the following information when completing table 10.

NOTE (2):

Failure to comply fully to the requirements as indicated above will result in disqualification.

NOTE (3):

SITA reserves the right to verify information provided.

## CIDB Registration Requirements

The Bidder must complete and sign ANNEX B as evidence that the Bidder is registered with the CIDB with a minimum rating or higher of 8EB or 8EP and attach it here.

## Key Personnel Qualification: Project Manager

Attach to ANNEX A copy of a valid Registration Certificate indicating that the Project Manager has been registered as professional for a minimum of five (5) years post professional registration.

The professional registration be either one (1) of the following:

- ECSA, Professional Engineer (Pr Eng), or

- ECSA, Professional Certificated Engineer, or

- ECSA, Professional Engineering Technologist, or

- ECSA, Professional Engineering Technician, or

- PMI, Project Management Professional (PMP), or

- SACPCMP, Professional Construction Project Managers.

NOTE (1):

SITA reserves the right to verify the information provided.

NOTE (2):

SITA reserves the right to verify the consent from the registered person.

NOTE (3):

The Bidder must also provide registered person contact details by completing table 11.

- Attach a copy of the Professional registration certificate here and contact details of the professional registered person:

Table 11: Registered Person Contact Details

| No | Contact person, telephone and/or e-mail address |
| --- | --- |
| 1 | <Person Name> <Tel> or <email> |

## Electrical Distribution Boards Data Sheet

Attach the following completed and signed Data Sheets here:

  - SITA Centurion LV BOARDS Data Sheets - LV BOARD (A, B, C & D)

  - SITA Centurion DB-G5 Data Sheets

Note (1):

Total two (2) data sheets are to be submitted.

Note (2):

SITA reserves the right to verify the information provided.

Note (3):

The data sheet information will be applicable with all other distribution boards.

## Electrical Distribution Boards General Arrangement Drawings

Attach to Annex A copies of General Arrangement drawings of the following Single Line Diagrams: and signed Data Sheets:

  - 1001547-DRG-EL-100-LV-A

  - 1001547-DRG-EL-700-DB-G5

  - 1001547-0000-DRG-EL-900-T0-MECH DB-A

Note (1):

Total three (3) GA drawings that are to be submitted.

Note (2):

SITA reserves the right to verify the information provided.

## Third Party Risk Management Assessment

The Bidder must comply with the Third-Party Risk Management Assessment requirement by completing All the questions in ANNEX E and attach it here.

NOTE (1):

SITA reserves the right to verify information provided.

NOTE (2):

Failing to complete all the questions or not Accepting the Declaration of Acceptance above will result in disqualification.

## Special Conditions of Contract Acceptance

The Bidder must accept ALL the Special Conditions of Contract (SCC) as stated in section 4.3, by signing in the declaration of compliance and acceptance of SCC in section 4.3.2.

Note (1):

Failure to accept ALL the Special Conditions of Contract will result in disqualification.

## Preference Points Preferential Goals Evidence

The Bidder must provide the following Preference Goal Requirements evidence and attach it here:

          - B-BBEE Requirements:

# Promotion of Transformational Objectives

          - Bidder to select the section for points they wish to claim (Mark as Y=Yes) in either tables 9A or 9B in section 4.6, dependant on which preference system the Bidder selects in line with section 4.6; and

          - Provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for as set out in table 7 or 8 in section 4.6 and attach it here:

    - Columns A, B, C and D in tables 9A or 9B:

Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act:

- B-BBEE certificate (from a SANAS Accredited Agency);

or

- Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only;

and/ or

    - Column D in tables 9A or 9B:

Copy of South African Identification Document (ID):

and/ or

    - Column E in tables 9A or 9B:

Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act.

Note(3):

The CIPC (Companies and Intellectual Property Commission) registration documents will also be used as evidence to confirm compliance to the Preferential procurement requirements as part of the evaluation process.

          - The promotion of Local Products in line with the PPP.

In line with the promotion of Local Products SITA will allocate Preference Points to Bidders whose products contain Local Content and production for Electrical and Telecom cables.

          - Bidder to select the section for points they wish to claim (Mark as Y=Yes) in either tables 9A or 9B in section 4.6, dependant on which preference system the Bidder selects in line with section 4.6; and

          - Provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for as set out in tables 7 or 8  in section 4.6 and attach it here:

# Evidence:
Bidder must complete, sign and submit the Local Content Requirements as indicated in Annex D.

# (3)	Indicate their commitment to claim points for each of the preference points by signing at par 4.5 in the Invitation to Bid document.

NOTE (1):

Failure on the part of a bidder to comply to paragraphs (1) and (2) and (3) above, will be interpreted to mean that preference points are not claimed.

CIDB Registration Requirement

The Bidder needs to complete and sign ANNEX B to confirm that the Bidder, is registered with the Construction Industry Development Board (CIDB) with a minimum rating or higher of 8EB, or 8EP.

      - The Bidder needs to indicate the CIDB rating by ticking next to the relevant CIDB rating in the table below:

| Service and Support (Milestones) | CIDB Rating | Bidder to Indicate the Bidder’s rating here |
| --- | --- | --- |
| CIDB Rating | 8EB |  |
|  | 8EP |  |
|  | Higher |  |

      - The Bidder needs to provide the Bidder’s CRS number in the space in the table below:

| Requirement | Bidder’s CRS Number |
| --- | --- |
| Bidder CRS number relating to the minimum rating of 8EB |  |
| Bidder CRS number relating to the minimum rating of 8EP |  |
| Bidder’s CRS number relating to the higher rating of EB or EP |  |

      - The Bidder confirms and will ensure compliance to the CIDB Basic Guide General Conditions of Contract for Construction Works (GCC 2004) as referred to in Annex F for the Bid Specification Scope of work for the duration of the contract.

NOTE 1:

SITA reserves the right to verify the information.

I, the Supplier (Full names) …………………………………………………. Representing (company name) …………………………………………………………….. hereby confirm that the Bidder is registered with Construction Industry Development Board (CIDB) and understand that it will form part of the contract and is legally binding.

Thus, done and signed at ……………………………………. On this………day of……………….20….

__________________

Signature

Designation:

Technical Information

# Technical Information

  - Project Specifications

- eSDHS-01355_SITA Electrical Technical Specification

  - Project Data Sheets

  - 01 - SITA Centurion LV BOARDS Data Sheets - LV BOARD (A, B, C & D)

  - 02 - SITA Centurion DB-G5 Data Sheets

  - Project General Arrangement Drawings

- 1001547-0000-DRG-EL-0002: INSTALLATION METHODOLOGY

- 1001547-0000-DRG-EL-110: NEW CONFIGURATION RETICULATION SHEET 1

- 1001547-0000-DRG-EL-111: NEW CONFIGURATION RETICULATION SHEET 2

  - Project Single Line Diagrams

- 1001547-0000-DRG-EL-100: LV-A

- 1001547-0000-DRG-EL-200: LV-B

- 1001547-0000-DRG-EL-300: LV-C

- 1001547-0000-DRG-EL-400: LV-D

- 1001547-0000-DRG-EL-700: DB-G5

- 1001547-0000-DRG-EL-800: SYNC PANEL

- 1001547-0000-DRG-EL-900: MECHANICAL DB A

- 1001547-0000-DRG-EL-1000: MECHANICAL DB B

- 1001547-0000-DRG-EL-1100: MECHANICAL DB C

- 1001547-0000-DRG-EL-1200: MECHANICAL DB D

# Local Content Requirements

# Local Content Requirements:

## The bidder must confirm compliance to the Local Content requirements.

## The following documents are attached to guide guidance in completing the Local Content requirements:

- Document 01:	Guidance Document for the Calculation of Local Content.

- Document 02:	South African National Standard:  Local goods, services and work –

Measurement and verification of local content.

## The Bidder must complete, sign and submit the following documents at bid closure:

- Document 03:	SBD 6.2 Declaration Certificate for Local Production and content for

Designated Sectors.

- Document 04:	Annexure C: Local Content Declaration.

The following Annexures should not be submitted by the bidder, however be kept by the by the bidder and be provide the documents upon request.

- Document 05: 	Annexure D: Imported Content Declaration.

- Document 06: 	Annexure E: Local Content Declaration.

NOTE: Failure to complete, sign and submit the documents as requested in section 7.3 above at bid closing will result in disqualification.

Third-Party Risk Management (TPRM) Assessment

# Instructions

- In terms of the approved SITA Third-Party Risk Management Framework, all Bidders responding to this bid must complete the following section by answering ALL the questions.

- By completing the Third-Party Risk Management Assessment, the Bidder agrees to provide all reasonable supporting documentation when requested to do so, as well as during contract finalisation as this is a pre-award condition of this bid.

- Any risk identified during the assessment process will have to be mitigated and/or remediated before or during the contract finalisation phase. A detailed mitigation plan, that is acceptable to SITA, may also be required.

- Supplier due diligence, as contained in the Special Conditions of Contract, is also applicable to this Third-Party Risk Management process.

- The following 6 (six) risk elements will be assessed:

  - Company risk: 10 questions;

  - Financial risk: 6 questions;

  - Operational risk: 8 questions;

  - Governance and compliance risk: 6 questions;

  - Information security and privacy risk: 7 questions;

  - Reputational risk: 6 questions.

## 8.1    Evaluation Criteria

### Company risk

  - Questions 2, 3, 6, 8, 9, 10:

| Evaluation criteria | Score |
| --- | --- |
| Yes | 0 |
| Partially meet requirements | 0.5 |
| No | 1 |

  - Questions 1, 4, 5:

| Evaluation criteria | Score |
| --- | --- |
| Yes | 1 |
| Partially meet requirements | 0.5 |
| No | 0 |

  - Question 7:

| Evaluation criteria | Score |
| --- | --- |
| Yes, actively operating for more than 5 years | 1 |
| 2-5 Years actively operating | 0.5 |
| No, actively operating for less than 2 years | 0 |

### All questions for all other risk elements:

| Evaluation criteria | Score |
| --- | --- |
| Yes | 1 |
| Partially meet requirements | 0.5 |
| No | 0 |

## Third Party Risk Assessment

  - The assessment of bidders’ responses to the questions will be determined by the completeness (i.e. all questions answered), undertaking signed (where required) and accuracy of substantiating evidence, when requested. Please note that SITA reserves the right to verify the information provided.

| Question to assess each risk element | Bidders response: Mark relevant box with an “X” |  |  |
| --- | --- | --- | --- |
| Company Risk |  |  |  |
| - Have you disclosed all interests and relationships as required in SBD 4, including whether any of your directors, members, trustees, or shareholders are employed by the state, have relationships with SITA employees, or have interests in other entities (whether they are also bidding for this contract, or not)? | Yes | Partially | No |
| - Are you currently involved in litigation against SITA – or do you foresee litigation being instituted within the next 6 months? | Yes | Partially | No |
| - Are there any law suits or ongoing litigation that could affect this transaction in any way or the bidder as an ongoing concern? | Yes | Partially | No |
| - Is customer service delivery or contract performance actively monitored by you? | Yes | Partially | No |
| - Do you have formal strategic planning processes in place? | Yes | Partially | No |
| - Are any of your directors or shareholders Prominent Influential People (PIP) or Politically Exposed Persons (PEP)? | Yes | Partially | No |
| - Has your company been actively operating as a going concern for more than 5 years? | Yes | 2-5 Years | Less than 2 years |
| - Is the company busy with a re-organisational/restructuring process that may impact this transaction? | Yes | Partially | No |
| - Are any of your suppliers located in a region where geopolitical risk exposure is high? | Yes | Partially | No |
| - Has any current director of the bidder ever served as a director of a company during a period where a Government contract was cancelled? | Yes | Partially | No |
| Financial Risk |  |  |  |
| - Did you have positive revenue growth in the past three years? | Yes | Partially | No |
| - Is the proposed bid price going to be less than 40% of your total annual revenue for the previous financial year? | Yes | Partially | No |
| - Is the financial health of your company in good standing? | Yes | Partially | No |
| - Were your Annual Financial Statement (AFS) unqualified in the last financial year? | Yes | Partially | No |
| - Do you have sufficient cash in the bank (2 or more months’ worth of operating cost) to operate under restricted conditions for at least 2 months? | Yes | Partially | No |
| - Do you have a clean credit record: No current or pending judgement, adverse listing, business rescue or principal sequestration listing? | Yes | Partially | No |
| Operational Risk |  |  |  |
| - Do you have operational redundancy (resilience) in terms of technology and energy resources to ensure high availability of services? | Yes | Partially | No |
| - Are your dependencies for logistics either fully under your own control or managed through supplier performance management contracts? (Choose “Yes” if fully under your own control and “No” for supplier contracts) | Yes | Partially | No |
| - Do you have operational procedure standards in place across the organisation, such as change control, release management, access control, incident management, back-up regimes and restore tests, etc? | Yes | Partially | No |
| - Do you have human resources management in place, including succession planning and mitigation against key reliance on single individuals? | Yes | Partially | No |
| - Do you have sound supply chain processes in place? | Yes | Partially | No |
| - Do you have sound third party risk management processes in place (fourth party for SITA)? | Yes | Partially | No |
| - Do you have a fully-fledged research and development (R&D) department to ensure continuous improvement? | Yes | Partially | No |
| - Do you rely on locally manufactured components or have actively managed the risk relating to lead times or delivery delays? (Choose “Yes” is you rely on locally manufactured components or can actively manage lead times and prevent delivery delays where manufacturing is not local i.e. not in South Africa) | Yes | Partially | No |
| Governance and Compliance Risk |  |  |  |
| - Do you comply with all legislation, including labour, health and safety regulations? | Yes | Partially | No |
| - Do you have the appropriate governance frameworks (Cobit, ITIL, King) in place with due monitoring against set standards? | Yes | Partially | No |
| - Do you have an internal audit function compliant with IIA standards (insourced, outsourced or co-sourced) in place? | Yes | Partially | No |
| - Do you follow formally documented enterprise risk management processes? | Yes | Partially | No |
| - Are all statutory requirements of the entity up to date? Specifically, the following: CIPC Returns, Tax returns, UIF and COIDA. | Yes | Partially | No |
| - Do you have comprehensive insurance in place, including cover for assets, business disruption and liability? | Yes | Partially | No |
| Information Security and Privacy Risk |  |  |  |
| - Are your physical security perimeters appropriately safeguarded? | Yes | Partially | No |
| - Do you have video surveillance of areas that will contain SITA information/products? | Yes | Partially | No |
| - Do you conduct security and suitability verification of all employees prior to employment? | Yes | Partially | No |
| - Do you have identification verification controls in place in all your buildings? | Yes | Partially | No |
| - Are your access control protocols verified to be effective by Internal and/or External Auditors? | Yes | Partially | No |
| - Do you have Security Information and Events Management (SIEM) processes in place? | Yes | Partially | No |
| - Do you have sufficient information security and cyber arrangements in place for employees working from home? | Yes | Partially | No |
| Reputational Risk |  |  |  |
| - Do you have anti-bribery and corruption, anti-money laundering and fraud prevention practices in place? | Yes | Partially | No |
| - Please confirm that neither the company, nor any of its directors has been named in any corruption scandal (choose “Yes” to confirm not being named in a corruption scandal) | Yes | Partially | No |
| - Do you have a social responsibility programme in place? | Yes | Partially | No |
| - Do you have an environmental protection policy, including potential harmful emission or hazardous waste management? | Yes | Partially | No |
| - Do you actively manage your organisation’s energy consumption? | Yes | Partially | No |
| - Is your employment equity plan up to date and actively managed? | Yes | Partially | No |

## Third Party Risk Management Declaration

  - The bidder hereby makes the following declaration and confirm the following information (mark with a “X” in the corresponding column):

| Statement of Declaration | Accept and Confirm | Do not accept and Confirm |
| --- | --- | --- |
| - All questions in this assessment were answered accurately. |  |  |
| - SITA can request additional supporting documentation, within reason, to confirm the accuracy and completeness of the information provided in this self-assessment. |  |  |

### Declaration of Acceptance

|  | Accept all | Do not accept all |
| --- | --- | --- |
| - The bidder declares that all information provided in this assessment is accurate. - The bidder understands that any false information may constitute misrepresentation. - SITA reserves the right to verify the information provided. - By completing the Third-Party Risk Management Assessment the Bidder agrees to provide all reasonable supporting documentation when requested to do so, as well as during contract finalisation as this is a pre-award condition of this bid. - The bidders understand and agrees that this section will form part of the contract and is legally binding. |  |  |
| Any additional comments by bidder pertaining to the third-party risk assessment: |  |  |

NOTE: Failing to complete all the questions or not Accepting the Declaration of Acceptance will lead to disqualification.

CIDB Basic Guide General Conditions of Contract for Construction Works (GCC 2004)

Refer to Attached document.