UGU DISTRICT MUNICIPALITY

DUNJAZANE WATER PIPELINE & PUMPSTATION EMERGENCY SCHEME

CONTRACT NO: UGU-07-1640-2023

CONSTRUCTION OF 110mm DIAMETER UPVC PUMPING MAIN OF 2 km, PUMP STATION, RETICULATION, STANDPIPES AND 500kl RESERVOIR

PART C3: 	SCOPE OF WORK

INDEX

PART C3 	SCOPE OF WORKS							SW 2

C3.1	STANDARDISED SPECIFICATIONS				SW 3

C3.2	PROJECT SPECIFICATIONS					SW 4

PROJECT SPECIFICATION: PORTION 1						SW 6

SABS 1200 PS:  GENERAL								SW 6

PS-1: PROJECT DESCRIPTION 							SW 6

PS-2: EXTENT OF THE WORKS 							SW 6

PS-3: DECSRIPTION OF THE SITE AND ACCESS					SW 7

PS-4: NATURE OF GROUND AND SUBSOIL CONDITIONS 				SW 7

PS-5: ENGINEERING AND DESIGN 							SW 7

PS-6: CONSTRUCTION AND MANAGEMENT REQUIREMENTS 			SW 8

PS-7: CONSTRUCTION PROGRAMME							SW 10

PS-8: SITE FACILITIES AVAILABLE 							SW 11

PS-9: SITE FACILITIES REQUIRED 							SW 12

PS-10: EXISTING SERVICES 								SW 13

PS-11: REQUIREMENTS FOR ACCOMODATION OF TRAFFIC				SW 16

PS-12: OCCUPATIONAL HEALTH AND SAFETY 					SW 17

PS-13: ADVERSE WEATHER CONDITIONS						SW 18

PS-14: SITE MEETINGS AND REPORTING						SW 19

PS-15: PREFERENTIAL PROCUREMENT						SW 19

PROJECT SPECIFICATION: PORTION 2						SW 20

SABS 1200 PSA:  GENERAL								SW 21

SABS 1200 PSC:  SITE CLEARANCE							SW 29

SABS 1200 PSD:  EARTHWORKS (PIPE TRENCHES)					SW 30

SABS 1200 PSL:  MEDIUM PRESSURE PIPELINE					SW 34

SABS 1200 PSLB:  BEDDING (PIPES)							SW 38

SABS 1200 PC:  VALVE METER AND CHAMBER					SW 41

SABS 1200 PSG:  CONCRETE (SMALL WORKS)					SW 44

SABS 1200 PA:  PREFABRICATED RESERVOIR					SW 55

SABS 1200 LE:  DISINFECTION OF RESERVOIRS					SW 57

SABS 1200 PSD:  EARTHWORKS							SW 58

PARTICULAR SPECIFICATION							SW 66

PARTICULAR SPECIFICATION PA:  BRICKWORK AND PLASTER		         SW 63

PARTICULAR SPECIFICATION PD:  DISINFECTION OF PIPELINES		         SW 67

PARTICULAR SPECIFICATION PSP:  STEEL PIPELINES			         SW 74

PARTICULAR SPECIFICATION PE:  THE CLIENT’S PRE-CONSTRUCTION AND
HEALTH PLAN									         SW 81

PARTICULAR SPECIFICATION PF: VALVES					       SW 100

PARTICULAR SPECIFICATION PES: ENVIRONMENTAL SPECIFICATION 	       SW 103

PART C3: 	SCOPE OF WORKS

C3.1	STANDARDISED SPECIFICATIONS

The standard specifications on which this contract is based are Standards South Africa's Standardized Specifications for Civil Engineering Construction SABS 1200.

Although not bound in nor issued with this Document, the following Sections of the Standardized Specifications of SABS 1200 shall form part of this Contract:

| AA | 1986 | : | GENERAL |
| --- | --- | --- | --- |
| AB | 1986 | : | ENGINEER’S OFFICE |
| C | 1980 | : | SITE CLEARANCE (As amended 1982) |
| DA | 1988 | : | EARTHWORKS (Small Works) |
| DB | 1989 | : | EARTHWORKS (Pipe trenches) |
| DK | 1984 | : | GABIONS AND PITCHING |
| DM | 1981 |  | EARTHWORKS (Roads and Subgrade) |
| GA | 1982 | : | CONCRETE (Small Works) |
| HA | 1990 | : | STRUCTURAL STEELWORKS |
| HC | 1988 | : | CORROSION PROTECTION FOR STRUCTURAL STEELWORKS |
| LD | 1982 |  | SEWERS |
| LE | 1982 | : | STORMWATER DRAINAGE |
| M | 1996 | : | ROADS (General) |

The following SANS specifications are also referred to in this document and the Contractor is advised to obtain them from Standards South Africa (a division of SABS) in Pretoria.

SANS 1921 (2004): 	Construction and Management Requirements for Works Contracts

Part 1: 		General Engineering and Construction Works; and

Part 2:	Accommodation of Traffic on Public Roads Occupied by the Contractor.

C3.2	PROJECT SPECIFICATIONS

The project specification is covered in the following sections:

| ITEM |  | DESCRIPTION |  |
| --- | --- | --- | --- |
|  |  | STATUS |  |
|  |  | PROJECT SPECIFICATION PORTION 1: GENERAL |  |
| PS-1 |  | Project Description |  |
| PS-2 |  | Extent of the Works |  |
| PS-3 |  | Description of the Site and Access |  |
| PS-4 |  | Nature of Ground and Subsoil Conditions |  |
| PS-5 |  | Engineering and Design |  |
| PS-6 |  | Construction and Management Requirements |  |
| PS-7 |  | Construction Programme |  |
| PS-8 |  | Site Facilities Available |  |
| PS-9 |  | Site Facilities Required |  |
| PS-10 |  | Existing Services |  |
| PS-11 |  | Requirements for Accommodation of Traffic |  |
| PS-12 |  | Occupational Health and Safety |  |
| PS-13 |  | Adverse Weather Conditions |  |
| PS-14 |  | Site Meetings & Reporting |  |
| PS-15 |  | Preferential Procurement |  |
|  |  | PROJECT SPECIFICATION PORTION 2 |  |
| PSA |  | General |  |
| PSC |  | Site Clearance |  |
| PSD |  | Earthworks (Pipe Trenches) |  |
| PSL |  | Medium Pressure Pipeline |  |
| PSLB |  | Bedding (Pipes) |  |
| PC |  | Valve Meter and Chamber |  |
| PSG |  | Concrete (Small Works) |  |
| PA |  | Prefabricated Reservoir |  |
| LE |  | Disinfection of Reservoirs |  |
| PSD |  | Earthworks |  |
|  |  | PARTICULAR SPECIFICATIONS |  |
| PA |  | Brickwork and Plaster |  |
| PD |  | Disinfection of Pipelines |  |
| PSP |  | Steel Pipes |  |
| PE |  | The Client’s Pre-Construction and Health Plan |  |
| PF |  | Valves |  |
| PES |  | Environmental Specification |  |

STATUS

The Project Specification, consisting of two parts, forms an integral part of the contract and supplements the Standard Specifications.

Part A contains a general description of the works, the site and the requirements to be met.

Part B contains variations, amendments and additions to the Standardized Specifications and, if applicable, the Particular Specifications.

In the event of any discrepancy between a part or parts of the Standardized or Particular Specifications and the Project Specification, the Project Specification shall take precedence. In the event of a discrepancy between the Specifications, (including the Project Specifications) and the drawings and / or the Bill of Quantities, the discrepancy shall be resolved by the Engineer before the execution of the work under the relevant item.

# project SPECIFICATION:  portion 1

# sabs 1200 PS:  GENERAL

PS-1	PROJECT DESCRIPTION

PS-1.1	Employer’s Objective

The Ugu District Municipality (UDM) recognised the need to implement infrastructure refurbishment and replacement programme in an effort to improve in operational efficiency as an answer to service delivery and revenue improvement as part of its overall Water Conservation/Water Demand Management strategy as well as its contribution towards the objectives of the National Water Conservation/Water Demand Management (WC/WDM) initiatives currently underway throughout the country in support of the protection of a scarce water supply resource.

The Dunjazana new 2km pipeline and pumpstation will seek to address the current intermitted water supply on this area, which for many years result in N2 in Bhobhoyi ABC being closed by communities.

PS-1.2	Overview of the Works

Under this Contract UGU-07-1640-2023, the Ugu District Municipality is inviting tenders for Construction Of 110mm Diameter UPVC Pumping Main Of 2 km, Pump Station, Reticulation, Standpipes And 500kl Reservoir.to Optimise the operations of the Dunjazane Water Pipeline & Pumpstation Emergency Scheme. This will cement the current high risk of community shutting of the N2 road in Bhobhoyi ABC area as happened many times in the past. This preventative plan automatically warranty or provide security in as far as the economy is concern up to national level as when N2 is shut millions are lost nationally and locally.

PS-2	EXTENT OF THE WORKS

Under this contract, the successful contractor will be required to construct 110mm Diameter UPVC Pumping Main Of 2 Km, Pump Station, Reticulation, Standpipes And 500kl Reservoir to optimise the operations of the Dunjazane Water Pipeline & Pumpstation Emergency Scheme.

The work will, inter alia, include the following:

- Civil Works

Pipeline trench excavation works, bedding, laying, backfilling and pressure testing for the following:

- Gravity main from Esperance reservoir

- Rising main from proposed pump station to proposed 500kl reservoir

- Reticulation pipelines at Dunjazane

- Provision of metered individual house connections culminating at standpipes

- Construction of air, inline valve and hydrant chambers

- Construction of meter and valve chambers

- Bulk earthworks at the proposed Pump Station and 500kl Reservoir

- Prefabricated clear water storage reservoir with a capacity of 500kl

- Fencing of pumpstation and reservoir sites

- Cleaning, clearing and rehabilitation of areas affected by construction activities.

- Compliance with the environmental management specifications in executing the works

- Construction of reinforced concrete structures

PS-3	DESCRIPTION OF THE SITE AND ACCESS

PS-3.1 	Access

The Project Plan being Drawing N⁰ MC052-4101 is included with the tender documentation and shows the general access to the sites.

A locality map of the Dunjazane Water Treatment Works site is provided. The coordinates for the Dunjazane WPPES are as follows:

| Latitude | Longitude |
| --- | --- |
| 30° 43' 39.69" S | 30° 24 '18.58" E |

The Ugu DM will arrange for the right to access the site.

PS-4 	NATURE OF GROUND AND SUBSOIL INVESTIGATIONS

Subsoil geotechnical investigations have not been undertaken on the site.

No responsibility is accepted for any conclusions drawn by Tenderers from the results and information supplied (if any) and Tenderers must satisfy themselves as to the nature of materials to be excavated under this contract.

PS-5 	ENGINEERING AND DESIGN

PS-5.1 	Design Services and Activity Matrix

The following matrix of responsibilities for design of permanent and temporary works will apply:

| Activity Work designed by, per design stage | Responsible Party |
| --- | --- |
| Concept, feasibility and overall process | Employer |
| Basic engineering and detail layouts to tender stage | Employer |
| Final design approved for construction stage | Employer |
| Temporary works | Contractor |
| Permanent Works | Employer |
| Preparation of as built drawings | Employer |

PS-5.2 	Employer’s Design

The Employer’s design will be for all permanent works and will be detailed in drawings, site instructions the technical specifications to be issued with the tender documents and issued during construction.

PS-5.3 	Design Brief

The contractor will be responsible for design of the following (which are all subject to approval by the Engineer):

Site layouts for the contractor’s camp and office accommodation

Site layouts for the Engineer Representative’s temporary office accommodation

Construction Methodology

Formwork

Scaffolding and all staging work

All other temporary works

Concrete Mix designs

The costs of the designs will be deemed to have been included in the scheduled items in the Schedule of Quantities. No other additional payments will be certified to cover these activities.

PS-5.4	Drawings

The following drawings will be required to be prepared by the contractor as a minimum:

Site layouts for the contractor’s camp and office accommodation

Site layouts for the Engineer Representative’s temporary office accommodation

Scaffolding and all staging work

The costs of the designs will be deemed to have been included in the scheduled items in the Schedule of Quantities. No other additional payments will be certified to cover these activities.

The tender drawings are applicable to the contractor are detailed in Part C5 of these documents. These drawings have been used for setting up the Bills of Quantities.

PS-5.5	Design Procedures

The contractor will be required to furnish the following designs for approval by the Engineer at the indicated times:

Site layouts of the Contractor’s camp and office accommodation – within 14 days from commencement date of the contract and in any case prior to the erection of the contractor’s camp and offices

Layouts for the Engineer’s representative office – within 14 days from commencement date of the contract and in any case prior to the erection of the Engineer’s Representative’s temporary office premises.

Formwork design – within 14 days of commencement of work and in any case prior to the construction of permanent reinforced concrete works.

Scaffolding and all staging work – within 14 days of commencement of work and in any case prior to the construction of permanent reinforced concrete works.

Concrete Mix Designs for the all classes of concrete as measured in the Schedule of Quantities prior to the placement of any concrete work

The costs of the designs will be deemed to have been included in the scheduled items in the Schedule of Quantities. No other additional payments will be certified to cover these activities.

PS-6	CONSTRUCTION AND MANAGEMENT REQUIREMENTS

PS-6.1	General

The Contractor is referred to SANS 1921: 2004: Construction and Management Requirements for Works Contracts, Part 1: General Engineering and Construction Works, and Part 2: Accommodation of Traffic on Public Roads. These specifications shall be applicable to the contract under consideration and the Contractor shall comply with all requirements relevant to the project.

Certain aspects however require further attention as described hereafter.

PS-6.2	Quality Assurance (QA)  (Read with SANS 1921 – 1: 2004 clause 4.4)

The Contractor will be solely responsible for the production of work that complies with the Specifications to the satisfaction of the Engineer.  To this end it will be the full responsibility of the Contractor to institute an appropriate Quality Assurance (QA) system on site.  The Engineer will audit the Contractor's quality assurance (QA) system on a regular basis to verify that adequate independent checks and tests are being carried out and to ensure that the Contractor's own control is sufficient to identify any possible quality problems which could cause a delay or failure.

The Contractor shall ensure that efficient supervisory staff, the required transport, instruments, equipment and tools are available to control the quality of his own workmanship in accordance with his QA-system. His attention is drawn to the fact that it is not the duty of the Engineer or the Engineer’s representative to act as foreman or surveyor.

PS-6.3	Management and disposal of water 	(Read with SANS 1921-1: 2004 clause 4.6)

The Contractor shall pay special attention to the management and disposal of water and stormwater on the site. It is essential that all completed works or parts thereof are kept dry and properly drained. Claims for delay and for repair of damage caused to the works as a result of the Contractor’s failure to properly manage rain and surface water, will not be considered.

PS-6.4	Disposal of spoil or surplus material	(Read with SANS 192-1: 2004 clause 4.10)

The Contractor shall dispose all surplus and unsuitable material in legal spoil areas of his own choice. He shall be responsible for all arrangements necessary to obtain such spoil sites.

PS-6.5	Testing 	(Read with SANS 1921 – 1: 2004 clause 4.11)

PS-6.5.1	Process control

The Contractor shall arrange for all tests required for process control to be done by a laboratory acceptable to and approved by the Engineer.

The Contractor may establish his own laboratory on site or he may employ the services of an independent commercial laboratory. Whatever method is used, the Contractor must submit the results of tests carried out on materials and workmanship when submitting work for acceptance by the Engineer. The costs for these tests shall be deemed to be included in the relevant rates and no additional payment will be made for testing as required.

PS-6.5.2	Acceptance control

The process control test results submitted by the Contractor for approval of materials and workmanship may be used by the Engineer for acceptance control. However, before accepting any work, the Engineer may have further control tests carried out by a laboratory of his choice. The cost of such additional tests will be covered by a provisional sum provided in the schedule of quantities, but tests that failed to confirm compliance with the specifications, will be for the account of the Contractor.

PS-6.6	Survey beacons	(Read with SANS 1921 - 1 : 2004 clause 4.15)

The Contractor shall take special precautions to protect all permanent survey beacons or pegs such as bench-marks, stand boundary pegs and trigonometrical beacons, regardless whether such beacons or pegs were placed before or during the execution of the Contract. If any such beacons or pegs have been disturbed by the Contractor or his employees, the Contractor shall have them replaced by a registered land surveyor at his own cost.

PS-6.7	Existing Services	(Read with SANS 1921 - 1 : 2004 clause 4.17)

The Contractor shall make himself acquainted with the position of all existing services before any excavation or other work likely to affect the existing services is commenced.

The Contractor will be held responsible for any damage to known existing services caused by or arising out of his operations and any damage shall be made good at his own expense. Damage to unknown services shall be repaired as soon as possible and liability shall be determined on site when such damage should occur.

PS-6.8	Management of the environment 	(Read with SANS 1921 - 1 : 2004 clause 4.19)

The Contractor shall pay special attention to the following:

(a)	Natural Vegetation

The Contractor shall confine his operation to as small an area of the site as may be practical for the purpose of constructing the works.

Only those trees and shrubs directly affected by the works and such others as the Engineer may direct in writing shall be cut down and stumped. The natural vegetation, grassing and other plants shall not be disturbed other than in areas where it is essential for the execution of the work or where directed by the Engineer.

(b)	Fires

The Contractor shall comply with the statutory and local fire regulations. He shall also take all necessary precautions to prevent any fires. In the event of fire the Contractor shall take active steps to limit and extinguish the fire and shall accept full responsibility for damages and claims resulting from such fires which may have been caused by him or his employees.

PS-6.9	Overhaul

No payment will be made for overhaul on this contract unless provision is made thereof in specific items.

PS-6.10	Excavations

Due to the depths of sewer lines and their location nets to a water course, the Contractor is to allow in their tendered rates for excavation, for shoring and protection of trenches.  No additional payment will be made for protection of excavations for whatever reason.

PS-6.10	Security

The Contractor shall provide security watchmen for the contract as he deems fit at no extra cost for the Employer.  The Contractor must ensure that all his employees as well as the employees of his subcontractors are able to identify themselves as members of the construction team.

PS-7	CONSTRUCTION PROGRAMME

PS-7.1	Preliminary programme

The Contractor shall include with his tender a preliminary programme on the prescribed form to be completed by all Tenderers. The programme shall be in the form of a simplified bar chart with sufficient details to show clearly how the works will be performed within the time for completion as stated in the Contract Data.

The Contractor shall be deemed to have allowed fully in his tendered rates and prices as well as in his programme for all possible delays due to normal adverse weather conditions and special non-working days as specified in the Special Conditions of Contract, in the Project Specifications and in the Contract Data.

In determining his construction programme, the contractor should allow for disruptions/stoppages/requirements and intermittent “hold” of work while awaiting Engineer’s inspections at the following critical stages:

| Stage |  | Delay |
| --- | --- | --- |
| 1. | Agreements and Compensation for Land with Land Owners | 2 weeks |
| 2. | Excavation works for pipelines and prior to preparation of bedding | 1 day |
| 3 | Excavation works for structures and prior to casting of blinding | 1 day |
| 4. | Following preparation of bedding and laying of pipes and prior to backfilling | 1 day |
| 5. | Prior to commencement of pressure testing of pipelines | 1 day |

No additional payments, other than through scheduled items, will be made for these stoppages/disruptions/constraints.

In addition, the contractor is required to establish the Engineer’s facilities within 14 days of commencement. Should the contractor fail to provide approved establishment within the stipulated 14 days, the contractor will pay a penalty calculated as follows:

- Mileage of the Engineer’s Representative from other offices from the nearest business centre to site and back to office at R3.00/km.

- Rented Office space equivalent to that stipulated in this contract at offices in Port Shepstone or other place closer to the site.

The Employer intends to award this contract for commencement of construction in 
March 2024.

PS-7.2	Programme in terms of Clause 5.6 of the General Conditions of Contract

It is essential that the construction programme, which shall conform in all respects to Clause 5.6 of the General Conditions of Contract, be furnished within the time stated in the Contract Data. The preliminary programme to be submitted with the tender shall be used as basis for this programme. The Contractor's attention is also drawn to clause 5.7.1 of the General Conditions of Contract 2015.

The Employer intends to award construction contracts by March 2024.

PS-8	SITE FACILITIES AVAILABLE

PS-8.1	Contractor's camp site and depot	(Read with SANS 1921 - 1 : 2004 clause 4.14)

The Contractor will be permitted to locate his offices, storage facilities, workshops, latrines, etc, on a site approved by the Engineer, in liaison with the community.

Temporary buildings and fencing are to be neat and presentable and the surrounding areas must at all times be kept in a neat, clean and orderly condition.  The Contractor must not cut down or damage any trees nor make any excavation without the written permission of the Engineer and will be required to restore the site to its original condition on completion of the Works.

All buildings and latrines shall be in accordance with the Local Authority and State Heath regulations and shall be kept in a clean, sanitary condition to the satisfaction of the Engineer.

PS-8.2	Accommodation of Employees

No employees except for security guards will be allowed to sleep or be accommodated on the site in urban areas.

No housing is available for the Contractor's employees and the Contractor shall make his own arrangements to house his employees and to transport them to site.

No informal housing or squatting will be allowed.

The Contractor shall provide the necessary ablution facilities at his camp site and the site of the works for the use of his employees. Chemical toilets only will be allowed where temporary facilities have to be provided.

PS 8.3	Source of Water Supply

The Contractor shall make his own arrangements for the supply of water for construction purposes. The source of water shall be subject to the approval of the Engineer.

The Water Services Authority in the area is Ugu District Municipality. Should the contractor’s source of water be Ugu District Municipality, the contractor will be required to ensure that the water account with Ugu District Municipality is in good standing prior to the issue of a completion certificate. The Engineer will withhold any payments until arrears are cleared with Ugu District Municipality.

PS 8.4	Source of Power Supply

The power supply authority is Eskom. The Contractor will be required to make his own arrangements with, and pay all the requisite connection and consumption charges to Eskom for whatever temporary power supplies he may require for his use on the site and his tender will be held to include for all such costs and charges.

PS-9	SITE FACILITIES REQUIRED

PS-9.1	Facilities Required for the Engineer

PS 9.1.1	Temporary/Permanent Offices

The Contractor is to provide a temporary office for use by the Engineer. The offices should be able to accommodate one full time Engineer’s Representative and two assistants.

The facilities are to be provided, to the satisfaction of the Engineer, within 14 days of commencement date. The Engineer may withhold certification of the first progress payment until these facilities are provided.

PS 9.1.2	Laboratory Facilities

The Contractor will not be required to provide a testing laboratory on site for use by the Engineer.

PS 9.1.3	Sanitary Facilities

All latrines shall conform to the requirements of the Local Authority and shall be subject to approval by the Engineer.  All sanitary fees and charges due under the Local Authority or State Health Regulations or bylaws shall be paid by the Contractor.  Throughout the progress of the contract, all latrines shall be maintained by the Contractor in a clean, sanitary condition to the satisfaction of the Engineer.

PS 9.1.5	Housing Facilities

The Contractor will not be required to provide housing facilities for the Engineer's staff.  However, a provisional sum has been provided in the schedule of quantities for payment through the contract for accommodation for the Engineer’s staff.

PS 9.1.6	Parking Facilities

The Contractor will be required to provide two uncovered parking bays for the Engineer.

PS 9.1.7	Engineer's Transport

The Contractor will not be required to provide transport for the Engineer’s staff.

PS 9.1.8	Security

The Contractor will be responsible for providing adequate security for the Works and for the site establishment.  All costs associated with the provision of security staff shall be borne by the Contractor and should allowed for in the rates tendered for items in the Schedule of Quantities. No additional payments will be made for security measures taken during the contract period, other through the schedule items in the Schedule of Quantities.

PS 9.1.9	Contract staff to assist the Engineer

The following staff will be recruited by the contractor to assist the Engineer in carrying out his services:

| Description of Staff | N⁰ Required | Remarks |
| --- | --- | --- |
| Environmental Monitoring | 1 | Provisional sum provided for appointment as directed by the Engineer. Personnel directed by and report to Engineer |
| Occupational Health & Safety Monitoring | 1 |  |
| Technical Assistant | 1 |  |
| ISD Consultant | 1 |  |
| Community Liaison Officer | 1 |  |

The required personnel will be identified by the Engineer and report to the Engineer. Provisional Sums and the relevant mark-up Items are provided for to cover these costs.

PS 9.1.10	Survey Equipment

The contractor shall provide the following survey equipment, in good condition, for use by the Engineer throughout the duration of the contract:

- A dumpy level

- Measuring tape

- An assistant, when required, to assist the Engineer to operate survey equipment, when provided

PS 10.	EXISTING SERVICES

PS 10.1	Care, Damage and Protection

Known services will be indicated in the tender and contract documents. The Contractor will be responsible for identifying all services with the relevant Service Providers.

The Contractor shall familiarize himself with all services and expose them at the start of the Contract to verify their position and establish their depths.

No additional payment will be made to the Contractor for identifying and locating services. Therefore, the Contractor will have to include the costs thereof in the scheduled items in the Schedule of Quantities.

Any information regarding existing services is given in good faith and without guarantee.

PS 10.2	Blasting

No blasting will be permitted unless the Contractor can satisfy the Engineer that his proposed blasting methods and controls are such that no damage will be caused to the adjoining building structures, pipelines or services.  In any event the Engineer will require the Contractor to plan and execute each blast in such a manner as to ensure that no damage will be caused to any structure, pipeline or service.  In addition, the Engineer will require vibro-recordings to be taken at no additional cost to the Employer.  No blasting is to be carried out in Eskom servitudes or wayleaves unless the Eskom authorities have been advised in writing three weeks prior to blasting.  Where blasting is done adjacent to Eskom power lines, the Contractor shall arrange for a representative of Eskom to be present prior to and during any blast.

PS 10.3	Environmental Aspects

The Contractor will be required to plan and undertake his work in a manner that minimises its impact on the natural environment.  Trees and other vegetation shall, wherever possible, be left undisturbed.  Trees that are marked by the Engineer shall not be damaged and in the event of the Contractor doing so, a penalty will be deducted from monies due to the Contractor.

Every effort shall be made by the Contractor to prevent pollution of the adjacent areas and river and to reduce the noise, dust and fumes emanating from his construction activities.

PS 10.4	Dealing with Water

The Contractor shall include with his tender a preliminary programme on the prescribed form to be completed by all Tenderers. The programme shall be in the form of a simplified bar chart with sufficient details to show clearly how the works will be performed within the time for completion as stated in the Contract Data.

In drawing up his programme, the tenderer is to take into account the following:

- Permissible period of downtime of the existing infrastructure to allow the contractor to make the necessary interconnections: 09:00 up to 16:00, i.e. 7 hours, during the day.

- The infrastructure must be operational every day except for the period mentioned above.

- The infrastructure is currently in use.

- The employer shall be responsible for the operation of all valves and its water supply system.

The Contractor shall not operate any valve unless the Contractor has received from the Engineer prior written permission to do so which permission shall be limited to a specific time and operation in each case unless expressly stated to the contrary in writing by the Engineer.

It shall be the responsibility of the Contractor to give prior written notice timeously (min 2 working days) to the Engineer in every case in which the Contractor may request valve operation or prevention of valve operation by the Employer.

The Employer cannot guarantee watertight closing of valves; it shall be the responsibility of the Contractor to do and provide everything necessary for the timeous, efficient and safe disposal of all water which may leak through closed isolating valves and thence into places from which, in the opinion of the Engineer, the leaking water has to be removed for good reason.   (The Engineer shall certify extra payment in respect of the costs of such valve-leakage-water disposal measures as in his opinion could not reasonably have been avoided or reduced.)

The Contractor shall be deemed to have allowed fully in his tendered rates and prices as well as in his programme for all possible delays due to normal adverse weather conditions and special non-working days as specified in the Special Conditions of Contract, in the Project Specifications and in the Contract Data.

Where necessary, the Contractor shall construct temporary drainage channels to divert ground water or leakage from non-closing valves and fire hydrants from his excavation and excess water must be pumped out.

No compensation for any variation of the actual conditions during construction from the data given will be considered.   Neither will additional compensation be considered for data omitted or inaccurately given.

The rates tendered shall allow for the requirements of this clause and all incidentals.

PS 10.5	Servitudes and Rights of Way

The Employer will, where necessary, obtain permanent servitudes and rights of way along the road routes indicated on the tender drawings.  New servitudes will only be registered after completion of the Works.

PS 10.6	Dealing with Damaged Services

In the event of any service being damaged or accidentally disconnected for any reason, the Contractor shall immediately contact the relevant authority for instruction and shall report the occurrence of the incident.  The damage is to be repaired as soon as possible to the approval of the Engineer and the authority.  The Contractor will be held responsible for paying all costs incurred by the authority or himself as a result of each such incident, where relevant.

PS 10.7	Accommodation of Traffic

The Contractor shall ensure the safe and expeditious passage of traffic at all times and shall provide all necessary temporary road traffic signs, barricades, flagmen, etc to safeguard the travelling public.  Any detours or bypasses constructed by the Contractor shall be adequately signposted, as per the South African Road Traffic Signs Manual, and maintained in such a manner as to provide safe and easy passage of traffic.

The contractor shall also ensure that property owners have access to the properties at all items regardless of pipeline trenches being excavated across driveways.

PS 10.8	Spoil Material

No indiscriminate spoiling of material will be allowed.  All surplus or unsuitable material shall be spoiled, levelled and spread in designated areas as directed by the Engineer.  All haul will be regarded as free haul.

PS 10.9	Finishing and Tidying and Defects Liability Period

On no account must rubble and spoil materials, other materials, equipment or unfinished operations be allowed to accumulate in such a manner as to unnecessarily impede the activities of other Contractors or Authorities.

Finishing and tidying must not simply be left until the end of the construction period.  The Contractor will be entitled, subject to prior agreement with the Engineer and within reasonable limits, to request that work in a particular area and/or work of a particular discipline, be inspected for partial completion.  The specified defects liability period in respect of any specific section of the Works shall commence on the date on which the relevant section is accepted by the Engineer as being completed, i.e. fully commissioned, including finishing and tidying.

On completion of the Contract the Contractor shall ensure that all materials used in the construction of the temporary Site office, workshop and storage yard are removed from Site.  Waste materials such as construction debris and soil contaminated with oil and fuel are to be disposed of at the solid waste disposal site used approved by the Engineer. Prior to the handover of the Site to the Employer, the Contractor and the Engineer will conduct a post construction audit to determine if any additional measures that are to be taken.  The Completion Certificate will only be issued after this stage.

PS 10.10	Employee Accommodation

(See Subclause 3.2.1 of Section A of Part 2 and Subclause 1.2.1 of Section A of Part 3 of SABS 0120)

The Contractor shall conform in all respects with the provisions of any Act, Regulations or By-Law of Ugu District Municipality, which may be applicable to employee accommodation.  Save for a security guard on active duty, no employees may be housed on Site or the Contractor’s campsite after normal working hours.

PS 10.11	Employment of Local Labour

The Employer has determined that 100% of the Contractor’s unskilled labour force shall be made up from the local community.  A labour sub-committee (of a Project Steering Committee) comprising representatives of the community and other stakeholders will be responsible for the recruitment of all local labour.  The Contractor will be required to provide details of the numbers of semi-skilled and unskilled workers he will require, together with their anticipated starting dates.  The PSC through its labour sub-committee will then make this labour available to the Contractor.

A minimum of 50% of the local labour shall comprise of women and, where appropriate, disabled labour shall be employed.  It is a requirement that tenderers acquaint themselves fully with requirements for registration with Unemployment Insurance Fund.

The Employer requires that the successful contractor registers all labour with the Unemployment Insurance Fund.  The local labour rate has been determined at R199 per day per labourer.  The task for excavation by hand has been agreed at 2,4 m³/day (e.g. 0,76 m x 1,0 m x 3,15 m).

During project execution, the successful contractor will be required to provide progress reports indicating to what level these requirements have been met.

PS 10.12	Frequency of Labour Wages Payments

The contractor will be required to pay labour on a fortnightly basis.

PS 10.13	Training and Capacity Building

No training of personnel is required under this contract.

PS-11	REQUIREMENTS FOR ACCOMMODATION OF TRAFFIC

PS-11.1	General

The Contractor will be responsible for the safe and easy passage of public traffic past and on sections of roads of which he has occupation or where work has to be done near traffic.

Accommodation of traffic, where applicable shall comply with SANS 1921-2: 2004: Construction and Management Requirements for Works Contracts, Part 2: Accommodation of Traffic on Public Roads occupied by the Contractor. The Contractor shall obtain this specification from Standards South Africa if accommodation of traffic will be involved on any part of the construction works.

PS-11.2	Basic Requirements

The travelling public shall have the right of way on public roads, and the Contractor shall make use of approved methods to control the movement of his equipment and vehicles so as not to constitute a hazard on the road.

The Contractor shall ensure that all road signs, barricades, delineators, flagmen and speed controls are effective and that courtesy is extended to the public at all times.

Failure to maintain road signs, warning signs or flicker lights, etc, in a good condition shall constitute ample reason for the Engineer to suspend the work until the road signs, etc, have been repaired to his satisfaction.

The Contractor may not commence constructional activities affecting existing roads before adequate provision has been made to accommodate traffic in accordance with the requirements of this document and the South African Road Traffic Signs Manual.

The Contractor shall construct and maintain all temporary drainage works necessary for temporary deviations.

The Contractor shall provide and grant access to persons whose properties fall within or adjoin the area in which he is working.

PS-11.3	Traffic Safety Officer

Where warranted by traffic conditions on or near the site, the Contractor shall nominate a suitable member of his staff as traffic safety officer to be responsible for the arrangement and maintenance of all the measures for the accommodation of traffic for the duration of the project. Duties of the traffic safety officer shall be as set out in SANS 1921 Part 2 and shall also be in compliance with the Occupational Health and Safety Act No 85 of 1993 and the Construction Regulations 2003.

PS-11.4	Payment

The Contractor’s tendered rates for the relevant items in the Bill of Quantities shall include full compensation for all possible additional costs which may arise from this, and no claims for extra payment due to inconvenience as a result of the modus operandi will be considered.

Items that may be considered for payment are specified in SABS 1200 Standardized Specifications and the related project specification.

PS-12	OCCUPATIONAL HEALTH AND SAFETY (Read with SANS 1921 - 1: 2004 clause 4.14)

PS-12.1	General statement

It is a requirement of this contract that the Contractor shall provide a safe and healthy working environment and to direct all his activities in such a manner that his employees and any other persons, who may be directly affected by his activities, are not exposed to hazards to their health and safety. To this end the Contractor shall assume full responsibility to conform to all the provisions of the Occupational Health and Safety Act No 85 and Amendment Act No 181 of 1993, and the OHSA 1993 Construction Regulations 2003 issued on 18 July 2003 by the Department of Labour.

For the purpose of this contract the Contractor is required to confirm his status as mandatary and employer in his own right for the execution of the contract by entering into an agreement with the Employer in terms of the Occupational Health and Safety Act by executing the Agreement form C1.2.4 included in Section C1: Agreements and Contract Data.

PS-12.2	Health and Safety Specifications and Plans to be submitted at tender stage

(a)	Employer's Health and Safety Specification

The Employer's Health and Safety Specification will be included in the tender documents as part of the Project Specifications.

(b)	Tenderer's Health and Safety Plan

The successful Tenderer shall, on receipt of notification that he has been awarded the contract, submit without delay his own documented Health and Safety Plan for the execution of the work under the contract. His Health and Safety Plan must at least cover the following:

(i)	a proper risk assessment of the works, risk items, work methods and procedures in terms of Regulations 7 to 28;

(ii)	pro-active identification of potential hazards and unsafe working conditions;

(iii)	provision of a safe working environment and equipment;

(iv)	statements of methods to ensure the health and safety of subcontractors, employees and visitors to the site, including safety training in hazards and risk areas (Regulation 5);

- monitoring health and safety on the site of works on a regular basis, and keeping of records and registers as provided for in the Construction Regulations;

- details of the Construction Supervisor, the Construction Safety Officers and other competent persons he intends to appoint for the construction works in terms of Regulation 6 and other applicable regulations; and

- details of methods to ensure that his Health and Safety Plan is carried out effectively in accordance with the Construction Regulations 2003.

The Contractor's Health and Safety Plan will be subject to approval by the Employer, or amendment, if necessary, before commencement of construction work. The Contractor will not be allowed to commence work, or his work will be suspended if he had already commenced work, before he has obtained the Employer's written approval of his Health and Safety Plan.

Time lost due to delayed commencement or suspension of the work as a result of the Contractor's failure to obtain approval for his safety plan, shall not be used as a reason to claim for extension of time or standing time and related costs

PS-12.3	Cost of compliance with the OHSA Construction Regulations

The rates and prices tendered by the Contractor shall be deemed to include all costs for conforming to the requirements of the Act, the Construction Regulations and the Employer's Health and Safety Specification as applicable to this contract.  Should the Contractor fail to comply with the provisions of the Construction Regulations, he will be liable for penalties as provided in the Construction Regulations and in the Employer's Health and Safety Specification.

Items that may qualify for remuneration will be specified in the Safety Specifications included or in the Project specifications.

PS-13	ADVERSE WEATHER CONDITIONS

In terms of Clause 5.12.2 of the General Conditions of Contract, extension of time will be considered for abnormal rainfall. The numbers of days per month on which work is expected not to be possible as a result of normal rainfall, and for which the Contractor shall make provision in his tendered rates, prices and programme, are listed in Table     PS-12.1 hereafter. Only the number of days lost as a result of adverse weather conditions, exceeding the number of days listed in Table PS-12.1, will qualify for consideration of extension of time.

During the execution of the Works, the Engineer's Representative will certify a day lost due to abnormal rainfall and adverse weather conditions only:

if no work was possible on the relevant working day on any item which is on the critical path according to the latest approved construction programme; or

if less than 30% of the work force and plant on site could work during that specific working day.

Extension of time as a result of abnormal rainfall and adverse weather conditions shall be calculated monthly being equal to the number of working days certified by the Engineer's Representative as lost due to rainfall and adverse weather conditions, less the number of days allowed for as in Table PS-13, which could result in a negative figure for certain months. The total extension of time as a result of abnormal climatic conditions for which the Contractor may apply, shall be the cumulative algebraic sum of the monthly extensions. Should the sum thus obtained be negative, the extension of time shall be taken as nil."

Table PS-13:   Expected N⁰ of Working Days Lost Monthly Due to Normal Rainfall

| MONTH | Expected number of working days lost as result of normal rainfall |
| --- | --- |
| JANUARY FEBRUARY MARCH APRIL MAY JUNE JULY AUGUST SEPTEMBER OCTOBER NOVEMBER DECEMBER | *5 5 4 1 1 1 1 1 2 3 4 5 |
| TOTAL | 33 days |

(Based on information obtained from the Weather Bureau, Department of Environment Affairs, Margate.  The average monthly rainfall figures quoted, are included for information only, and shall not be taken into consideration for calculation of extension of time. The number of working days lost for December and January allows for the builders' holidays from 15 December 2023 and ending on 09 January 2024.)

PS-14	SITE MEETINGS AND REPORTING

The Contractor will be required to attend site meetings organised by the Engineer. In these meetings the Contractor will be required to provide progress reports and other reports to monitor the outputs of the contractor, as may be required from time to time, to be presented in a format prescribed by the Engineer. The frequency of such meetings will be monthly, as a minimum. However, the frequency can be reviewed, depending on the progress of the contract.

PS-15	PREFERENTIAL PROCUREMENT

For the purpose of this contract the Contractor shall comply with the preferential procurement statement provided in F.3.11 and T2.2 of the Tender Data.

PROJECT SPECIFICATION:  PORTION 2

AMENDMENTS TO THE STANDARD AND PARTICULAR SPECIFICATIONS

INTRODUCTION

In certain clauses the standard, standardized and particular specifications allow a choice to be specified in the project specifications between alternative materials or methods of construction and for additional requirements to be specified to suit a particular contract. Details of such alternative or additional requirements applicable to this contract are contained in this part of the project specifications. It also contains additional specifications required for this particular contract.

The number of each clause and each payment item in this part of the project specifications consists of the prefix PS followed by a number corresponding to the number of the relevant clause or payment item in the standard specifications. The number of a new clause or payment item, which does not form part of a clause or a payment item in the standard specifications and which is included here, is also prefixed by PS, but followed by a new number which follows on the last clause or item number used in the relevant section of the standard specifications.

# Variations and additions to the Standard Specifications:  portion 2

# sabs 1200 PSA :  GENERAL

This section covers the variations and additions to the SANS 1200 Standard Specifications applicable to this Contract, as per SANS 0120. Note: the number in brackets denotes the Standard Clause number.

This section covers the variations and additions to the SANS 1200 Standard Specifications applicable to this Contract, as per SANS 0120. Note: the number in brackets denotes the Standard Clause number.

- General

  - Scope (1)

Replace sub-clause 1.1 with the following:

"This specification covers requirements, principles and responsibilities of a general nature which are normally applicable to all civil engineering contracts as well as the requirements for the Contractor's establishment on Site."

  - Interpretations (2)

    - Definitions (2.3)

(a)	General (a)

Add the following definitions:

“Task: 		A quantified activity or operation.

Task work: 		Work paid for by the completed task or job.

Daily rate: 		The remuneration of a day’s work, regardless of output.

Daily wage: 		See daily rate.

Task rate: 		The remuneration for a completed task.

Labour intensive construction:

The employment of as great a portion of labour as is technically feasible to produce as high a standard of construction as demanded by the specifications and allowed by the funding available, thus the effective substitution of labour for mechanised or motorised plant.

Labour based construction:

See Labour intensive construction.”

(b)		Measurement and payment (c)

Replace the definitions for fixed charge, time-related charge and value-related charge with the following:

"Fixed charge: 		A charge that is not subject to adjustment on account of variation in the value of the Contract amount or the Contract time of completion.

Time-related charge: 	A charge, the amount of which is varied in accordance with the time for completion of the work as adjusted in accordance with the provisions of the Contract.”

    - Abbreviations (2.4)

(a)	Abbreviations relating to standard documents (a)

Add the following abbreviation:

"CKS: SANS Co-ordinating Specification."

  - Materials (3)

    - Quality (3.1)

Add the following:

“Where applicable, materials are to bear the official standardisation mark.

Where proprietary materials are specified, it is to indicate the quality or type of materials or articles required and where the terms "or other approved" or "or similar approved" are used in connection with proprietary materials or articles, it is to be understood that the approval shall be at the sole discretion of the Engineer”.

    - Ordering of Materials (New Sub-Clause)

The quantities set out in the Schedule of Quantities have been determined from calculations based on data available at the time and should therefore be considered to be only approximate quantities.  The liability shall rest entirely and solely with the Contractor to determine before ordering, the required types and quantities of the various materials required for the completion of the Works in accordance with the Specifications and the Drawings issued to the Contractor for construction purposes.

Any reliance placed by the Contractor on the estimated quantities stated in the Schedule of Quantities issued for Biding purposes, or measurements made by the Contractor from the drawings issued for Biding purposes, shall be entirely at the Contractor's risk, and the Employer accepts no liability whatsoever in respect of materials ordered by the Contractor on the basis of Bid Documents.

  - Plant (4)

    - Silencing of Plant (4.1)

Alter the reference to the “Machinery and Occupational Safety Act, 1983 (Act 6 of 1983)” to “Occupational Health and Safety Act, 1993 (Act 85 of 1993)”.

    - Restriction on the Use of Plant (New Sub-clause)

The Contractor shall use only hand tools and equipment in the construction of the portions of the Works identified as being a Labour Intensive Contract, except for the following items of mechanical plant and as approved by the Engineer:

- vehicles to be used for transporting purchased items from the Contractor's campsite or the storage site, to the places on site where they will be incorporated into the Works

- water bowser for transporting water

- pedestrian operated compactors

- wackers

- Excavation equipment (only where digging by hand is impractical due to the nature of the ground as determined by the Engineer).

    - Dealing with water on works

Add to the Sub-Clause

The contractor shall within 14 days from the Commencement Date provide to the Employer/Employer’s Representative a compressive method statement and schematic drawings, of how he intends to construct the weir, paying particular attention that river must be flowing all the times. There must be no disruption to the fauna and flora downstream.

    - Environmental management (new sub-clause)

Add the new sub-clause:

“The Contractor shall take all necessary measures to minimise damages to the natural environment.”

  - MEASUREMENT AND PAYMENT (8)

    - Scheduled Fixed Charge and Value Related Items (8.3)

      - Other Fixed Charge obligations (8.3.3)

Add to the description:

“The Contractor’s initial costs for management of labour intensive construction, as well as complying with the Environmental Management Plan and the New Construction Regulations, 2003 of the Occupational, Health and Safety Act, 1993 (Act 85 of 1993), shall also be included in the Sum Bided.

      - Establishment of Facilities on Site (8.3.2)

    - Scheduled Time Related Items (8.4)

      - Contractual Requirements (8.4.1)

PSA 5.2.2	Health and Safety Obligations (new sub-clause)

(a)	 “The Contractor’s general time related costs for complying with the New Construction Regulations, 2003 of the Occupational, Health and Safety Act, 1993 (Act 85 of 1993) shall be included in the Sum Bided.

General Health and Safety Obligations …………………………………………………………………………….Unit: Sum

The sum Bided shall be paid in instalments pro-rata to the estimated percentage completion of the Works.

PSA 5.2.3	Environmental Management (new sub-clause)

“The Contractor’s time related costs for complying with the Environmental Management Plan shall be included in the Sum Bided.”

Time Related Environmental Management (New sub-clause) ……………………………………………………………………Unit: Sum

The sum Bided shall be paid in instalments pro-rata to the estimated percentage completion of the Works, and shall cover the cost of complying with the recommendations of the Environmental Management Plan for the project.

Sums stated provisionally by the Engineer (8.5)

PSA 5.2.4 – Community Liaison Officer

Add new clause:

“This item refers to the payment for a nominated member of the community to serve as a Community Liaison Officer for the duration of the Contract. The nominated person shall be employed by the Contractor and shall be provided with all necessary employment benefits for the duration of the contract. Monthly payments shall be made to the CLO and claimed from the Contract under this item.

PSA 5.2.4.1	Provisional Sum  for Community Liaison Officer……..…………………Unit:   Prov Sum

PSA 5.2.4.2	Management, overheads, charges and profit on the above item…………….Unit:    %

PSA 5.2.5 – Engineer’s Accommodation

Add new clause:

“This item refers to the payment for accommodation for the Engineer’s representative for the duration of the Contract. The Contractor shall make payments to the nominated establishment on a monthly basis and payment shall be made to the Contractor based on the actual invoiced amounts and payments made, as well as a markup on said amounts paid.

PSA 5.2.5.1	Provisional Sum for Engineer’s Accommodation…….………………Unit:   Prov Sum

PSA 5.2.5.2	Management, overheads, charges and profit on the above item……….Unit:    %

PSA 5.2.6         Provisional Sum for Acceptance Testing (new sub-clause)

A provisional item has been scheduled to cover any acceptance testing specified by the Engineer to ensure that appropriate quality standards are being met in the construction of the Works. The Contractor shall undertake his own testing during the Works, such testing being deemed to be covered in the Bided rates for said items. This specific item refers to additional testing that may be required and requested by the Engineer to be undertaken by an external testing facility to ensure compliance by the Contractor with the standards and requirements as set out.

Payment shall be made for all invoices paid by the Contractor to the external testing facility based on actual invoices approved and requested by the Engineer, with a markup on the item for the Contractor paid separately.

PSA 5.2.6.1 	Provisional Sum for Acceptance Testing…………..………………………Unit:   Prov Sum

PSA 5.2.6.2	Management, overheads, charges and profit on the above item……………....Unit:    %

PSAB 1	ENGINEER’S OFFICE

    - PSAB 1.1 		Name boards

Add the following:

“One name board shall be provided, as detailed on the Bid Drawing. The details shall be confirmed prior to Construction.”

The Bided rate for this item shall include for all materials, plant, labour, profits and any other costs associated with the construction of the name boards and maintenance of same for the duration of the contract.  Payment for this item shall be made as a lump sum for the provision and erection of the name board on site, as well as a monthly maintenance lump sum paid out per percentage progress on the Works.

Pay Item	Description                                                                                                                                                          Unit

PSAB 1.1.1	Fixed charge item – name boards………………………………………………………….sum

PSAB 1.1.2	Time related item – name boards…………………………………………………………..sum

    - PSAB 1.2		 Computers, Printer & Cellphone

Replace with the following:

“The Provisional Sum scheduled shall cover the cost of the Engineer’s and Engineer’s assistant’s computer, printer and cell phone and internet costs for the duration of the contract. The Contractor shall provide the Engineer with 2 hand set cellphones capable of making and receiving national calls, with a built in camera and video capability, text messaging capability and connection to a network for the duration of the contract. In addition to the above, the Contractor shall provide the Engineer with a single data card for the exclusive use by the Engineer’s personnel with a monthly allocation of 5 GB of data for the duration of the Contract. The Contractor shall further provide a laptop with a minimum i7 internal processor, Windows 10, Microsoft Office Excel, Word, Outlook & Powerpoint programmes installed. The Contractor shall also provide for a black & white laser printer on site with photocopying and scanning capability for A4 paper. The Contractor shall ensure that the laptop and printer are in good working condition for the duration of the Contract, and shall allow for the provision of 2 reams of A4 printer paper per month for the use of the Engineer and his staff for the duration of the Contract.”

Payment for this item shall be made on a lump sum basis for the provision of the service under the fixed charge items with a time related lump sum paid per percentage of works progress for the duration of the contract.

Pay Item	Description                                                                                                                                                         Unit

PSAB 1.2.1	Fixed charge item – computer, printer & cellphone	sum

PSAB 1.2.2	Time related item – computer, printer & cellphone	sum

    - PSAB 1.3	 Engineer’s Office (4.1)

Add the new sub-clause:

“The Contractor shall provide and equip the Engineer’s site offices as described hereunder.

The offices shall comprise the following:

- 1 office of area greater than 12 m² in plan for the exclusive use of the Engineer

- 1 office of area greater than 10m²t in plan for the exclusive use of the Engineer

- 1 kitchen

- 1 toilet for the exclusive use by the Engineer.

All offices shall be lockable and shall be equipped as follows:

Large office:

- Boardroom table capable of seating at least 8 people

- 8 chairs for the table

- Air conditioner for heating and cooling

- Window of area at least 1.2 m² complete with blinds

- One double socket electrical plug point

- One overhead double fluorescent light fitting minimum 1.2m long

Smaller Office:

- Desk and chair with a plan area not less than 1.5m²

- 2 x visitors chairs

- Bookcase

- Lockable steel cupboard

- Drawing table of minimum area 3m²

- Air conditioner unit for heating and cooling

- Laser jet printer complete with toner cartridges and paper for the duration of the contract – black and white printing only

- Window of area at least 1.2 m² complete with blinds

- One double socket electrical plug point

- One overhead double fluorescent light fitting minimum 1.2m long

Kitchen:

- Microwave oven minimum 20 litre capacity

- Electric kettle for heating water

- Fridge with capacity not less than 90 litres

- Kitchen sink

- Set of 6 cups and saucers

- Set of 6 coffee mugs

- Set of 6 plates

- Cutlery consisting of 6 spoons, 6 forks and 6 knives

- Consumables for the duration of the contract (tea, coffee, sugar, milk, cleaning products, dishcloths and potable water)

Toilet:

- Lockable door

- Toilet seat

- Flushing mechanism

- Hand wash basin with potable water

- Toilet paper and consumables for the duration of the contract

All offices shall be maintained and cleaned on a regular basis (not less than 3 times weekly) for the duration of the contract. The Contractor is to allow for the replacement of consumables on a needs basis.

Payment for this item shall be made on a fixed cost lump sum for the provision and setup of the facilities, as well as a monthly payment based on the percentage completion of the Works.  The Bided rates shall include for all costs associated with the provision of the offices and services and the maintenance and operation of same for the duration of the contract period.

Pay Item	Description                                                                                                                                                          Unit

PSAB 1.3.1	Fixed charge item – Engineer’s office	sum

PSAB 1.3.2	Time related item – Engineer’s office	sum

    - PSAB 1.4		Engineer’s Vehicle

Add new clause:

“This item refers to the provision of a vehicle on site for the sole use of the Engineer and his representatives. The vehicle shall be provided at the start of the Contract and shall meet the following minimum requirements:

- Single cab

- 4 x 4 capability

- Minimum 2500 cc engine capacity

- Airconditioning unit

- Power Steering

- Not older than 2 years

- Vehicle to be roadworthy

- Vehicle to be licenced

- Doors to be lockable

- All tyres to have minimum of 8mm tread

- Spare wheel, jack and wheel spanner

- Emergency triangle

The vehicle shall be maintained by the Contractor and serviced and licenced in accordance with the regulations. The Contractor shall be responsible for the supply of all fuel and consumables for the vehicle for the duration of the contract. The vehicle shall be used for the undertaking of work on the project by the Engineer and shall be budgeted to travel a distance not exceeding 5000 km per month. The Contractor shall take all necessary insurances on the vehicle including excess waiver for the event of loss of or damage to the vehicle. The vehicle shall be returned to the Contractor upon completion of the contract.

Payment shall be made on a fixed lump sum for the provision of the services as well as a monthly payment based on the percentage completion of the Works. The Bided rates shall include for all costs associated with the provision of, maintenance and operation costs associated with the vehicle. All fuel, oils, consumables, servicing, insurance, wear and tear and any other costs associated with the provision of the vehicle and the operation and maintenance of same for the duration of the contract.

Pay Item	Description                                                                                                                                                          Unit

PSAB 1.4.1	Fixed charge item – Engineer’s vehicle	sum

PSAB 1.4.2	Time related item – Engineer’s vehicle	sum

    - PSAB 1.5		Engineer’s Vehicle Shelter

Add new clause:

“The Contractor shall provide on the site establishment, covered parking for two motor vehicles for the sole use of the Engineer. The shelter shall be constructed of materials that can be readily removed upon completion of the works. The shelter shall have a gravel floor and shall have minimum dimensions of 8m wide x 6m long with no obstructions in the path of the vehicle. “

Payment shall be made on a fixed lump sum for the provision of the services as well as a monthly payment based on the percentage completion of the Works. The rates are to include for all costs associated with the provision of the shelter as well as for the upkeep and maintenance of the shelter for the duration of the contract period.

Pay Item	Description                                                                                                                                                          Unit

PSAB 1.5.1	Fixed charge item – Engineer’s vehicle shelter	sum

PSAB 1.5.2	Time related item – Engineer’s vehicle shelter	sum

    - PSAB 1.6		 Fencing around Site Establishment

Add new clause:

“This item refers to the construction of a security fence around the perimeter of the site establishment. The site shall be fenced off along the perimeter with galvanised weldmesh fencing 2.1m high with appropriate straining posts and stays to suit, as well as a lockable double gate for the vehicle entrance.“

Payment shall be made per metre run of fencing constructed as well as a monthly payment based on the percentage completion of the Works. The rates are to include for all costs associated with the provision of fencing and gate around the site and maintenance and repair of same during the contract period.

Pay Item	Description                                                                                                                                                          Unit

PSAB 1.5.1	Fixed charge item – fencing around site establishment	m

PSAB 1.5.2	Time related item – fencing around site establishment	sum

PSAB 2	Construction (5)

PSAB 2.1	Survey Equipment (New Sub-Clause 5.6)

Add new Sub-Clause :

"The Contractor shall provide the following survey equipment on the Site from the commencement to the completion of the Works:

- *One automatic levelling Engineer's level plus tripod and ancillaries

- *One levelling staff (4m long, 1cm gradations)

- *One staff angle bubble

- *One metal change-point for levelling

- *One spirit laser level (one metre long)

- *One steel-tipped ranging rods each 2,5m long

- *One hammer (2kg)

- Two canvas carry-bags

- *One 30m steel tape - Webco, Stanley, or similar approved.

- *Three 5m steel tape - Webco, Stanley, or similar approved.

- *One measuring wheel

* This survey equipment is for the sole use of the Engineer or his representative on Site. The Contractor shall keep the equipment continuously insured against any loss, damage, or breakage and he shall indemnify the Engineer and the Employer against any claims in this regard.

The Contractor shall arrange for the repair & replacement of any damaged equipment. All equipment provided shall be supplied with the appropriate and valid calibration certification to the Engineer.

The cost of providing and maintaining the equipment is to be included in the contractor’s other fixed charge obligations and general time related items. The equipment shall revert to the contractor when no longer required by the Engineer.

PSC	SITE CLEARANCE

PSC 1	Scheduled items (8)

PSC 1.1	Clear and grub (8.2.1)

Add to the description:

“The free haul for the disposal of materials to a site designated by the Engineer shall be 0.5km from the source.”

PSC 1.2	Take down existing fences (8.2.5)

Add the following to the description:

“Where the Contractor is required to take down existing fences, the Contractor’s price shall include for re-erection and repair of any damage incurred during the taking down or re-erecting of the fences.”

PSDB		Earthworks (Pipe Trenches)

  - PSDB 1		Materials (3)

    - PSDB1.1		Backfill Material (3.5)

In the third line of a) substitute "100 mm "for "150 mm".

    - PSDB1.2		Materials for Reinstatement of Roads and Paved Areas (3.6)

Delete the sub-clauses 3.6.1 and 3.6.2 and substitute:

"Material used in the reinstatement of roadways shall fall into either of the following categories:

(a)	Foundation material recovered from the excavation of trenches across existing roadways, which, if so instructed by the Engineer, shall be set aside and re-used as sub-base material.

(b)	New material that shall conform to the requirements of:

I) 	Clause 3.2.1 of SANS 1200 ME for the sub base

ii)	Clauses 3.2 and 3.3 of SANS 1200 MF for the base course

iii)	Clause 3.2.2 of SANS 1200 ME for the gravel wearing course."

    - PSDB1.3		Selection (3.7)

Delete the second sentence and substitute the following:

"The Contractor is not required to use selective methods of excavating but may do so at his own cost.  The Contractor shall, however, if so instructed by the Engineer, screen or otherwise treat excavated material in order to produce material suitable for bedding or covering or both bedding and covering for the pipeline."

  - PSDB 2		Plant (4)

    - PSDB 3.1		Excavation Equipment (4.1)

Insert at the beginning of this Clause:

“Although Labour Intensive construction methods shall be used for trench excavation, situations could arise where excavating plant is required and then the Contractor”

Add to the Sub-clause:

"Excavations on gradients too steep for normal excavating equipment to operate on (greater than 1:3) or in locations prohibiting the use of normal excavating equipment, such as amongst buildings, may have to be done by hand.  Items have been included in the Schedule of Quantities for necessary hand excavation."

  - PSDB 3		Construction (5)

    - PSDB3.1		Minimum Base Widths (5.2)

Replace the sub-clause with the following:

“Unless otherwise ordered by the Engineer, the trench widths shall be as follows:

Pipe size			Trench width

Up to 160mm Ø			600mm (hand excavation)

Up to 160mm Ø			800mm (machine excavation)

250mm Ø			800mm (machine excavation)

400mm Ø			1000mm (machine excavation)

The Contractor shall only be paid for excavating the above trench widths unless it is deemed by the Engineer that a larger excavation bucket is appropriate where machine excavation is employed.

The Contractor shall use compaction tools that suit the smaller side allowance of trenches excavated by hand.  Because of the reduced side allowance, the Contractor shall take special care to excavate the trenches true to line. Where existing pipes are to be exposed to be removed and replaced, the minimum base widths shall be the pipe outside diameter plus 250mm on either side of the pipe for pipes up to 450mm nominal diameter.

Where two pipes are to be laid in a single trench, the width shall be equal to the sum of the outside pipe diameters plus 300mm between the pipes, plus 150mm on either side of the pipes.

Trench sides shall be as near vertical as possible in order to minimise the quantity of backfill material and to avoid possible difficulties where pipelines have to be installed parallel to existing services, fences, hedges, etc."

    - PSDB3.2		Site Clearance (5.3)

Replace the first sentence with:

“The Contractor shall clear a 2m wide strip along the pipe trench, using labour intensive methods, only when ordered to do so by the Engineer.”

    - PSDB3.3		Trench Bottom (5.5)

Add to the second paragraph:

"Where the bottom of the trench is in water logged conditions, the Engineer may instruct the Contractor to lay a 200mm thick layer of 20mm graded stone, under the pipes."

PSDB 3.4		Backfilling (5.6)

      - PSDB3.4.1 		General (5.6.1)

Add:

"Notwithstanding the requirements of Sub-Clauses 5.6.1 and 5.6.6 of SANS 1200 DB, no pipe joint or pipe fitting shall be covered by either the blanket fill or the main fill prior to the successful completion of the visual inspection and the pressure testing of the relevant section of the pipeline."

      - Disposal of Soft Excavation Material (5.6.3)

Replace the Sub-Clause with:

"Soft excavation material from the trench, which is unsuitable or has become surplus because of bulking, displacement by the pipe and importation, shall be disposed of along the trench servitude, at designated spoil areas or approved spoil areas furnished by the Contractor, as applicable.  The requirements of SANS 1200DA shall apply to overhaul and to free haul for the disposal of surplus excavated material."

PSDB 3.5	Compaction (5.7)

PSDB 3.5.1	Areas Subject to Traffic Loads (5.7.2)

Add to the Sub-Clause :

"for an extent of 1 m on either side of the carriageway at each crossing."

PSDB 4	Measurement and Payment (8)

PSDB 4.1	Basic Principles (8.1)

PSDB 4.1.1	Basic Principles of Measurement (8.1.1.1)

Replace the first sentence with:

“Although the Contractor’s basic unit of measuring performance during a contract using Labour Intensive construction methods is task work, the basic principles of measurement and payment to the Contractor for earthworks for a pipe trench is that the rates tendered for excavation shall cover the cost of excavation and the re-use of the excavated material for backfilling and the disposal of any surplus material along the route of the pipeline within free haul distance of the source.”

Add:

“Where mechanical excavation is required for deep trenches under Labour Intensive construction conditions, the tendered rate shall cover the cost of the excavation only.  Backfilling shall be done by hand.”

      - 8.1.2 (a) and (b)

Replace the sub-clauses with:

All new trench excavations shall be measured by length for the computation of volumetric excavation as described in clause PSDB 4.2. Where existing pipes are exposed, the excavations shall be measured volumetrically.

    - PSD 4.2		Computation of Quantities (8.2)

      - PSDB 4.2.1		8.2.3

Replace the sub-clause with:

“For all new trenches, the Contractor shall be paid for required volumes excavated: Length of trench (m) x Width of trench (m) x Depth of trench (m). The depth of trench will be that depth required to provide the prescribed cover to the pipe: Bedding cradle + pipe diameter + prescribed cover (neat).

The prescribed depth of cover to pipes, unless otherwise ordered by the Engineer, is as follows:

Untrafficked areas: 		600mm cover

Trafficked areas: 		900mm cover

Within district road reserves:	1000mm cover

Where existing pipes are exposed, the Contractor shall be paid for actual volumes excavated.

Widths for the computations for excavations for new trenches as well as exposing existing pipelines shall be as specified in clause PSDB 3.1.”

    - PSDB 4.3		Scheduled Items (8.3)

      - PSDB 4.3.1		Site Clearance (8.3.1)

        - PSDB 4.3.2		Clear vegetation and trees of girth up to 1m

Add to the description in the sub-clause with:

“The rate for clearing along the pipe line route shall be for a 2m wide strip; 1m on either side of the centre line. The rate shall be for the clearance of thick vegetation other than veld grass, or boulders which can be removed by hand, only as ordered by the Engineer.”

        - PSDB 4.3.1.2	Remove topsoil

Replace the first sentence in the description in the sub-clause with:

“The rate shall include for clearing veld grass as well as removing the topsoil to a depth of 150mm along the pipe route. The width shall be the specified trench width.”

      - PSDB 4.3.1.2	Excavation (8.3.2)

Replace the contents of the sub-clause with:

    - “Excavate in the following materials and use for embankment or backfill or dispose of surplus material, as ordered, using hand excavation as ordered by the Engineer:

Excavation in all materials: Unit:	m³

Intermediate Excavation 	Unit:	m³

Boulder Excavation	Unit:	m³

    - “Excavate in the following materials and use for embankment or backfill or dispose of surplus material, as ordered, using plant excavation as ordered by the Engineer. Payment for excavation shall be the metre run between specified depths of excavation with extra over items for the various classes of excavation material encountered.

Excavation in all materials trench width and depth specific	Unit: 	m

Intermediate Excavation 	Unit:	m³

Boulder Excavation	Unit:	m³

Hard Rock Excavation	Unit:	m³

Separate items will be provided for depth increments.  Volumes will be computed from the trench width determined in accordance with PSDB 4.2. The rates shall cover the additional cost of the excavation and handling of the more difficult material and, in the case of rock, of the disposal within free haul distance and the replacement of unsuitable material.

      - PSDB 4.3.3		Existing Services that Intersect or Adjoin a Pipe Trench (8.3.5)

Delete the last sentence of the sub-clause and substitute the following:

"The tendered rate for an item scheduled in terms of 8.3.5.1 and 8.3.5.2 shall include for:

(a)	Care in excavation necessitated by presence of such service in or across the trench.

(b)	All work involved in locating the service by hand excavation.

(c)	Notifying and attending upon the proprietor of the service.

(d)	Supporting and protecting the service while excavating in its vicinity.

(e)	Maintaining the service in operation.

(f)	Supporting and protecting the service while the pipeline is installed, inspected, tested and backfilled.

(g)	Any repairs necessitated by damage caused by the Contractor."

- Medium-Pressure Pipelines

  - Interpretations (2)

    - Abbreviations (2.4)

Add the following:

“HDPE - High Density Polyethylene

MPVC - Modified Polyvinyl Chloride

DI – Ductile Iron”

  - Materials (3)

    - Steel pipes, fittings and specials (3.4)

      - Pipes of nominal bore up to 150mm (3.4.2)

Add the following:

"The pipes shall be 'normalized' or seamless steel pipes and shall be used with malleable cast iron fittings complying with the requirements of SABS 509."

and delete "shall be screwed" in the second and third lines.

    - Other Types of Pipe (3.7)

      - Unplasticized Polyvinyl Chloride (uPVC) pipes

Unplasticized polyvinyl chloride (uPVC) and modified polyvinyl chloride (mPVC) pipes and couplings used for this Contract shall comply with the specifications of SANS 966: 2006 parts 1 and 2 respectively.

      - Polyethylene pipes

Polyethylene pipes shall be in accordance with SANS 4427.

Polyethylene pipes and fittings of less than 75mm nominal diameter shall be Type PE80 PN 16 and Type PE80 PN12.5 for pipes and fittings 75mm nominal diameter and larger and shall be joined by means of compression fittings.

      - High Density Polyethylene pipes

High density polyethylene (HDPE) pipes and associated compression couplings used for this Contract shall comply with the specifications of SANS ISO 4427:1996 and shall be product type 80PE HDPE (equivalent to the Type 4 HDPE pipe of SABS 533).

    - Jointing material (3.8)

      - Loose Flanges (3.8.4)

Add to the Sub-Clause:

Bolts and nuts are to comply with SANS 136.

    - Corrosion protection (3.9)

      - Steel Pipes (3.9.2)

        - Steel Pipes of Nominal Bore over 150mm (3.9.2.1)

Add to the Sub-Clause:

"Unless described otherwise in the Schedule of Quantities, the internal protection shall consist of an epoxy coating by means of the application of an epoxy primer, followed by at least four coats of high-build epoxy material to give a total dry film thickness of at least 250 mm, each coat having a colour different from that of it's predecessor and applied not less than 6 hours and not more than 24 hours after it, care being taken that the previous coat has dried sufficiently to prevent solvent entrapment.

The external protection shall consist of a bitumen coating applied by wrapping with a double layer of bitumen impregnated glass fibre complying with the requirements for Type 1 of SANS 1130 to form a coating of average thickness 5 mm and of minimum thickness 4,5 mm and, on completion of the coating white washing of the sheathing."

      - Protection against Electrolytic Corrosion (3.9.3)

Delete the third line and substitute the following:

"tape or tape impregnated with petroleum based material, or other approved insulating material, shall be applied in".

      - Flexible Couplings (3.9.4)

All flexible couplings shall be thoroughly wrapped with tape impregnated with a petroleum-based material.

      - Valves (3.10)

Valves shall comply with the requirements of Project Specification PF: Valves, meters and chambers

    - Manholes and surface boxes (3.11)

      - Bricks (3.11.1)

Delete the first sentence and substitute the following:

"Bricks shall be obtained from an approved manufacturer and shall be either engineering bricks that comply with the applicable requirements of SANS 227: 2007 or solid concrete masonry units (222 x 106 x 73) that comply with the applicable requirements of SANS 1215: 1984."

      - Sand (New Sub-Clause)

Add new Sub-Clause:

"Sand used for mortar (general purpose) and for plaster (external) shall comply with the applicable requirements of SANS 1090: 2002."

PSL.2.6.3.	Cement (New Sub-Clause)

Add new Sub-Clause:

"The cement used on the Works shall be CEM 1, grade 42.5 complying with the requirements of SANS EN 197-1: 2000."

  - Construction (5)

    - Laying (5.1)

      - Depths and cover (5.1.4)

        - General (5.1.4.1)

Delete the Sub-Clause and substitute the following:

"Except as allowed in sub-clause 5.1.4.3, water mains shall be so laid in road verges and erven that the minimum cover from the finished surface level to the top of the pipe barrel is as per PSDB 4.2.1."

    - Jointing methods (5.2)

      - Concrete Spigot and Socket Pipelines (5.2.4)

Add to this sub-clause:

"Rubber joint sealing gaskets which comply with the applicable requirements of SANS 676 (or SANS 677) for the type of joint recommended by the approved manufacturer shall be used for making the joint."

    - Valve and hydrant chambers (5.6)

      - General (5.6.1)

Replace "Drawing L-1" with "Typical Drawings”.

      - Construction of Chambers (5.6.2)

Replace "Drawings L-1, L-2 and L-3" with "Typical Drawings”.

    - Brickwork in Chambers and Manholes (5.8)

Delete the eleventh line and substitute the following:

"Mortar for brickwork and plasterwork shall be composed of one part of cement to four parts of sand."

Twelfth and thirteenth lines to be deleted.

Add to the Sub-Clause:

"Plaster is to be applied in one coat not less than 12mm in thickness."

    - Lifting and relaying of existing pipes (5.9)

Alter the title to read:

"Lifting, relaying of, and joining into existing pipes"

Add to the sub-clause:

"Where a connection into an existing pipe is required, shall carefully assemble the components of the new connection to ensure that the assembly will fit into the space occupied by the pipe length to be removed.  The connection shall be made without undue delay."

    - Marker posts (New sub-clause)

'Marker posts shall be placed to mark valves or the location of a water main as directed by the Engineer.  Details of the marker posts are shown on the drawings."

    - Road Crossings (New sub-clause)

“Road crossings shall be executed per the details provided in the drawings. Prior to construction of road crossings, the Contractor shall inform the Engineer and the responsible road traffic management of the intended work a minimum of 7 days prior to the work being executed.

As part of the road crossing construction, the Contractor shall provide all necessary signage, including warning signs at least 100m either side of the crossing, warning road users of the work, as well as all other signage to ensure that traffic is smoothly handled around the crossing. Works shall be executed in half widths to enable traffic to pass without total stoppage. Appropriate signal persons shall be used to direct and control traffic for the duration of the work in that area.

Reinstatement of the road shall be as follows:

Tar roads – The existing asphalt surface shall be saw cut to form a neat, uniform edge for reinstatment and the layerworks above the sleeve pipe shall be as per the details provided. Initially, the layerworks shall extend to the road surface level and compacted to ensure that the road crossing does not cause a dip in the road. The final reinstatement of the asphalt layer shall be completed a minimum of 28 days after completion of the road crossing. This is to ensure that adequate compaction and settlement has taken place prior to the new asphalt surface being constructed. Prior to the reinstatement of the asphalt surface, the base layer shall be ripped to a minimum of 50mm below the finished surface level and compacted with a roller vibrator to compact as much of the layer as possible. Thereafter the area shall be primed with an appropriate primer to be approved by the Engineer, and hot mix asphalt used to reinstate the tarred surface.

Gravel roads – the layerworks shall be constructed and compacted as per the details provided and bult up to reach the final road surface level. The crossing shall be maintained for a minimum period of 3 months after construction to ensure that any dip in the road crossing shall be attended to and filled and compacted within 48 hours of being informed of said depression in the crossing.

For all road crossings, the Contractor shall ensure that the crossing is maintained at all times to ensure that the depressions caused by the works shall not be a nuisance to the public. Road crossings for tar roads shall be maintained on a regular basis until the final tar surface has been reinstated.

  - Measurement and Payment (8)

    - Schedule Items (8.2)

      - Supply, Lay, Joint and Bed Pipes Complete with Couplings (8.2.1)

Delete the fourth and fifth lines and substitute the following:” the handling, inspecting, transporting, forming joint holes, bedding, laying, jointing, cutting, testing and, when relevant, disinfecting of the pipes and the joints.  (See Clause 8.2.4)".

      - Anchor/Thrust Blocks and Pedestals (8.2.11)

Delete the last line and substitute the following: "formwork, concrete, reinforcement (if any), and screeding to top surfaces".

      - Valve and hydrant chambers (8.2.13)

Alter the description to read: “Valve, hydrant chambers and hydrant pedestals.”

Add: "The rate for hydrant pedestals shall cover the cost of formwork, joint sealants and concrete."

      - Marker posts (New Sub-clause)………………………………………………..Unit:№

"Separate items will be scheduled for various marker posts.  The rate shall cover the cost of manufacturing and installing or of casting in-situ and painting of the marker posts."

      - Connecting to an existing pipeline (New Sub-clause)………………………..Unit:№

“The rate shall cover the cost of cutting into the existing pipeline, as scheduled, any preparation necessary for new fittings to be installed, and the removal of unwanted fittings. New fittings shall be claimed separately.”

      - Road crossings – tar roads  (New Sub-clause)…………………………………….…..Unit: m

      - Road crossings – gravel roads  (New Sub-clause)………………………………….…..Unit: m

“The rate for the construction of road crossings shall include for all costs associated with the execution and construction of the crossing, including labour, plant, equipment, signage, materials and additional costs. Payment shall be made per metre length of road crossing and shall be measured as the nett length of the HDPe pipe used for the road crossing. The costs for the PVC sleeve pipe and HDPe pipe shall be included in the rate. The cost for the flange adaptors is measured elsewhere and shall NOT form part of the rate for road crossings.”

- Bedding (Pipes)

  - Materials (3)

    - Bedding (3.3)

Add to the Sub-Clause:

“The bedding for all rigid pipes laid under this Contract shall be of Class A or C (Drawing LB-1) as applicable and scheduled except that joint holes (pockets) shall be provided in the bedding, as per Drawing LB-2, at each pipe joint and coupling.  No sharp-edged stones shall come into contact with either the pipes or the couplings (joints).  No extra payment will be made for forming joint holes (pockets).”

    - Selection (3.4)

      - Suitable Material available from Trench Excavation (3.4.1)

Delete the sub-clause and substitute the following:

“The excavation of a pipe trench shall comply with the requirements of Sub-Clause 5.4 of SANS 1200 DB, and the provisions of Sub-Clause 3.7 of SANS 1200 DB (in terms of which, for the purposes of providing bedding materials, the Contractor is not required to use selective methods of excavating) shall apply.  Nevertheless, the Contractor shall take every reasonable precaution to avoid burying or contaminating material that is suitable and is required for bedding or covering the pipeline.  If, in the opinion of the Engineer, bedding material can be produced from the excavated material, the Contractor if so ordered by the Engineer, shall screen or otherwise treat the excavated material in order to produce material suitable for bedding (See also Sub-Clause 8.1.2.).”

  - Plant (4)

PSLB 2.1	Placing, compacting and testing equipment (4.1)

      - Placing and compacting (4.1.1)

Replace the sub-clause with:

“The Contractor shall provide adequate tools and equipment for the placing and compacting of the bedding by hand as specified in 5.1.3 and 5.1.4.”

  - Construction (5)

    - General (5.1)

      - Trench (5.1.1)

        - Width (5.1.1.1)

Replace the Sub-Clause with:

“The Contractor shall so excavate each trench that the width conforms to the requirements of Sub-Clause 5.2 of SANS 1200 DB and its project specification.”

      - Details of Bedding (5.1.2)

Replace the contents of the sub-clause with:

“Ductile iron pipes shall be bedded and protected in accordance with the details shown on Drawing LB-1 of SANS 1200-LB, appropriate to Class C bedding for rigid pipes, while the bedding required for uPVC, mPVC and HDPE pipes have been detailed on the drawings.”

      - Compacting (5.1.4)

When sand is used for the bedding of pipes and for backfilling over pipes, the degree of compaction attained shall be 100% of modified AASHTO density.

    - Selection (3.4)

      - Suitable material, requiring screening, available from trench excavation (new sub-clause)

Copy the sub-clause 8.4.1, but replace the second sentence with:

“The Contractor shall screen the excavated material in order to produce material suitable for bedding or covering the pipeline.”

    - Placing and Compacting Rigid Pipes (5.2)

      - Class 'A' Bedding (5.2.1)

Delete the first sentence of 5.2.1(a) and substitute the following:

"The pipes shall be supported on a continuous cradle of 20/19 grade concrete".

      - Class B and Class C Bedding (5.2.2)

Delete the third, fourth and portion of the fifth lines and substitute the following:

"The pipes shall be bedded on a continuous mound of selected granular material in the manner shown in Drg LB-3 (b) or (c) as relevant.  The remainder of the bedding shall be placed in layers under the overhang and up the sides of the pipe, each layer being compacted, until thicknesses are reached as shown on Drg LB-1 (a) or (c) as relevant".

      - Stone Bedding (New sub-clause)

Add new Sub-Clause:

"Where ordered by the Engineer, special drains consisting of 200 mm thickness (See PSDB 5.5) of 6mm to 20mm graded stone extending the full width of the trench shall be provided below the bedding to the pipes.  The excavation for these drains will be measured in cubic metres at the rate applying to unsuitable excavation below the bottom of the trench.  The stone filling will be measured for payment in cubic metres.  All measurements in this connection will be to a width equal to the specified base width of the trench".

    - Concrete Casing to Pipes (5.4)

Add to the Sub-Clause:

"Where concrete casing is ordered by the Engineer it is to be of 20/19 grade concrete with a minimum thickness of 150mm above the top of the pipe".

  - Measurement and Payment (8)

    - Principles (8.1)

      - Supply of Bedding Materials Measured Separately (8.1.1)

Add to the description:

“Therefore, bedding acquired from alongside the trench that does not require loading, transporting and offloading of the material at the point where it is required, shall not be measured under the supply of bedding materials.”

      - Volume of Bedding Materials (8.1.3)

Add to the sub-clause:

a)	"The volume of bedding material shall be measured net i.e. the volume of the pipe is to be deducted".

      - Disposal of displaced material (8.1.5)

Replace the contents of this sub clause with the following:

"Material displaced by the pipeline and by importation of material from sources other than trench excavation, shall be disposed of as specified in SANS 1200 DB - sub-clause 5.6.4 and its relevant Project Specification."

    - Scheduled Items (8.2)

      - Provision of Screened Bedding from Trench Excavation for Pipelines (new sub-clause)

Add a new sub-clause:

“(a) Screened selected granular material………………………………………………..Unit: m³

(b)  Screened selected fill material……………………………………………………..Unit: m³

The rates shall cover the cost of acquiring, from within 0.5km, insitu trench material, of screening it (10mm sieve), delivering it to points alongside the trench spaced to suit the Contractor’s methods of working, and of disposing of displaced material within a free haul distance of 0.5km.”

Add the note as per item 8.2.1.

- VALVES, METERS AND CHAMBERS

  - Scope

This specification covers the specific requirements for valves and chambers for the project.

  - Interpretations

    - Supporting specifications

Where this specification is required for a project, the following specifications shall, inter alia, form part of the Contract Document:

a)	SANS 1200 A or SANS 1200 AA, as applicable

b)	SANS 1200 D or SANS 1200 DA, as applicable

c)	SANS 1200 G or SANS 1200 GA, as applicable

    - Definitions

For the purpose of this specification, the definitions and abbreviations given in the applicable of the specifications listed in PF 2.1 shall apply.

  - Materials

    - Concrete

All concrete work shall be carried out in accordance with the requirements of SANS 1200 G or SANS 1200 GA, as applicable.

    - Valves general

Valves shall be of the types specified in the schedule or on the drawings, and shall be capable of withstanding the applicable test pressures.  All valves shall be supplied complete with coupling and jointing material. Unless otherwise stated in the Schedule of Quantities or otherwise not applicable, all valves shall be supplied with operating caps. Satisfactory temporary end covers shall be provided to protect threads, flanges and prepared ends of valves from damage during transportation and handling on site.

Valves shall be so transported, stored and handled as to prevent damage.  Valves damaged in any way shall be removed from the site.

    - Gate valves

All gate valves shall comply with the requirements of SANS 664 and shall carry the SANS mark.  The valves are to be cast iron fitted with non-rising spindles and all valves shall be of the resilient seal type except those that are fitted for scour purposes, which shall be the wedge type. The direction of spindle rotation for valve closing will be clockwise.

Gate valves shall be of a class commensurate with a maximum working pressure as defined by the Engineer or as shown on the drawings.

The valve trim shall be Type B, gunmetal trim, to SANS 664 i.e. gunmetal seats (body and gate), bronze spindle, and gunmetal spindle nut.

The seating rings on valves up to and including 300mm diameter shall be pressed into undercut recesses, machined into both the gate and valve body in such a manner that the permanent distortion of the seating ring prevents them becoming loose.

    - Air valves

The air valves shall be the following Vent-O-Mat types or similar approved:

All pipelines: 	50mm Ø Vent-O-Mat RBX valve.

    - Pressure reducing valves

Pressure reducing valves shall be hydraulically operated, diaphragm actuated Bermad control valves for waterworks, Model 720. The flanged bodies shall be ductile iron and have a minimum pressure rating of 16 bars. The tubing shall be copper. The pressure reducing valves shall be fitted with pressure gauges.

    - Pressure relief valves

Pressure relief valves shall be hydraulically operated, diaphragm actuated Bermad control valves for waterworks, Model 730. The flanged bodies shall be ductile iron and have a minimum pressure rating of 16 bars. The tubing shall be copper. These shall be fitted with pressure gauges.

    - Meters

Meters shall be Meinecke (Sensys) COSMOS WPD meters or similar approved. These shall have flanged, cast iron bodies, fusion bonded sintered epoxy coatings and a pressure rating of 16 bars, unless otherwise shown on the drawings.

    - Strainers

The strainers shall be flanged cast iron Meinecke (Sensys) COSMOS WPD-F strainers, or similar approved, with a pressure rating of 16 bars, unless otherwise shown on the drawings. The sieve element shall be the standard stainless steel sieve.

    - Gabions and reno mattresses for scour valves

Reno mattresses and gabion baskets shall be in accordance with the SANS 1580 specification.  The geotextile shall be grade A2 Bidim or similar approved product. The wire basket shall be made of hexagonal mesh class A galvanised mild tensile steel wire, in accordance with the SANS 675 specification.

    - Chamber materials

Materials used to construct chambers shall be as per the requirements of clause PC Building Work in this document. Chamber marking shall be done in black road marking paint to SANS 731. The Contractor shall use a stencil for lettering, ensuring each letter is at least 100mm in height.

    - Locks

The Contractor shall supply keyed-alike locks for each lockable manhole cover installed. These shall have solid brass bodies with stainless steel shackles, such as Viro 50mm, or similar approved.

  - Plant

All tools and equipment for the handling of the material and the proper completion of the work shall be provided by the Contractor.

  - Construction

The layout drawings shall show the positions of all valve and meter chambers. The Engineer shall confirm each of these positions on site.

    - Air valve chambers

Air valve chambers and fittings shall be constructed as detailed on the construction drawings:

    - Scour valve chambers

Scour valve chambers and fittings shall be constructed as detailed on the construction drawings:

    - Isolating valve chambers

Isolating valve chambers and fittings shall be constructed as detailed on the construction drawings.

    - Meter chambers

Meters and associated fittings shall be housed in chamber structures constructed as detailed on the construction drawings:

  - Tolerances

    - General

The method of measurement and accuracy of dimensions required for the completed building work of the chambers shall be as described in SANS Code of Practice 0155, unless otherwise specified in the Project Specifications.

  - Testing

    - General

The pipework and fittings of the completed chambers shall be subjected to the same hydraulic testing as the lines on which they are constructed.

PSG 	Concrete (Structural)

  - Materials (3)

    - Cement (3.2)

PSG 1.1.1	Applicable Specifications (3.2.1)

Unless agreed to otherwise by the Engineer, the cement used on the Works shall be CEM 1, grade 42.5 complying with the requirements of SANS ENV 197-1.

PSG 1.1.2	Storage of Cement (3.2.3)

Add to the sub-clause:

“Cement shall not be kept in storage for longer than three weeks without the Engineer's permission.  The cement store shall be run on a first in, first out basis.”

    - Aggregates (3.4)

PSG 1.2.1	Applicable Specification (3.4.1)

Add to the Sub-Clause:

“Sand from a source selected by the contractor and approved by the Engineer after testing will be used under this Contract.

The Contractor shall demonstrate by means of a report from an approved laboratory that the aggregates do not exhibit excessive shrinking properties, in accordance with clause C.14 of appendix C of SANS 1083.

The fineness modulus of the sand aggregate shall not vary by more than 0.2 from the fineness modulus of the sand used in the trial mix.  Where the variation in fineness modulus exceeds this limit, the mix shall be adjusted to suit.  If the fineness modulus of the fine aggregate varies by more than 0.5 from the sand used in the trial mix, the Engineer may call for a new trial mix to be made for re-approval.

PSG 1.2.2	Use of Plums (3.4.2)

The use of plums will only be permitted, if agreed to by the Engineer, in mass-fill concrete.

    - Admixtures (3.5)

Unless approved by the Engineer, neither admixtures nor air-entraining agents shall be used in any concrete.

  - Plant (4)

    - Formwork (4.5)

PSG 2.1.1	Design (4.5.1)

Add to the Sub-Clause:

“The Contractor shall arrange for a professional engineer to design and sign the drawings for the formwork (including all supports to be used for the roof shuttering).”

PSG 2.1.1	Ties (4.5.3)

Add to the Sub-Clause:

“The water tightness requirement of the structure shall be taken into account when deciding upon the type of tie to be used.  The cover requirement will apply to ties left permanently in place.”

  - Construction (5)

    - Reinforcement (5.1)

      - Bending (5.1.1)

Add to the Sub-Clause:

“Reinforcement shall be cut with cropping or shearing equipment only.  Cutting torches shall not be used.”

      - Fixing (5.1.2)

Add to the Sub-Clause:

“No welding of reinforcement will be permitted.”

    - Formwork (5.2)

      - Classification of Finishes (5.2.1)

Delete Clause 5.2.1(b) and replace with:

“This finish shall be obtained by the use of steel-faced forms arranged in a regular pattern to fit the appearance of the structure.  After stripping, all small fins, bulges and other projections shall be removed, surface honeycombing, surface discolorations and other irregularities repaired and the surface rubbed to from a smooth finish of uniform texture and colour.  The finish shall be to Degree of Accuracy 1 tolerances defined in Clause 6.2.2 and 6.2.3.”

Add to the Sub-Clause 5.2.1 (c) :

“The quality of the formwork to the external surfaces shall fall within the "Special" category and shall be such that no after-treatment e.g. rubbing down, other than the sealing of ferrule holes (which themselves shall be placed with precision in a regular pattern) will be necessary.  The formwork used shall be unblemished and erected in a regular pattern so that the joints shall be a feature of the finished surface which shall be to Degree of Accuracy 1 tolerances as defined in Clauses 6.2.2 and 6.2.3.”

      - Removal of Formwork (5.2.5)

Rephrase the first two lines of 5.2.5.2 to read:

“For this purpose and except as allowed in 5.2.5.3, the formwork shall remain in place, after all the concrete has been placed in the relevant lift, for the appropriate minimum period of time given in Table 2.”

    - Holes, Chases and Fixing Blocks (5.3)

Add:

“Fixing blocks for the attachment of fixtures may be embedded in concrete if the strength or any other desirable feature (such as appearance) is not, in the opinion of the Engineer, impaired thereby.”

      - Chamfers (New Sub-Clause)

Unless otherwise noted on the drawings, all exposed sharp edges shall be chamfered 20 x 20 mm.

    - Pipes And Conduits (5.4)

Add to the Sub-Clause:

“2 No. G.M.S. Ventilation Pipes are required to be supplied and constructed into the roof slab of the reservoir in position as shown on the drawings.  Each G.M.S. Ventilation Pipe is to be provided with a puddle flange, and the exterior opening is to have an "insect proof" galvanised wire mesh cover.”

    - Concrete (5.5)

      - Quality (5.5.1)

PSG 3.5.1.1	Consistency (5.5.1.2 (b))

Delete the paragraph (b) and substitute the following:

(b)	by the Engineer in respect of prescribed mix and strength concrete, or

PSG 3.5.1.2	Durability (5.5.1.5)

Add to the Sub-Clause:

“The exposure conditions at the site of the works are to be considered as being severe.”

PSG 3.5.1.3	Prescribed Mix Concrete (5.5.1.6)

| Grade | Size of stone (mm) | Cement (kg) | Sand (m³) | Stone (m³) |
| --- | --- | --- | --- | --- |
| 20 | 19 | 50 | 0.11 | 0.140 |
| 15 | 19 | 50 | 0.13 | 0.160 |
| 10 | 37.5 | 50 | 0.16 | 0.22 |

Ignore the fourth to tenth lines inclusive from the sub-clause and substitute the following;

“The grades of prescribed mix concrete are designated 20, 15 and 10 and are composed of cement, sand and stone, as specified herein before, proportioned as listed in the accompanying table.

While the proportion of cement to the combined quantity of sand and stone must remain constant for each grade of concrete, as set out in the table, the relative proportions of sand and stone are to be adjusted if required by the Engineer, so as to attain the most suitable consistency of concrete, due allowance being made for the bulking of sand due to moisture.

The addition of water shall be regulated by the use of properly calibrated containers, only sufficient water being added as will in the opinion of the Engineer, afford a workable mix.

The fine and coarse aggregate approved for use in strength concrete Grades 30 and 25 are to be used for prescribed concrete mixed Grades 20 and 15.

PSG 3.5.1.4	Strength Concrete (5.5.1.7)

| Grade | Size of stone (mm) | Cement (kg) | Sand (m³) | Stone (m³) |
| --- | --- | --- | --- | --- |
| 30 | 19 | 50 | 0.080 | 0.110 |
| 25 | 19 | 50 | 0.095 | 0.125 |

Replace the contents of the sub-clause with:

“The grades of strength concrete are designated Grade 30 and Grade 25 and are composed of cement, sand and stone, as specified herein before, proportioned as listed in the accompanying table.

The concrete mixes for Grade 30 and Grade 25 strength concrete shall be designed by the Portland Cement Institute’s laboratory nearest to the site of the Works, or other competent laboratory approved by the Engineer.

The concrete mix for Grade 35A strength concrete shall be OPC Fly ash (FA) or slag are to be factory blended into a mixture such that the FA forms 25% by mass of the combined mixture.  The maximum and minimum cementitous mixture contents of the concrete shall be 450 and 325 kg/m³ respectively.  The maximum water content shall be 200 l/m³ and the minimum cement/water ratio shall be 2.0. curing of the concrete to be strictly in accordance with SANS 2001-CC1 :2007 and SANS 0100-2 clause 20.8

At least three weeks before placing any strength concrete on the Works, the Contractor shall supply and deliver to a laboratory at his own cost, samples of the aggregates he proposes to use in the strength grade concrete.  While the proportion of cement to the combined quantity of sand and stone must remain constant for each grade of concrete, as set out in the table, the relative proportions of sand and stone may be adjusted to achieve the requirements of this Specification.  The proportions given above are to guide the Tenderer in pricing the grades of strength concrete.

PSG 3.5.4.5	No-fines Concrete (New sub-clause)

No-fines concrete shall be composed of cement and coarse aggregate only, the fine aggregate being, omitted from the mix.  The proportions of the cement and stone shall be one part by volume of cement to eight parts by volume of stone.  The stone shall comply with the grading requirements of 19 mm single-sized crushed stone to Table 7 of SANS 1083.

Only sufficient water shall be added to the mix to produce a smooth grout to completely cover each and every particular of aggregate.

Proportions may be varied on site with the approval (or to the direction) of the Engineer to obtain a more satisfactory result.  The upper surface of the no-fines is to be finished off with a wood float to provide a smooth working surface while adding just sufficient dry mix mortar (1 to 8) to close the upper surface of the voids in order to prevent the ingress into the interstices of foreign matter.

Mixing shall be carried out in a mechanical batching plant and the hopper shall first be charged with the aggregate to which a small quantity of water has been added to moisten the aggregate particles.  The cement shall then be added and shall be followed by the remainder of the water.

The no-fines concrete shall be placed within 20 minutes of having been mixed and shall be rodded and hand tamped into position.  The use of vibrators will not be permitted.

No traffic shall be permitted to traverse the surface of the no-fines concrete during the three days following upon the placing of the no-fines concrete and then only over planks or boards placed for this purpose.

      - Batching (5.5.2)

PSG 3.5.2.1	Aggregates (5.5.2.3)

Add to the Sub-Clause:

“Batching is to be by mass using an approved type of weigh-batching plant.”

      - Mixing (5.5.3)

PSG 3.5.3.1	Ready Mixed Concrete (5.5.3.2)

Delete the first sentence and substitute the following:

“Concrete produced at a central concrete production facility other than at the site of the Works shall only be accepted for use in the Works with the prior and express approval of the Engineer.  When such approval has been given, the Engineer shall then decide whether or not to accept the test results obtained by the facility concerned.”

      - Placing (5.5.5)

PSG 3.5.4.1	Dropping Concrete Freely (5.5.5.5)

Replace the contents with:

“Dropping concrete freely will only be permitted if the Engineer is satisfied that this is the only practical method of placing.”

PSG 3.5.4.2	Pumping of Concrete (5.5.5.9)

Delete the sub-clause 5.5.5.9 and substitute the following:

“The placing of concrete by pumping will not be permitted.”

PSG 3.5.4.3	Placing in Continuous Walls (New Sub-Clause)

Add new sub-clause:

In the case of continuous walls, these are to be cast in lifts of such height that each lift can be poured uninterruptedly in one continuous operation over the entire perimeter of the wall.  No vertical or inclined construction joints of any kind will be permitted in continuous walls unless they have been specifically ordered or authorised by the Engineer.  The placing of concrete shall commence at convenient points on the perimeter of the wall and shall proceed both ways simultaneously so that fresh concrete meets fresh concrete.  Any rest pauses, such as for meals, shall be avoided as far as possible, and the Contractor may be required by the Engineer to make the operation continuous by working shifts.  A workable arrangement must be made before each concreting operation commences.

PSG 3.5.4.4	Blinding Layer (New Sub-Clause)

Add new sub-clause:

Beneath all structural grades of concrete or elsewhere, if so ordered by the Engineer, or shown on drawings, the bottom of the excavation is to be covered by a blinding layer (screed) in Grade 15/20 concrete to a specified depth to prevent disturbance of the ground and to serve as an even and accurate positioned working floor for setting steel and placing foundation concrete. This blinding layer shall be laid immediately after excavations have been taken out and trimmed to the required depths and have been inspected and approved by the Engineer.

PSG 3.5.4.5	Under-drainage Layer (New Sub-Clause)

Add new sub-clause:

Quantities have been included in the Schedule of Quantities for the placing of a no-fines concrete under-drainage layer between the top of the blinding and the underside of the structural concrete floors where shown on the drawings.

      - Construction Joints (5.5.7)

PSG 3.5.5.1	General Preparation of Construction Joints (5.5.7.3)

Delete sub-clauses (a), (b), (c), and (d) and substitute:

All horizontal and vertical construction joints shall be cleaned of all dirt and loose particles and shall be prepared to the satisfaction of the Engineer.  All intersections of construction joints with concrete surfaces which will be exposed to view shall be made straight and level or plumb and shall be constructed to the details shown on the drawings.

The Contractor shall provide a compressor on site for the whole period during which concreting is in progress, and this must be available for cleaning concrete faces prior to placing fresh concrete or pouring joints.

“Blowing” off may generally be carried out on horizontal surfaces but under special circumstances approved by the Engineer it may also be carried out on vertical surfaces.  The surface concrete to be prepared shall be between 4h and 8 h old after completion of placing and shall be blown off using a mixture of air and water under a pressure of at least 500 kPa or by using a high pressure water jet until all dirt, laitance, etc Is removed and particles of clean coarse aggregate are exposed sufficiently to produce a rough surface.  Any loose particles of coarse aggregate shall also be removed.  The success of this method of preparation depends on selecting the correct time (dependent on the type of cement) so that the concrete has set to just the necessary degree of hardness, The operation may therefore require to be undertaken outside normal working hours and at night.  When the surfaces are at least 12 h old any remaining loose fine aggregate particles shall be washed off.

“Scabbling”, which refers to removal of all surface laitance plus roughening the concrete surface with pneumatic picks in order to expose the coarse aggregate in a uniform pattern, may be carried out on both horizontal and vertical surfaces.  The surfaces to be prepared in this manner shall be at least 12 h old after mixing the concrete.  At least 35% of the roughened surface area shall consist of exposed course aggregate.

All surfaces either prepared, by “blowing-off” or by ”scabbling”, shall be kept continuously wet until the next lift of fresh concrete is to be placed against them; the minimum time being 12 h.

The use of approved wet-to-dry epoxy resin concrete adhesive, strictly in accordance with the manufacturer's instructions, will be permitted in the formation of concrete joints at surfaces where the concrete is older than 7 days.

PSG 3.5.5.2	Placing Fresh Concrete at Joints (New Sub-Clause)

Vertical construction joint surfaces shall be, as instructed by the Engineer, either 	smooth, clean and kept damp for at least 24 h before placing fresh concrete against them, or scabbled, cleaned and dampened as specified above.

Horizontal construction joint surfaces shall have been “scabbled” or “blown off”, cleaned and kept continuously wet as specified above before fresh concrete is placed over them.  Immediately before placing the fresh concrete, the damp surface of the set concrete shall be evenly coated (by brushing or brooming) with a layer of cement mortar between 10 mm and 15 mm thick.  The water/cement ratio and the cement/sand ratio of this mortar shall be the same as that of the fresh concrete to be placed and the mortar shall be produced by leaving the coarse aggregate fraction out of a batch of the fresh concrete.  Coating with mortar is to be done in stages immediately before areas of set concrete are covered with fresh concrete, so that no mortar is exposed for longer than one hour after mixing, or less if the mortar has become dry or has started to set before being covered with fresh concrete.  Any dried out mortar shall be removed and, after cleaning the surface, shall be replaced with fresh mortar.

No fresh concrete shall be placed on the top surface of concrete, which is laterally restrained (e.g. by formwork or by in-situ earth) while the top layer of concrete is between 3 hours and 12 hours old after mixing.  No fresh concrete shall be placed on top of the concrete with an unrestrained lateral surface while the top layer of concrete is between 2 hours and 12 hours old after mixing.

      - Curing and Protection (5.5.8)

Add to the Sub-Clause:

“Not withstanding the acceptable methods of curing itemised under (a) to (c) of the sub-clause, the walls of thin-wall reservoirs or other structures shall be subjected to continuous spray curing for a minimum period of 7 days.”

Delete from the sub-clause all references to the curing periods relating to concrete made with Portland Blast Furnace Cement since the use of the latter is not permitted in terms of the Contract.

      - Adverse Weather Conditions (5.5.9)

PSG 3.5.7.1	Hot Weather Concreting (5.5.9.2)

Add to the Sub-Clause:

“When concrete operations are being carried out at ambient temperatures in excess of 32ºC, the Contractor shall apply the relevant recommendations for hot weather concreting set out in PCI 305 ‘Recommended practice for hot weather concreting’ .”

      - Concrete Surfaces (5.5.10)

        - Exposed Surfaces of Concrete (5.5.10.1)

Add to the Sub-clause:

“Concrete surfaces that require special treatment before or after the striking of forms and the treatment to be given are as detailed in the Schedule of Quantities.”

        - Unformed Concrete Surfaces (5.5.10.2)

Add to the Sub-clause:

"All unformed concrete surfaces shall be finished to one or more of the following classes of finishes:

Class 1 : Screeded Finish

Immediately after being poured the concrete shall be screeded with a straight edge working between templates set accurately to line and level.  No mortar shall be added to overcome surface irregularities.  These shall be made good by rescreeding or by the addition of concrete.

Class 2 : Wood Floated Finish

After screeding to line and level and when the water sheen has disappeared, the concrete surface shall be trowelled by hand with a wood float to a uniform consolidated surface free from any trowel marks and uniform in texture and appearance.

Class 3 : Steel Trowelled Finish

Commence as for Class 2 and finish with a steel trowel.  The final finish shall be done at the correct time, for example, while the concrete is still sufficiently plastic to take polish but when it has hardened sufficiently to prevent drawing water and fine materials to the surface.  Any adherence of mortar to the steel trowel indicates that the correct stage has not yet been reached.

        - Positions of Surface Finishes (New sub-clause)

a)	Top of foundations (external to reservoir wall): Class 1 - Screeded finish.

b)	Top of foundations and slabs (internal to reservoir wall): Class 3 - Steel trowelled finish.

c)	Top of walls: Class 3 - Steel trowelled finish.

d)		Top of roof slab: Class 2 -Wood floated finish.

        - Tolerances (New sub-clause)

a)	Surface Class 1 shall not vary by more than 6 mm measured from a 3 m straight edge placed anywhere on the surface.

b)	Surface Class 2 and 3 shall not vary by more than 3 mm measured from a 3 m straight edge placed anywhere on the surface

c)	Special surfaces such as bearing seats shall be finished to a higher degree of accuracy, as shown on the drawings."

      - Grouting (5.5.13)

Add at the end of the sub-clause the following:

“Grouting shall be done to the instruction of the Engineer using materials of suitable consistency as follows.  Unless otherwise directed, grouting mixtures shall consist of one part cement to two parts concrete sand by volume, well mixed and with sufficient water added to obtain the required consistency.  Where recesses to be filled are of appreciable dimensions, the Engineer may direct the Contractor to replace a proportion of sand with fine stone to reduce shrinkage.”

        - Liquid Grout (New Sub-Clause)

Add new Sub-Clause:

“Where liquid grout is required for bolt holes, etc, water shall be added in such quantity that, when the material is thoroughly mixed and stirred, it shall flow readily so as to fill all recesses and air spaces in the work to be grouted.  Before grouting any section of the work with liquid grout, the surfaces to receive grout shall first be thoroughly cleaned and flushed with water.  The grout shall then be introduced in such a manner as to fill effectively all recesses.  When the grout has set the surface of the work shall be finished off flush and smooth with cement mortar.”

        - Grouting of Pipes/Specials through Walls (New Sub-Clause)

Add new sub-clause:

“Where entry holes for pipes / specials have been proofed in the walls, the Contractor shall be responsible for the grouting in of such pipes / specials regardless of whether or not these have been supplied by himself.

Before commencing the positioning in holes of any pipes/specials the Contractor

(a)	Remove all shuttering and boxing remaining in the holes;

(b)	Make any alterations required to the position and shape of the holes;

(c)	Thoroughly clean the sides of the holes so as to obtain, satisfactory bond surface for the new concrete; and

(d)	Free all surfaces of the pipes / specials of all coatings, and thoroughly scrape and clean the pipes / specials.

After accurately positioning the pipes / specials in the respective holes, the Contractor shall fix the pipes / specials in the holes.

Immediately prior to grouting being carried out by the placing of mortar and concrete around the pipes, the surface of the existing concrete shall be saturated with water.  All surplus water shall be removed and the surface covered with a layer, approximately 12 mm thick, of mortar consisting of three parts concrete sand and one part cement.

The concrete ingredients shall be mixed and placed as dry as possible to obtain a dense, waterproof concrete.  Where a watertight seal is required, the concrete shall be carefully worked around the puddle flange, if any, and the pipe barrel of body of the special, shall be vibrated in layers so as to obviate any failing away from pipe / special surfaces of the concrete already placed.  The whole shall, when set, forms a dense, homogeneous, and waterproof mass.  A spare vibrator with an independent power source shall be kept in readiness to ensure continuity of placing in the event of the breakdown of the duty vibrator.

Smooth formwork that has been suitably strengthened for use with a vibrator shall be provided for facing the concrete around each pipe / special.”

        - Dry-Packed Grout (New Sub-Clause)

Add new sub-clause:

“When dry-packed grout is specified, under base plates etc, only sufficient water shall be added to make the mixture ball when squeezed in the hand.  Before any grouting is done with dry caulking the surfaces between which the caulking is to be placed shall first be thoroughly cleaned and flushed with water.  All surplus visible water shall be wiped or blown away and the dry caulking shall be forcefully rammed or hammered into place using suitable tools.  Exposed surfaces shall be finished off neatly with a trowel and extensive exposed areas shall be covered with wet sacking and kept damp for at least 24 hours.

Where additives are required for grouting operations, these shall be brought onto site in the manufacturer’s unopened containers and used strictly in accordance with the manufacturer’s instructions, which the Contractor shall not fall to obtain.  If necessary, the Engineer may require the Contractor to undertake preliminary tests to check the behaviour of proprietary additives under the conditions obtaining on the site.”

        - Epoxy Grout (Epoxy mortar type only) (New Sub-Clause)

Add new sub-clause:

“The manufacturer’s instructions shall be observed when an epoxy grout is used.”

        - Cement Mortar (New Sub-Clause)

Add new sub-clause:

“Where cement mortar is specified for filling around pipes etc. water shall be added to obtain a firm paste, which can be worked with a trowel but is not fluid.  Surfaces to receive mortar shall be well wetted and excess water allowed to drain, or be removed. The mortar shall be worked into place with a trowel or tamping rod, exposed surfaces floated off, covered with wet hessian for 24 hours, and allowed to harden without disturbance.”

      - Joints (New Sub-Clause)

        - Fibreboard (New Sub-Clause)

Add new sub-clause:

“Fibreboard shall be provided between concrete sections wherever shown on the drawings.  Fibreboard shall be impregnated and treated with a special bituminous compound to protect it from weathering, e.g. “F1excell”, as manufactured by Expandite (Pty) Ltd or a similar approved board of comparable composition, which shall be securely fixed in position to avoid distortion or displacement while concreting operations are in progress. “

        - Expansion Joints (New Sub-Clause)

Add new sub-clause:

“Joint recesses to receive sealing compound are to be formed to the dimensions and shapes indicated on the drawings, these recesses are to be formed with rough sides and so shuttered that the shuttering can be removed without any timber having to be left in the recesses.  Shuttering shall be left in the joints until the joints are ready for priming and filling with sealant.  After the removal of the shutters, joints shell be cleaned by mechanically operated wire brushes and shall be hacked and scabbled and all dust removed.”

        - Sealing Joints (New Sub-Clause)

Add new sub-clause:

“The sealing of the joints (contraction / movement) is to be carried out by the Contractor under the supervision of a representative of the specialist firm supplying the sealing compounds.  The Contractor is to be responsible for supplying these approved materials, transporting them to site, storing and using them, as required, and providing all labour, tools, equipment and everything necessary to prime and fill the joints.

Before priming and pouring, the joints recesses are to be thoroughly cleaned and dried out, in which connection, the use of compressed air is stipulated, to the approval of the Engineer.

No sealing of joint recesses is to be carried out until at least 21 days after the adjacent concrete has been cast.

Every care shall be exercised by the Contractor to ensure that the work shall be carried out in accordance with the requirements of this specification and in strict conformity with any special instructions given by the manufacturers for the proper use and treatment of the sealing materials provided by them.”

      - Anchor bolts to Pipelines (New Sub-Clause)

Add new sub-clause:

“Concrete pipeline anchors at horizontal bends, vertical bends and on steep slopes shall be constructed where directed by the Engineer in accordance with type drawings to be supplied.  Bolts, clamping straps and reinforcement shall be provided as directed.

In general, anchors will be provided at all horizontal bends in flexibly coupled pipelines and at such vertical bends as the Engineer may decide.  Details of the anchors will be supplied by the Engineer.”

      - Bituminous Coatings to Earth Faces (New Sub-Clause)

Add new sub-clause:

“All earth covered concrete surfaces shall receive two applications of an approved bituminous coating such as Ebsco E55 Bituminous Waterproofing Compound or similar approved.

The coatings shall be applied strictly in accordance with the manufacturer's instructions and shall be repaired to the satisfaction of the Engineer if damaged during backfill operations."

      - Waterproofing of Roof Slabs (New Sub-Clause)

Add new sub-clause:

“Roof slabs shall receive at least two coats of a suitable waterproofing compound such as Bituseal Liquid or similar approved.  The compound shall be applied strictly in accordance with the manufacturer’s instructions.  The sealed surface shall be protected from damage both prior to and during the placing of the protective layer of stone detailed on the drawings.”

  - Tolerances (6)

    - Permissible Deviations (6.2)

      - Specified Permissible Deviations (6.2.3)

Add to the sub-clause:

“Except for the special smooth and special finish described in PSG 3.2.1 above, where applicable, the Contractor shall work within the limits of the permissible deviations laid down for Degree of Accuracy II with the following modifications:

Foundations:

Position on plan	± 20 mm

Surface level	± 10 mm

Above foundations:

Position on plan	± 20 mm

Surface level	± 5 mm”

  - Tests (7)

    - Testing (7.2.)

      - Laboratory Testing (7.2.3)

Add to the sub-clause:

“The Contractor will be liable for all costs incurred in designing the concrete mixes and making structural concrete cubes and having these tested.”

PSG 6	Crawl Beam

Add new clause:

“The item refers to the construction of a 200 IPE crawl beam in the pumpstation as per details. The rate shall include for all costs associated with the procuring, manufacture, painting, installation and load testing of the beam. The beam shall be provided with a load test certificate from an accredited testing facility once installed and the appropriate signage provided on the beam indicating the safe load capacity. An appropriate chain and pulley system shall be supplied and installed with the crawl beam to be able to lift a load of 800 kg along the length of the beam. Payment shall be made per metre of beam finally constructed while a separate pay item is provided for the chain and pulley system.

PSG 6.1	Crawl beam ……………………………………………………………………………………………….Unit : m

PSG 6.2	Chain & pulley……………………………………………………………………………………………..Unit : sum

PSG 7 – Miscellaneous Pumpstation Items

Add new clause:

“This item refers to the various items required for construction of the pumpstation.

PSG 7.1 – Sliding joint at walls

This item refers to the provision of a sliding joint between the top of the masonry walls and the roof slab. The use of 2 layers of 3 ply malthoid shall be made for this purpose with the top of the walls being cleaned free of any excess mortar and dust, the malthoid being placed in –situ and kept in position for the pouring of the concrete roof slab. The rate shall include for all costs associated with this work. Payment shall be made per linear metre of the joint so constructed.

PSG 7.1	Sliding joint at walls……………………………………………………………………………………….Unit :m

PSG 7.2 – GMS Louvres

This item refers to the construction of galvanised mild steel louvres in the pumpstation. The louvres shall conform to the size as shown on the drawings and shall be manufactured from mild steel and hot dip galvanised before transporting to site. After fixing into position repairs shall be made to any galvanizing that has been damaged by means of cold galv or other such products as approved by the Engineer. The tendered rate shall cover all costs associated with this activity in the procurement, manufacture, delivery to site, installation and repairs if necessary of the louvres. Payment shall be made per louvre installed.

PSG 7.2	GMS louvres………………………………………………………………………………………………Unit : no.

PSG 7.3	Transformer Door

Add new clause:

“This item refers to the supply and installation of transformer doors. The doors shall be of standard steel construction and hot dip galvanised prior to delivery to site. The doors shall be manufactured in accordance with the relevant SANS specifications applicable to the manufacture of same. The larger door shall have a cut-out to allow for the crawl beam to pass through.

The tendered rate is to include for all costs associated with the procurement, manufacture, delivery to site and installation and repairs if required, as well as all and any other costs associated with the installation of the doors in the building. Payment shall be made per door so supplied.

PSG 7.3.1 – Transformer door 3000 high x 1829 wide…………………………………………………………..Unit :no.

PSG 7.3.2 – Transformer door 2438 high x 1829 wide…………………………………………………………..Unit :no.

PSG 7.4	Cable ducts

Add new clause:

“This item refers to the construction of cable ducts within the building to cater for electrical cabling. The ducts shall consist of Ø90mm PVC pipes and bends complete with draw wire for electrical cables. The unit of measurement shall be the linear metre of pipe constructed.

PSG 7.4	Cable ducts ……………………………………………………………………………………………….Unit : m

PSG 7.5	Brickwork

Add new clause:

“This item refers to the construction of masonry brickwork in structures. The brickwork shall be of engineering quality NFX bricks and shall be SANS approved. Bricks shall be laid in stretcher bond formation. All mortar and construction shall be in accordance with the requirements of SANS 10400. The tendered rate shall include for all costs associated with the supply of material, labour, mortar mix, plant, tools and equipment including profit for the construction of brick walls as specified. Payment shall be made per square metre of wall constructed.

PSG 7.5	Brickwork 230mm wide………………………………………………………………………………………Unit : m²

PSG 7.6 	Filter Media

Add new clause:

“This item refers to the provision and incorporation into the Works of filter media for the sludge pond. The filter media shall consist of specially selected materials to effect filtering of the wastewater from the package treatment plant before discharging into the Luhane River. Materials shall be provided as specified and laid in the sludge beds in layers as specified on the construction drawings. The rate for this item shall include for all costs associated with the construction of the filter media in the Works and shall b epaid for per cubic metre of material in it’s final compacted state.

PSG7.6.1 – Filter media 200mm thick fine sand……………………………………………………………………..Unit: m³

PSG7.6.2 – Filter media 200mm thick Umgeni sand……………………………………………………………………..Unit: m³

PA	PREFABRICATED RESERVOIRS

PA 1	Scope

This specification covers the specific requirements for the Galaxy Range of Reservoirs or similar approved.

PA 2	Interpretations

PA 2.1	Supporting specifications

Where this specification is required for a project, the following specifications shall, inter alia, form part of the Contract Document:

a)	SANS 1200 C, as applicable

b)	SANS 1200 D, or DA, as applicable

c)	SANS 1200 L, as applicable

d)	SANS 1200 LB, as applicable

PA 2.2	Definitions

For the purpose of this specification, the definitions and abbreviations given in the applicable of the specifications listed in PL2.1 shall apply.

PA 3	Materials

The materials for this section shall be provided by the Nominated Sub-Contractor.

PA 4	Plant

All plant and equipment for the handling of the material and the proper construction of pipelines shall be provided by the Nominated Sub-Contractor.

PA 5	Construction

PA 5.1	General

The reservoir shall be constructed in the position as indicated by the Engineer’s representative on site. The location shall be positioned such that there is adequate access around the reservoir as well as space for the required inlet and outlet chambers, scour chambers etc.

PA 5.2	Testing of reservoir

The reservoir shall be tested for water tightness as follows:

The reservoir shall be filled o the top water level and marked. The reservoir shall stand with the water at this level for a period of 7 days at which stage the drop in water level will be measured. The allowable drop in water level shall be 10mm over 7 days. Water for testing shall be provided free of charge by the Employer for one test. All subsequent tests resulting from failures shall be for the Contractor’s account.

PA 5.3	Disinfection of reservoir

The Contractor shall disinfect the reservoir in accordance with the conditions of the disinfection procedures as outlined elsewhere in this document.

PA 6	Scheduled Items

PA 6.1	Supply & Construct Galaxy Reservoir by supplier complete………………………………..Unit : PC Sum

PA 6.2	Contractor’s markup on item…………………………………………………………………………………..Unit  : %

The rate shall cover the cost of supplying and installing the specified Galaxy reservoir by the supplier on site. The extent of responsibility of the Works is defined by the flanged connections into and out of the reservoirs with an overflow, inlet, outlet and scour flange being provided by the supplier. The contractor shall clear the site and prepare the site for the construction of the reservoir. Payment for the reservoir work shall be made based on the actual invoice received from the tank supplier after work has been complete. A percentage markup shall be applicable by the Contractor for the handling and administration costs associated with this activity.

- Disinfection of Reservoirs

  - Scope

This specification covers the disinfection of potable water reservoirs before commissioning.

  - Procedure

    - Cleaning

The walls and floors of the reservoir shall be cleaned by thorough sweeping and scrubbing before disinfection.  All scaffolding, planks, tools, rags, or any other material not part of the structure shall be removed before cleaning the reservoir.

    - Disinfection

The inner surfaces of the reservoir or tank shall be saturated with a strong (200mg/l) chlorine solution.  The solution may be prepared by dissolving 30 grams of 65 percent strength powdered calcium hypochlorite to every 10 litre of water.  The powder should be made into a paste and then added to the water.  If liquid bleach or sodium hypochlorite is used, the solution shall consist of 125ml of 5 percent strength bleach to 40 litres of water.

The solution shall be sprayed over all surfaces of the empty reservoir or tank by suitable spraying equipment.  The surfaces to be disinfected shall be wetted with the chlorine solution and remain in contact with the chlorine solution for at least thirty minutes before disinfection shall be considered complete and before the reservoir may be filled.  In order to ensure the surfaces remain wet for the required period, it may be necessary to spray the surfaces more than once only.  Care shall be taken to also spray the surfaces of the inlet and outlet piping inside the reservoir or tank.

The Contractor shall ensure that the persons conducting the disinfection operations are protected with suitable protective clothing and that they are equipped with gas masks or respirators.  The footwear, after being thoroughly washed with soap and water, and the protective clothing of the persons conducting the disinfection, shall be sprayed with the chlorine solution before entering the reservoir or tank, before commencement of the disinfection operation.

  - Measurement and Payment

The activity of disinfecting the reservoir shall be measured and paid as a sum on the assumption that the disinfection operation will be done once only and will require 200 litres of one of the chlorine solutions specified in PF 2.2.  The sum tendered shall be reduced or increased pro-rata to the actual quantity of solution used for the disinfection of the reservoir.

  - Scheduled Items

| - Disinfection of Reservoir | Unit: Sum |
| --- | --- |

The tendered rate shall cover the Contractor’s cost of supplying all the chemicals, water, labour and protective clothing to disinfect the reservoir as specified.  Disinfection shall be measured once only unless the Contractor is ordered to perform additional work inside the reservoir once disinfection is complete.  Separate items shall be scheduled for reservoirs of different sizes if applicable.

# project SPECIFICATION:  portion 2

# sabs 1200 PSD:  EARTHWORKS

PSD-1	EARTHWORKS

The Contractor is referred to SANS 1921 - 5: Earthworks activities which are to be performed by hand

PSD-3	MATERIALS

PSD-3.1	Classification for excavation purposes

PSD-3.1.2	Classes of excavation

The classes of excavation in clause 3.1.2 shall in general apply to all excavations where use is made of conventional methods and plant and equipment.

Where labour-intensive methods applicable to targeted labour are specified, soft excavations shall be defined as follows:

“PSD-3.1.2(a)	Soft excavation

Soft excavation for labour-intensive work where excavations are to be carried out by hand methods, shall be excavation in material that can be efficiently removed and loaded with picks, shovels and other hand tools by an average able-bodied person or group of persons. Soft excavation shall include small boulders that can be removed by hand methods.

Soft excavation can be further broken down by introduction of an additional class such as “Soft Excavation Class A”, which is excavation defined as soft, but which can only be excavated with difficulty.

The criteria for classifying Soft Excavation Class A shall be as follows:

Granular material: -	dense material with high resistance to penetration by the point of a geological pick; several blows are required for removal of material; 7 to 15 blows of the dynamic cone penetrometer are required to penetrate 100 mm; and

Cohesive materials -	stiff to very stiff material requiring 6 to 8 blows of the dynamic cone penetrometer to penetrate 100 mm, where:

"stiff" material 		can be indented by thumbnail; slight indentation produced by pushing a geological pick point into the soil; cannot be moulded by fingers; and where:

"very stiff" material	can be indented by thumbnail with difficulty; slight penetration of point produced by blow of geological pick.

Where soft excavation class A material is encountered, it shall be measured and paid for as an extra over soft excavation.

PSD-5	CONSTRUCTION

PSD-5.1	Precautions

PSD-5.1.1	Safety

PSD-5.1.1.2	Safeguarding of excavations

- Add the following subparagraph:

“(g) 	The Contractor or his agent or his representative shall not require or allow any person to work under unsupported overhanging material or in an excavation which is more than 1,5 m deep, and any excavation which has not been adequately supported or braced if there is a danger of the overhanging material or the sides of the excavation collapsing.  The support, shoring or bracing to be designed and constructed by the Contractor, shall be strong and sturdy enough to support the sides of the excavation in question.”

PSD-5.2.2.1	Excavations for general earthworks and for structures

- Add the following additional subparagraph:

“(f) 	The Contractor shall so plan his cut-to-fill operations that all excavated material is used in the manner that is most appropriate.

The Contractor shall conserve all suitable surplus material and he shall not borrow, spoil or waste any material unnecessarily.  If excavated material designated for a particular purpose become contaminated, is incorrectly used or becomes unavailable through injudicious planning of excavation operations, the Contractor shall replace the contaminated material and make good any shortfall with material of quality at least equal to that of the said selected material.

Where selection of excavated material is required, the method of excavation shall be so arranged as to avoid double handling.  Wherever possible excavated material shall be placed in its final position without being stockpiled.  If stockpiling is unavoidable, materials intended for different uses shall be stockpiled separately

# project specification:  portion 2

# sabs 1200 PSD:  EARTHWORKS (Pipe trenches)

PSDB-5	CONSTRUCTION

PSDB- 5.1	Precautions

PSDB-5.1.5	Trench Excavations (additional subclause)

The precautions for excavations as specified in Clause 5.1.1 of Section 1200 D, 1200 DA, and the relevant clauses in PSD and PSDA, shall also apply to all trench excavations.

The Contractor shall take all the steps necessary to ensure that no person is required or allowed to work in a trench or any other unsupported overhanging excavation which is more than 1,5 m deep, and any excavation which has not been adequately supported, shored or braced if there is any danger whatsoever of the sides of the excavation collapsing. The support, shoring or bracing to be designed and constructed by the Contractor, shall be strong and sturdy enough to support the sides of the excavation in question.

# project specification:  portion 2

# sabs 1200 GA:  CONCRETE (SMALL WORKS)

PS GA-3		MATERIALS

PS GA-3.2		Cement

PS GA-3.2.1	Applicable specifications

The standard cement specifications SABS 471, SABS 626, SABS 831, SABS 1466 and SABS 1491, have been withdrawn and are replaced by SANS 50197-1: Common cements, and SANS 50413-1: Masonry cement. These specifications will be applicable to this contract and the descriptions and types of cements, where specified, will be based on the designations as defined in these specifications.

PS GA-5.4.1.4 	Prescribed mix concrete

Add the following:

“The structural concrete in this contract shall comply with the following specification.

The minimum 28 day strength shall be as specified in drawings

The maximum water/cement ration shall be 0.42

The minimum cement content shall be 400 kg/m3

The cement used must be extended with a minimum of 30% Fly Ash or 50% GGBS

A detailed mix design by an approved concrete testing laboratory before any concrete is poured in the works and provision shall be made by the contractor for the cost of the design in his rates.

PS GA-8:	MEASUREMENT AND PAYMENT

PS GA-8.1	Measurement and rates

PS GA-8.1.2	Reinforcement

Replace subclause 8.1.2.2 with the following:

PSGA-8.1.2.2	Mild steel and high tensile steel will be measured by mass for the diameters or range of diameters as scheduled.

Welded mesh will be scheduled separately for each type and mass per square metre of mesh.”

Replace subclause 8.1.2.3 with the following:

“PSGA-8.1.2.3	The unit rate for steel bars shall cover the cost of supply, cutting, bending, placing in position, and fixing of the reinforcing and supporting steel scheduled. The rate shall also include the provision of all spacer devices and binding wire, as well as the cost of tests in terms of SANS 920.

The unit rate for welded mesh shall cover the supply, cutting and placing of mesh, as well as the cost of all waste due to laps.”

Project specification:  portion 2

sabs 1200 lb:  bedding (pipes)

PS LB 3.3	BEDDING

Add the following to LB 3.3:

All pipes shall be classified as rigid pipes and shall be laid on a Class C bedding except sub soil drainage, which shall be classified as flexible pipes.

PS LB 5	CONSTRUCTION

PS LB 5.1	General

PS LB 5.1.4	Compacting

Substitute "90 % of mod AASHTO" in LB 5.1.4 with "93 % of mod AASHTO (100 % for sand)".

PS LB 8	MEASUREMENT AND PAYMENT

PS LB 8.2	Scheduled Items

PS LB 8.2.2.4	From stockpile (provisional)

a)	Selected granular material 	  Unit  :  m3

b)	Selected fill material 	  Unit  :  m3

The rate shall cover the cost of obtaining, handling and transport regardless the distance, of the required bedding material from the stockpile, the delivery thereof at positions that are spaced along the trench in such a way as suits the working method of the Contractor, as well as the removal of material displaced by this importation within the free-haul distance.

## PARTICULAR SPECIFICATION:  PA

BRICKWORK AND PLASTER

PA1	SCOPE

PA1.1	This specification covers the general requirements for buildings and other masonry structures, including plastering.

PA2	INTERPRETATION

PA2.1	Other relevant Standards/Specification

This specification should be read together with SABS 1200 AA.

PA2.2	Applicable Edition of Standards

Each standard specification referred to in this specification shall be deemed to be the latest edition, applicable on the tender closing date.

PA2.3	Definitions and Symbols

For purposes of this specification, the definitions and symbols given in the National Building Regulations and Building Standards Act, 1977 (referred to further on in this specifications as "Building Act"), where applicable, shall apply.  (Definitions: pages 5 to 14, Symbols: page 23.)

PA3		MATERIALS

PA3.1	Cement

Cement shall conform to the requirements of SABS 471.

PS3.2	Lime

Lime shall be of approved manufacture, well burnt and of uniform quality conforming with SABS 523.

PA3.3	Sand

Sand to be used for mortar and plaster shall comply with the requirements of SABS 1090.

PA3.4	Clay Bricks

Clay bricks must conform to SABS 227. A sample of bricks to be used for construction must be given to Engineer for approval before construction bricks are delivered to site.

The contractor will be required to carry out necessary tests and provide certificates for compliance of the bricks with SABS 227. The cost of these tests will be deemed part of the scheduled rates and no additional payment will be made therefore.

Best quality engineering bricks shall be used for all foundation and concealed situations.

PA3.5	Damp-Proofing

Material used as a dampproof course shall conform to the requirements contained either in SABS 248 or in SABS 952.  Type FV fibre-felt sheets or Type C polyethylene sheets shall be supplied under the contract.

PA3.6	Fibre Cement Sheets

Fibre cement flat sheets, minimum 15 mm thick, shall comply with the requirements of SABS 685.

PA3.7	Storage

PS3.7.1	Cement and Lime

Cement and lime stored on the site shall be properly protected against moisture to the satisfaction of the engineer.

PA4	CONSTRUCTION

PA4.1	Brickwork

Brickwork shall be well and regularly bonded, with no false headers and none but whole bricks except where legitimately required as closers.  All bricks must be thoroughly dampened before laying and each brick is to be laid with full joints and pressed into its bed so as to squeeze out superfluous mortar and give a finished joint not exceeding 8 mm thick in the case of the face work or 13 mm thick in the case of plastered walls or work not exposed to view.  All joints, both horizontal and vertical, notwithstanding any grade custom to the contrary, are to be filled solid with mortar for their full width and depth, each course being flushed with mortar, worked well down into all vertical joints before the succeeding course is laid.  Horizontal joints and vertical joints of face work shall be pointed flush in manholes and catchpits, but shall be pointed and finished with a tooled recessed joint elsewhere.  Plastered walls shall have the joints raked out to a depth not less than 13 mm and not more than 20 mm, and subsequently refilled with mortar of the same proportions as the original bedding mortar.  In no circumstances may joints to be so formed as to expose any perforation in the units.

Wire ties, where required, shall be stainless steel and are to be installed at 5 per square metre.

PA4.2	Mortar

The mix proportions for the mortar are given below:

Portland cement	50 kg

Lime			0-40 l

Sand*			200 l max.

* measured loose and damp

PA4.3	Plastering

Plaster shall be of the same proportions as the bedding mortar. Any other plaster mixes will be subject to the approval of the Engineer.

PA4.4	Dampproof Courses

The areas to be covered by dampproof courses are indicated on the drawings.  Dampproof shall be laid on a surface which shall not contain any sharp objects which may perforate the membrane.  The full width of the wall and the whole area under the floor is to be covered by the membrane and shall overlap by not less than 100 mm under the floor, and by not less than 150 mm under the wall.  All joints shall be effectively sealed.  Where shown on the drawing, the dampproof course is to be stepped up one course of brickwork in the inner skin.  Proper returns are to be made at all doorframes.

PA4.5	Window Sills

Windowsills shall be formed as shown on the drawings and as hereafter described:

Dampproof sheeting shall be provided one brick course below the sill and shall be turned upwards and terminate behind the window frame to provide an efficient weather-tight seal.

All external sills and some internal sills, where shown, shall be formed in quarry tiles and other internal sills where shown are to be of fibre cement sheet minimum thickness 15 mm to SABS 685 with approximately 20 mm projection beyond the finished face of the walls.

External sills shall be laid to a 20 weathered slope while internal sills shall be laid horizontal.

All tiles shall be bedded in 3:1 cement mortar and neatly pointed.

PA4.6	Lintels with Brickwork Reinforcement

Lintels over doors, windows and openings, where ordered by the Engineer, shall be reinforced with four layers of BRC brickforce, or approved equal.  The latter reinforcement shall extend a minimum of 450 mm beyond any opening.  All joints in the six courses of brickwork above the opening shall be fully flushed with cement mortar.  Shoring to soffits of lintels shall be left in position for at least 14 days after building the lintel and the brickwork shall be kept damp with wet bags for the whole of this period.

PA4.7	Wall Vents

Ventilator openings shall be formed through walls where indicated and shall be provided with double brick terracotta louvred air bricks (fitted with plastic insect screens) both externally and internally (where scheduled) set flush into the work and neatly pointed.  Internal wall vents are to be of an approved plaster of paris type where scheduled.

PA4.8	Building in Frames, etc

Door and window frames are to be set up, built into position, bedded and pointed in cement mortar, with any necessary cutting to brickwork, fitting and making good, as the brickwork is built up.  In the case of doorframes, wrought iron right angled cramps are to be fixed to doorframes and built into brickwork at every eighth course.

Where pipes, frames, brackets or other such parts pass through or have to be set into brickwork, the bricks shall be carefully cut and fitted to maintain regularity of courses and uniformity of joints, the shaped bricks being embedded and pointed to conform with the surrounding brickwork.  Where such parts have to be set into position after brickwork is built, holes shall be left wherever possible, in preference to cutting out bricks, and the work shall be subsequently made good in the manner described.

PA4.9	Floor Finishes

PA4.9.1	Granolithic Floor Screed

Granolithic shall consist of one part cement, one part sand and two parts 5 mm stone chips and oxide where required, thoroughly mixed as for concrete and placed in a layer not less than 20 mm thick, levelled or graded and trowelled to a smooth uniform surface.  To ensure proper bond, the concrete surface to be covered shall be clean, roughened by chipping, flushed with water and coated with cement grout just before placing of the granolithic layer.  Granolithic finish is to be steel floated with V joints in squares of 1,20 m to 1,80 m, the joints extending for the full depth of the granolithic.  Joints are not required in the granolithic screed where it is to be overlaid by tiles or carpeting.

PA4.10	Chasing Walls

Where indicated by the electrical contractor, the construction contractor shall chase brickwork and concrete work to accommodate electrical conduit - such chasing shall precede plastering or rendering and on no account shall plastering or rendering be commenced until the electrical tubing has been installed.  No horizontal or diagonal chases shall be permitted.

Elsewhere, electrical conduit shall either be cast into concrete or shall be run on the surface afterwards as may be directed by the Engineer.

PA4.11	Weather

In any period of interruption caused by inclement weather, and at the completion of each day's bricklaying, freshly laid brickwork should be protected.

PARTICULAR SPECIFICATION: PD

DISINFECTION OF PIPELINES

PD 1	INTRODUCTION

The price for testing and disinfecting pipelines and fittings is included in the scheduled items for supply and installation.

On completion of construction, after pressure testing and prior to commissioning the pipeline is to be disinfected by the contractor in accordance with this specification.

PD 1.1	Scope of the Code of Practice

This Code of Practice relates to the disinfection of parts used for the disinfection of complete installations.

It includes the requirements for bacteriological sampling and dosage of disinfectants, dose rates of disinfectants, disposal of chlorinated water and quality standards for bacteriological samples.

PD 1.2	Definitions

Within this document the term HYPOCHLORITE SOLUTION means a commercial solution of sodium hypochlorite containing 10% to 15% of available chlorine.  Also, 10% HYPOCHLORITE SOLUTION means hypochlorite solution diluted one part in ten which thus has approximately 1% of available chlorine.

Within this document AVAILABLE CHLORINE and all chlorine concentrations means FREE CHLORINE available to the water environment for its disinfection.

'Water Supply Personnel' means any employee or contract or casual labour whose work includes, even temporarily, the performance of work concerned with partially or fully treated water and sources of underground water and who must possess a current certificate of medical suitability signed on behalf of the Authority.

PD 1.3	Hygiene

Only 'Water Supply Personnel' may undertake the procedures laid out in this Code of Practice.

PD 1.4	Safety

This Code of Practice does not cover the safety aspects of the construction or maintenance of installations or apparatus or of disinfection procedures.

Remember always that chlorinating agents are strongly corrosive so protect EYES AND HANDS especially.

PD 2	GENERAL REQUIREMENTS FOR DISINFECTION OF POTABLE WATER APPARATUS

PD 2.1	Components and Equipment

Clean all pipework components, equipment and tools used for repair and remove all grease or scale from components and equipment before use or assembly.

Where full chlorination and bacteriological testing is impractical, then disinfect all materials, components and equipment which could transmit contamination.  Use a solution containing 1% of available chlorine (e.g. 10% chloros or other commercial hypochlorite solution or 2% solution of bleaching powder.  Contact time must exceed 20 minutes.  Rinse or flush the equipment with mains water to prevent excessive corrosion.

PD 2.2	Completed Installations

Ensure that all water used for disinfection purposes has a free chlorine residual of at least 20 mg/ℓ.  Refer to section PD 4 and Tables 1 and 2 for volumes or dose rates.

During chlorination the pipeline shall be kept full of water.

Whenever possible keep the installation at normal operating pressure or greater during the contact period.

PD 2.3	Portable Test Equipment

Portable test equipment which may be used in contact with potable water must be kept clean.  Any equipment which is in uncertain condition or which is contaminated must be cleaned and disinfected before use.

PD 3	MAINS

PD 3.1	New Mains

PD 3.1.1	Introduction

Do not connect any new main into supply until the water from designated sampling points, having stood in the main for at least 20 hours, has met the criteria specified herein.

New mains are laid with the intention of ensuring as far as possible, the exclusion of debris and contamination, but presume at the disinfection stage that debris and contamination does exist and that this debris is resistant to disinfection, e.g. compacted soil or detritus in joints.

The disinfection procedures, which should follow pressure testing, include:

(a)	swabbing and flushing of the main

(b)	soaking of the main for a minimum period of 20 hours, using a minimum concentration of 20 mg/ of available chlorine in mains water.

- removal of excess chlorine by flushing the main

PD 3.1.2	Pressure Testing

Only use potable quality mains water for pressure testing new mains.  Pressure testing normally follows the construction of each section of the pipeline but precedes final connection to supply.  Do not rely on a single sluice valve to isolate the new main from the supply network, while the main is under pressure until disinfection and approval are complete.

PD 3.1.3	Swabbing and flushing

Swab all new mains after pressure testing and prior to disinfection.

After insertion of a soft foam swab, which has been soaked in 10% hypochlorite solution, recharge the pipeline at a rate less than 50 mm per second (3 m per minute) to ensure that the swab is not moved.

Open the inlet valve fully and drive the swab along the pipeline, at a velocity less than 0,5 m per second (30 m per minute), by controlling the valve at the discharge end.

When the swab reaches the discharge end of the pipeline, flush the main for at least 5 minutes to remove all excess chlorine and discoloured or dirty water.  Where possible open inlet and outlet valves as fully as possible.

If the swab removes excessive amounts of debris then re-swab the main.

PD 3.1.4	Chlorination

Chlorinate all new mains to a minimum of 20 mg/ available chlorine and leave to soak for a minimum of 20 hours, prior to flushing with mains water to a chlorine residual equal to that of the background level in the incoming mains water.

Tables in PD 4 show the required minimum dose rates and volumes.

To chlorinate sections of distribution main, less than about 50 m long not exceeding 150 mm in diameter, use a soft swab which has been soaked in 10% hypochlorite solution and proceed as follows: -

-	Pour 1 litre of hypochlorite solution for each 1 m³ of pipeline, into the end of the pipe upstream of the final connection.

-	Insert the swab into the end of the upstream pipe to retain the hypochlorite solution.

-	Make the final connection.

-	Drive the swab past the final connection and along the pipeline, but do not allow the swab to travel at a speed greater then 0,3 metres per second (20 m per minute).

-	Remove the swab and flush the main for 25 minutes.

-	Close up the main prior to soaking and sampling in accordance with section PB 3.1.6.

The volume of hypochlorite needed for 50 m of pipeline is: -

50 mm - 100 m,	 75 mm - 200 m,	100 mm - 500 m,

150 mm - 900 m, 	200 mm -1600 m, 	250 mm - 2500 m.

Take all necessary care with the disposal of chlorinated water; follow the procedure laid out in PB 5.

PD 3.1.5	Sampling for Bacteriological Analysis

Once all pressure testing, swabbing and chlorination is complete, fill the main with clean mains water free from excessive chlorine.

Flush all hydrants, washouts and other outlets until the water is clean and free from excessive chlorine.  Shut the valves and leave the main to soak for a minimum period of 20 hours.

First check with the laboratory staff of the Ugu District Municipality to determine a suitable time for collection of samples and delivery of them to the laboratory for analysis.

Then pressurise the main and take samples for bacteriological analysis in accordance with the procedure given in section PB 3.1.6.  Take these samples from sampling points agreed with the Resident Engineer.

Deliver all samples to the laboratory as soon as possible.  Analysis must start within six hours but store the samples in a refrigerator if the delay between taking the sample and the start of analysis is likely to exceed four hours.

Then isolate and leave the main until the results of analysis are available.  In the event that the samples fail, flush the main and re-sample after a further soak period of at least 20 hours.

Repeat the above process until disinfection criteria have been satisfied.

The costs of all necessary testing are to be borne by the Contractor.

PD 3.1.6	Sampling Points

Sample points should consist of a ferrule connection, with a short length of polythene piping terminating in a ½" BSP gate valve or manual air valve.  Protect this sampling outlet by suitable boxing.  Attach a sampling standpipe to the gate valve, disinfect the apparatus with hypochlorite solution and then flame the bib tap outlet on the standpipe.  Flush out all traces of hypochlorite, check that the residual chlorine level is not greater than the normal level in the incoming mains water.

At scour points and air valves, flush out all trace of hypochlorite, check that the residual chlorine level is not greater than the normal level in the incoming mains water, then take samples.

PD 3.1.7	Temporary Cross Connections and Final Connections

Where a temporary cross connection supplies mains water to the new main, before making the final connection complete the disinfection procedure of the new main as set out above.

When the new main has been proved bacteriologically satisfactory the cross connection may be removed and isolated after suitable disinfection.

PD 4	DOSAGE OF CHLORINATING AGENTS

PD 4.1	Sodium Hypochlorite Solution

Bulk supplies of sodium hypochlorite solution (Chloros for instance), are supplied at 10 to 15% available chlorine.  This fraction declines progressively as the hypochlorite decays to chloride, chlorate and oxygen.  Assume in practice that there is only 10% available chlorine.

Assuming 10% available chlorine, and using mains water having a zero chlorine demand, then the following values give estimates of the dilutions required.

-	10% hypochlorite solution (1 part hypochlorite solution in 10 parts solution) contains 10,000 mg available chlorine per litre of 10 kg available chlorine per cubic metre.

-	20 mg available chlorine per litre is equivalent to 200 ml of hypochlorite solution per cubic metre of water.

-	0,5 mg available chlorine per litre is equivalent to 5 ml of hypochlorite solution per cubic metre of water.

PD 4.2	Chlorine Gas

Chlorine gas, dosed into water by weight, is likely to be about 98% available chlorine.  Therefore a direct measurement gives a reasonable estimate.

-	Disinfection of replacement parts with chlorine gas in not a practicable possibility.

-	20 mg Chlorine gas (by weight) per litre for disinfection of complete installation is equivalent to 20 grams per cubic metre.

-	0,5 mg Chlorine gas (by weight) per litre of water is equivalent to 0,5 grams per cubic metre.

PD 4.3	Bleaching powder, granules and tablets

Bleaching powders, granules or tablets based on Calcium hypochlorite contains 50% to 70% of available chlorine by weight.  These materials must be stored under dry conditions.  During storage some available chlorine is lost.  Follow the manufacturers instructions particularly concerning the shelf life of the material and dose rate of the tablets.

For calculation purposes presume a maximum value of 50% available chlorine i.e. 1 gm of powder, granules etc in 1 litre of water provides 500 mg per litre available chlorine.

PD 4.4	Dose rates

Tables 1 and 2 provide estimates of the minimum dose rates of sodium hypochlorite solution, chlorine gas or bleaching powder, tablets or granules to achieve available chlorine levels of 20 mg per litre when dilute with mains water which has a zero chlorine demand.

Table 1 - dosage for 1,000 m of pipeline to give 20 mg available chlorine per litre

| Pipe Diameter | Volume of 1000 m of pipeline | Weight of bleaching powder granules or tablets to give 20 mg/ | Weight of chlorine to give 20 mg/ | Volume of hypochlorite solution to give 20 mg/ |
| --- | --- | --- | --- | --- |
| mm | m³ | gm | gm | litres |
| 50 75 100 150 200 250 300 350 400 500 600 | 1,9 4,4 7,9 17,7 31,4 49,1 70,7 96,2 125,6 196,3 282,6 | 80 180 320 700 1,260 2,000 2,800 3,800 5,000 7,800 11,200 | 40 90 160 350 630 980 1400 1900 2500 3900 5600 | 0,4 0,8 1,5 3,5 6,2 9,7 14,0 19,0 24,6 38,4 55,4 |

Table 2 - dose rates for 20 mg available chlorine per litre

| Flow rate in pipeline* |  | Hypochlorite solution injection rate for 20 mg/ |  | Chlorine injection rate for 20 mg/ |
| --- | --- | --- | --- | --- |
| litres/sec | m³/hr | litres/hr | m/sec | gm/hour |
| 1 2 3 4 5 6 7 8 9 | 3,6 7,2 10,8 14,4 18,0 21,6 25,2 28,8 32,4 | 0,7 1,4 2,2 2,9 3,6 4,3 5,0 5,8 6,5 | 0,2 0,4 0,6 0,8 1,0 1,2 1,4 1,6 1,8 | 72 144 216 288 360 430 500 576 650 |

* For flows greater than 9 litres/sec the dose rates can be calculated by multiplying by an appropriate factor of 10 e.g.

186 litres/sec = 100 +n 80+ 6 litres/sec

hypochlorite solution = 70+ 58 + 4.3 = 132,3 litres/hr

PD 5	DISPOSAL OF CHLORINATED WATER

PD 5.1	Introduction

When the pipeline has passed all disinfection criteria if must be drained without causing hazard.

PD 5.2	Methods of Disposal

PD 5.2.1	Overland

Explore the possibility of soaking away disinfection water on adjacent land in rural situation.

PD 5.2.2	Foul sewers

Where disinfection water is discharged into a combined or foul sewer, no de-chlorination is normally necessary but in the former case take care that the rate of discharge of disinfection or flushing water avoids operation of storm sewage overflows and/or the creation of a hazardous atmosphere within the sewer.

PD 5.2.3	Watercourses

In rural areas where disinfection water is discharged to watercourses, either directly or through surface water drains, do not permit a free chlorine concentration in the receiving stream in excess of 0,1 mg/l about 50 metres downstream of the point of discharge.  If the discharge is into a ditch, which is not a spawning ground or a nursery or a fishing stream, take advantage of that ditch to mop up chlorine provided that in a significant stream the earlier mentioned limit is not exceeded.  In these circumstances use flush water to dilute the chlorinated water whenever possible.  Avoid discharge of disinfection water to the head of a watercourse because this area is probably a spawning ground.

PD 5.2.4	Disposal of large volumes

When disposing of large volumes of disinfection water from very long lengths of new main, or in any cases of doubt, consult through the Resident Engineer, the laboratory staff of the Employer.

PD 5.3	De-chlorination

There is no objection to the use of thiosulphate or sulphur dioxide as de-chlorination agents.  In some cases, at least partial de-chlorination may be achieved by discharge over land.  In all cases consult the Resident Engineer.

PD 6	QUALITY STANDARDS AND REPORTING PROCEDURES

PD 6.1	New Mains

PD 6.1.1	Bacteriological Standards

No coliform organisms shall be detected in 100 ms of the sample.

The increase in the yeast agar plate count when compared with that of the incoming water shall generally be less than 50 and never more than 150 colonies per ml when incubated at 37C for 24 hours.

PD 6.1.2	Procedure for Unsatisfactory Samples

Whenever even one E.Coli, or 5 or more coliforms per 100 ml are detected, re-chlorinate the main or serve reservoir.  When E.Coli are not detected but the total coliform count is less than 5 per 100 ml flush and re-sample the main.

PD 6.1.3	Physical Standard

If the sample is unusually coloured, turbid or frothy flush the main until acceptable.  If this condition is severe, re-sample the main but do not put into service until the samples have passed the required standards.

PD 6.2	Reporting Procedure

Records of disinfection are to be handed to the Resident Engineer.

PARTICULAR SPECIFICATION: PSP – STEEL PIPES

1.	SCOPE

This specification covers the design, manufacture and supply of bare, electric welded low carbon steel pipes, specials and other fittings for the conveyance of water at ambient temperatures and at medium pressures.

2.	INTERPRETATIONS

2.1	Supporting specifications

2.1.1	Where this specification is required for a project, the following specifications

shall form part of the contract document:

(a)  Project specifications;

(b)  SABS 1200A and SABS 1200AA, as applicable;

2.1.2	Reference is made to the latest issues of the following standards:

DWS	1131	Lining and coating of steel pipes and specials.

SABS	1200	As given in 2.1.

SABS	62	Steel pipes and pipe fittings up to 150 mm nominal bore, suitable for

screwing to

SABS 1109 	pipe threads.

SABS	719	Electric welded low carbon steel pipes for aqueous fluids (ordinary

duties).

SABS	974	Rubber joint rings (non-cellular).

SABS	1431	Weldable structural steels.

SABS	044	Welding.

SABS	0121	Cathodic protection of buried and submerged structures.

BS	534	Steel pipes and specials for water and sewage.

BS	2633	Class 1 arc welding of ferritic steel pipework for carrying fluids.

BS	2815	Compressed asbestos fibre jointing.

BS	4360	Weldable structural steels.

BS	4416	Method for penetration testing of welded or brazed joints in metals.

BS	4504	Flanges and bolting for pipes, valves and fittings.  etric series.

BS	5500	Specification for unfired fusion welded pressure vessels.

SIS	05 59 00	Pictorial surface preparation standards for painting steel surfaces

(Swedish)

API	5L	Line pipe.

API	1104	Standard for welding pipelines and related facilities.

AWWA	June 1955	Design of wye branches for steel pipe.

AWWA	M11	Steel pipe - a guide for design and installation.  (Second edition)

ISO	2084	Pipeline flanges for general use

2.2	Application

This specification contains clauses that are generally applicable to the design, manufacture and supply of steel pipes, specials and fittings for duties up to 4,6 MPa.  Should no other specification for pipes of outside diameter larger than 2 220 mm be included in a contract, then the requirements of this document shall apply.

2.3	Definitions

For the purposes of this specification the definitions and abbreviations given in the applicable specifications listed in 2.1 and the following definitions shall apply:

Skelp:    The jointing edges of steel coils used to manufacture spiral welded pipes.

H:   The cross-sectional shape of a weld at skelp

Cut and shut bend:  See definition with sketches in BS 2633

3.	MATERIALS

3.1	Pipes and specials

Materials used for the manufacture of pipes and specials of nominal bore up to 150 mm shall conform to SABS 62 and API 5L:  steel grades up to X52, whilst that for pipes and specials of nominal bore over 150 mm shall conform to SABS 719:  steel grades A, B and C, as well as API 5L:  steel grades X46, X52, X56 and X60.

Flanges shall be manufactured from steel plates conforming to BS4360, or SABS 1431 grade 300W.  Specials and fittings shall be manufactured from materials conforming to SABS 62 for nominal bores up to 150 mm, and to BS 534 for nominal bores over 150 mm.

3.2	Rubber joint rings

Rubber rings shall comply with SABS 974 Class F.

3.3	Jointing materials

Bolts, studs, nuts and washers for flanges shall be of materials conforming to the requirements of BS4504 unless otherwise specified.  Gaskets for flanged joints shall be of compressed asbestos fibre to BS 2815 grade A, and full faced with a minimum thickness of 3 mm.  For pressures up to and including 1,6 MPa, cloth-inserted rubber may be used.

4.	PLANT

The Contractor shall supply and maintain suitable tools, plant and equipment to manufacture and supply steel pipes, specials and fittings to the required standard.

5.	GENERAL REQUIREMENTS

5.1	Design of pipes

The design stress for pipes subjected to the specified design pressures shall be 60% of the minimum yield stress of the steel.

Unless otherwise specified in the Schedule of Quantities or on the drawings, the minimum pipe wall thickness to prevent buckling of straight piping due to internal sub-atmospheric pressures, shall not be less than the following:

| Outside diameter (mm) | Minimum wall thickness (mm) |
| --- | --- |
| 160 to 558,8 | 4.5 |
| 609,6 to 660,4 | 5 |
| 711,2 to 812,8 | 6 |
| 863,7 to 1092 | 8 |
| 1118 to 1245 | 10 |
| 1397 to 1620 | 12 |
| 1708 to 1860 | 14 |
| 2020 to 2220 | 16 |

5.2	Dimensional requirements

Unless otherwise specified in the Schedule of Quantities or on the drawings, all line pipes shall be of one fixed standard length between 9 metres and 19,5 metres.  Standard pipes from which samples for destructive testing have been cut may be jointed together by butt-welding to form single pipe lengths of the required standard length.

The tolerances on all other dimensions shall be in accordance with SABS 719 clause 4.1, except that for pipe outside diameters bigger than 1 250 mm it shall be +6 mm and -6 mm.  The tolerances on the outside diameters of pipe ends and bodies shall be as specified for pipe diameters of 250 mm to 1 250 mm.

5.3	Fabrication

5.3.1	Welding

Welds shall comply with SABS 719, SABS 044 and BS 2633 as modified below.

a.	Sections 1, 2 are excluded.

b.	Section 8

In addition to clause 8.1 the following shall also apply:

All butt-welds and branch fillet welds on specials shall where considered possible (refer clause 3.2.4.2, Section 3) have an internal weld.  The weld bead of this internal weld shall not extend above the prolongation of the original inside surface of the pipe by more than 1,0 mm.  Internal reinforcement in the form of backing rings at weld seams shall not be permitted.

c.	Section 10

Procedure qualification and qualifying tests shall be restricted to branch connections only.

The internal weld bead/upset metal and flash on the inner surface shall not exceed 1 mm. For pipes and specials to be jointed by butt welding, the internal weld bead shall not protrude more than 1 mm into the bore of the pipe or special.  For electric resistance welded pipes, the height of upset metal and flash on the inner surface shall not exceed 1 mm.  For pipes and specials to be jointed by butt welding, the internal weld bead shall be ground flush with the pipe body for a length of 200 mm from the ends to be jointed.  For pipes and specials to be coupled by flexible couplings, external weld reinforcement or upset metal and flash shall be ground flush with the pipe body for a length of 200 mm from the end to be coupled.

Where automatic submerged-are welding is employed, at least one pass shall be made on the inside and at least one pass on the outside.  This shall apply for double jointing of pipes in the factory as well.  The number of longitudinal weld seams shall not exceed:

(a)  1 for pipes up to 1 000 mm nominal diameter;

(b)  2 for pipes larger than 1 000 mm and up to 2 220 mm nominal diameter.

For pipes to be jointed by flexible couplings the pipe manufacture is required to weld steel plates not less than 50 mm x 75 mm x 6 mm thick to each end of all pipes during the pipe manufacturing process, (i.e. before priming, lining and coating).

All manual or semi-automatic welds and repair welds shall only be undertaken by welders qualified under the tests laid down in the Code of Practice for Welding SABS 044.

5.3.2	Pipes

Pipes shall be manufactured in conformity with SABS 719.

5.3.3	Specials and fittings

5.3.3.1 General

All specials and fittings shall be designed and manufactured by the Contractor in accordance with the general arrangement shown on the drawings and/or described in the Schedule of Quantities, in conformity with SABS 62 or sections 3 and 4 of BS534.  In the latter case specials shall be manipulated or fabricated by welding from pipes which have been tested to SABS	719.  Detailed drawings shall be approved by the Engineer.

5.3.3.2	Bends

Bends shall either be smooth formed or segmented.  The maximum angle between oblique butt-ends of segments for gussetted bends shall not exceed 22£ degrees.  Cut-and-shut bends shall not be permitted.  Segmented bends shall be classified as short, medium and long with radii equal to one, two or three diameters respectively.  All bends shall however be of a long radii type, unless otherwise specified in the Schedule of Quantities or on the drawings.

5.3.3.3	Branch connections

Branch connections shall have barrel and branch plate thicknesses such that the maximum stress shall not be greater than that for an uncut pipe of the theoretically required minimum thickness.  However, where it is more economical to provide external reinforcement in the form of saddle-type rings or triform shoes, these forms of reinforcement shall be used to achieve the same results.  The attachment of reinforcement to the pipe branches shall be by full penetration welding.  Branch connections shall be as remote as possible from the seam weld on the barrel, and except where specifically indicated to the contrary on the drawings, the positioning and extent of external reinforcement is to be determined by the following methods:

(i)	Saddle-type reinforcement:  section 13.3 of AWWA Manual M11.

(ii)	Triform-shoe reinforcement: in accordance with "Design of Wye Branches for Steel Pipe" by H.S. Swanson and co-authors, published in the Journal of the AWWA, June 1955.

Scour valve tees are to be at right angles to the barrel of the pipe, but tangential to the circumference at the invert of the pipe.  The flanges are to be aligned to suit the gradient of the pipeline as indicated on the drawings.

Unless otherwise specified complete flanged air valve and access branches shall be supplied loose with the one end profiled and prepared for welding to the pipe or special.  Branches are to be prealigned to suit the pipeline gradient as indicated on the drawings.

5.3.3.4	Reducers

Taper pieces shall not have more than two longitudinal weld seams.

5.3.3.5	Flexible couplings

Flexible couplings shall be of the Viking-Johnson type with centre register, except where specified to the contrary in the Schedule of Quantities or on the drawings.  Flexible couplings shall be supplied complete with all necessary bolts, nuts and rubber jointing rings.

5.3.3.6	Insulated joints

Insulated joints shall have their insulation material arranged as given in 	SABS 0121, unless otherwise specified.

5.3.3.7	Flanges

Flanges shall be of the steel-plate for welding type and shall have flat joint faces, with dimensions and joint surfaces in accordance with BS 4504 or ISO 2084, unless otherwise specified in the Schedule of Quantities or on the drawings.  For flange thickness not covered in BS 4504 and for domed and conical ends the various thicknesses and methods shall be calculated in accordance with section 3 and where applicable manufactured in accordance with the remainder of BS 5500.  Back surfaces may be left unmachined.  All flanges shall be suitable for field welding to pipes and specials and shall conform to BS 2633, section 7, with preparation of plate flanges as shown in figure 41 ("slip-on") for pipes and specials up to 100 mm N.B. and figure 39 or 40 ("bore and fillet") for pipes and specials 125 mm N.B. and larger.  Unless otherwise specified, jointing material i.e. bolts, nuts and washers, in conformity with BS4504 shall be supplied by others.

6.	MARKING OF PIPES AND SPECIALS

All pipes and specials shall be clearly hard stamped alongside a longitudinal or spiral weld on one end of the pipe with the following:

(a)  grade and thickness of steel;

(b)  serial number of the pipe or specials;

(c)  nominal diameter;

(d)  hydraulic test pressure.

The applicable drilling table shall be stamped on the periphery of all flanges.  Bends shall have their centre plane marked with two small punch marks close to both ends to facilitate correct positioning in laying.

7.	STORAGE, HANDLING AND TRANSPORT

Pipes and specials shall be protected against damage at all stages from manufacture to delivery.  The ends of all pipes and specials shall be protected against denting.  Pipes shall be transported and stacked in a manner such as to prevent deformation of the pipe body in excess of 2 percent of the diameter.  Dents causing a protrusion in excess of 3 mm into the interior of the pipe shall be repaired by cutting out.  The Contractor shall be responsible for dispatching and transporting of the pipes to site and off-loading.   Suitable access along the pipeline route will be provided unless otherwise specified.

Access for delivery on site might be restricted by poor weather conditions and the Contractor shall make due allowance for such disruption.  Unless otherwise specified the pipes shall be off-loaded adjacent to the laying position, and placed on sandbags or other approved protective supports.

As indicated on the drawings, the Contractor shall stack the pipes, specials and fittings at the top or bottom of very steep inclines from where the pipeline construction Contractor will transport them to their destination as required.  He will furthermore provide in the rates for his delivery trucks to be hauled/towed up the steep inclines along the pipeline route where necessary.

8.	INSPECTION AND METHODS OF TEST

8.1	General

Factory inspection, supervision of tests, and adjudication of test records shall be carried out by an independent Inspectorate appointed by the Employer to act on behalf of the Engineer.  Tests and inspections shall be carried out at the manufacturer's works at his expense.  He shall provide all necessary testing facilities, labour, instruments, equipment and samples that might be required, free of charge.  The Inspectorate shall be afforded every facility during the course of manufacture and testing to enable the inspection to be carried out effectively.  All test samples shall be selected by the appointed inspectors, and all instruments used for testing purposes shall be approved by the inspectors and if in their opinion any instrument should require calibration, such instruments shall be calibrated at the expense of the Contractor, by the SABS or other such body as may be approved by the Inspectorate.  No mechanical working or straining of pipes and specials shall be allowed after testing and inspection.

8.2	Non-destructive inspection

8.2.1	Visual inspection

All finished pipes and specials shall be visually examined and shall be free of injurious defects as defined in API 5L section 10.7.  In addition, welds on specials shall be inspected by the application of a penetrant-dye on the inside of the welds.  No trace of the dye should appear on the outside.

8.2.2	Ultrasonic inspection to API 5L

Pipes shall be made by an approved welding process and 100 percent of all longitudinal or spiral welds on straight pipes shall be checked with an approved ultrasonic method capable of continuous and uninterrupted inspection of the weld seam in accordance with API 5L, sections 9.14, 9.15, 9.16, and 9.17, except that the equipment shall be checked with an applicable reference standard at least twice every working turn.

8.2.3	Radiographic inspection to API 1104

(a)	Longitudinal welds:  All electric fusion welded pipes shall be inspected by radiological methods for a distance of 200 mm from each pipe end.

(b)	Spiral welds: All electric fusion welded pipes shall be inspected by adiological methods for a distance of 100 mm from each end of each length of pipe and of the complete "H" at all skelp and welds, including 150 mm of the spiral welds in both directions away from the intersection points of the skelp and welds.

(c)	Circumferential butt welds and welds on specials: 100 percent of the weld length shall be examined.  When consistently acceptable results are obtained, the number of welds to be so tested may be reduced by mutual agreement between the Engineer, Inspectorate and Contractor.

(d)	Repairs

(i)	Straight piping - 100 percent of the total length of all repairs shall be examined radiographically.  Where repairs are made before ultrasonic inspection, and such repairs pass ultrasonic inspection, no further radiographic inspection of same is required.

(ii)	Specials - 100 percent of all repairs shall be examined radiographically.

(e)	Pipes for rail, road and river crossings:  100 percent of the total length of all welds shall be examined radiographically.

8.2.4	Hydrostatic testing

All pipes shall be hydrostatically tested to a pressure such as to produce a circumferential tensile stress in the steel not less than 90 percent of the minimum yield stress of the steel, or 9 MPa, whichever is the lesser.  Each individual straight pipe shall be subjected to a hydrostatic test in accordance with the methods described in API 5L section 5.  Leaks or sweats shall be considered injurious defects.  Should it not be possible to hydrostatically test straight piping and/or specials, a liquid penetrant test shall be done on all welds over and above the non-destructive tests specified above.  This will only be applicable with the prior written approval of the Engineer.

8.2.5	Liquid penetrant testing

Where requested by the Inspectorate, liquid penetrant testing shall be done in accordance with BS 4416.

8.2.6	Magnetic particle testing

Where requested by the Inspectorate, magnetic particle testing shall be done in accordance with ASME Boiler and Pressure Vessel Code, Section V, Article 7.

8.3	Repair of injurious defects

Injurious defects found by non-destructive testing of welds, visual examination, hydrostatic testing or determined by any other means to exceed the limitations in API 5L section 10.7 shall be repaired in accordance with API 5L sections 10.8 and 10.9, but subject always to the requirements of this specification.

8.4	Destructive testing

8.4.1	Tests

Destructive tests shall be performed in accordance with SABS 719 clause 7.2 on the first pipe and thereafter on one of every 500 subsequent pipes.

8.4.2	Sampling and compliance with the specification. This shall be performed in accordance with SABS 719 clause 6.

9.	MEASUREMENT AND PAYMENT

Measurement and payment shall be per linear metre of straight pipe fabricated, supplied and delivered to site.  Measurement and payment of specials and fittings shall be per the number of each special and fitting fabricated, supplied and delivered to site.  Where pipe linings and coatings are applied prior to delivery, the rates for pipes, specials and fittings shall include for all such linings and coatings as required under Departmental Specification DWS 1131, unless otherwise specified in the Schedule of Quantities.

PARTICULAR SPECIFICATION: PE

THE CLIENT’S PRE-CONSTRUCTION AND HEALTH PLAN

### PE1		INTRODUCTION

PE1.1	Purpose and Scope

This document describes the procedure upon which the COMPANY shall comply with the requirements set out in the client’s Health and Safety Specification.

This document defines the Management System that is implemented by the COMPANY for the management of Health and Safety on the project, which includes ensuring subcontractor compliance with the same standards.

The aim of this document is to present the safety aspects that will be controlled and managed on the project.

PE1.2 		Reference Documents

- Occupational Health and Safety Act, (Act No. 85 of 1993)

- Compensation for Occupational Injury and Diseases Act.

- Client Health and Safety Specification.

- Construction Regulations 2003.

- The Construction Kit. (CD)

### PE1.3 		Definitions

The following definitions will apply to the Safety Management Plan, acronyms given hereunder shall apply:

Construction / Building Work (as defined by the Occupational Health and Safety Act: Construction Regulations 2003):

Means any work in connection with –

- The erection, maintenance, alteration, renovation, repair, demolition or dismantling of or an addition to a building or any similar structure;

- The installation, erection, dismantling or maintenance of a fixed plant where such work includes the risk of a person falling;

- The construction, maintenance, demolition or dismantling of any bridge, dam, canal, road, railway, runway, sewer or water reticulation system or any similar civil engineering structure; or

- The moving of earth, clearing of land or making of an excavation or work on any similar type of work.

Hazard Identification and Risk Assessment and Risk Control (HRA):

Means a documented plan, which identifies hazards, assesses the risks and detailing the control measures and safe working procedures, which are to be used to mitigate and control the occurrence of hazards and risks during construction or operation phases.

Site

Means the area in the possession of the Contractor for the construction of the works. Where there is no demarcated boundary it will include all adjacent areas, which are reasonably required for the activities for the Contractor, and approved for such use by the Engineer and/or client.

The Act

Means, unless the context indicates otherwise, the Occupational Health and Safety Act, 1993 (ACT NO. 85 of 1993) and Regulations promulgated there under. (OHSA)

Hazard

Means a source of or exposure to danger (source which may cause injury or damage to persons, or property)

Risk

Means the probability or likelihood that a hazard can result in injury or damage.

Contractor’s Responsible Person / s

Means any person appointed in writing by the Contractor to supervise construction or building work. The appointment shall be as required by the OHSA which shall stipulate health and safety responsibilities, area of responsibility and the proposed duration of the project.

Hazardous Chemical Substance (HCS)

Means any toxic, harmful, corrosive, irritant or asphyxiant substance, or a mixture or substances for which an occupational exposure limit is prescribed, or an occupational exposure limit is not prescribed, but which creates a hazard to health.

Construction Plant (TEM)

Encompasses all types of plant including but not limiting to, cranes, piling frames, boring machines, excavators, dewatering equipment and road vehicles with or without lifting equipment.

Contractor

Means “subcontractor”.

Health and Safety Programme

Encompasses the COMPANY safety planning spreadsheet.

Health and Safety Plan (HSP)

The content of this document which will be made available on site for inspection by an inspector, Technical Officer, Agent, subcontractor, employee, registered employee organisation, health and safety representative, or member of the health and safety committee.

Health and Safety File

Describes the safety file holding all records on health and safety for the project, which shall be available at all, times for evaluation, and copy of which will be forwarded to the client upon completion of the project.

### PE1.4 		Responsibilities

#### Notification of Intention to Commence Construction Work

The Provincial Director of the Department of Labour shall be notified by the appointed safety consultant to the COMPANY, immediately upon receipt of the Letter of Acceptance of project commencement in accordance with the following requirements:

The demolition of a structure exceeding a height of 3 meters; or

The use of explosives to perform construction work; or

The dismantling of fixed plant at a height greater than 3 meters; or

The work exceeds 30 days or will involve more than 300 person days of construction 
work; and

Includes excavation work deeper than 1 meter; or

Includes working at a height greater than 3 meters above ground or a landing.

A copy of the notification letter to the Provincial Director shall be forwarded to client for their records and shall be made available to an Inspector, Project Engineer or employee.

#### Assignment of Contractor’s Responsible Persons to Supervise Health and 
 	Safety on Site

The Contracts Manager and Site Agent shall ensure copies of all the appointment letters of the responsible persons appointed on site will be made available to the client and that all legal appointments shall be conducted in accordance with the requirements set out in the OHSA and Client specifications. 

 The above shall also be imposed upon all subcontractors.

#### Safety Officer Appointment

A part--time Health and Safety consultant shall be appointed upon commencement of the project.

The safety officers shall be tasked with monthly inspections of the site, the results of which shall be forwarded to the client or his appointed representative.

#### Risk Assessment Competent Person

The Project Manager shall appoint a competent person in writing at commencement of the project to control the risk assessment process on site. A copy of the risk assessment appointment is attached with duties and responsibilities defined. 
(Annexure E)

#### Competency for Contractor’s Responsible Persons

The Project Manager acknowledges that all management personnel (responsible for health and safety) shall undergo a half-day Health and Safety Management Course, which is to be arranged and conducted by the appointed safety consultant prior to commencement of activities on site.

#### Health and Safety Representatives

At least one (1) Health and Safety Representative shall be nominated, elected and trained to carry out his / her functions in his / her area of responsibility. This will include areas where less than fifty (50) employees are engaged in activity. Employees elected shall be designated in writing for a specific area and period of time.

The designated persons shall conduct monthly inspections within their area of responsibility, the records shall be kept for auditing and that deviations recorded are reported to the responsible supervisor within the designated persons area so that appropriate action can be taken.

The designated person/s shall be permitted to participate in the Health and Safety Committee Meetings.

### PE1.5		Objectives and targets

Compliance with the COMPANY Health and Safety Policy.

Everyone is responsible for organising accident prevention at his or her own level on site.

Safety training is important.

Prevention.

Working safely ensures your job.

The COMPANY management commits itself to the objectives and targets.

Disabling Injury Frequency Rate (DIFR) of 2.0 or less.

90% compliance on monthly Health and Safety Audits.

Compliance with the legal requirements set out in the Occupational Health and Safety Act, Act 85 of 1993, (OHSA) and Regulations.

Compliance with the Client’s Safety Specification for Construction.

### PE1.6 		Planning and Procedure

The procedures to be used for the project are to be in accordance with the Safety Manual in use in the COMPANY under the guidance of the appointed safety consultant.

The sub-headings covered under the Safety Manual are as follows:

Administration

Appointments

Safety Committees

Registers, checklists and permits

Incident Management

Emergency Planning

Contractors

Risk Assessments

Audits

Hazardous substance control

Training

Mining Requirements

Roads Requirements

Planning

### PE1.6 		Implementation of the Occupational Health and Safety Specification

The COMPANY is committed to implementing client specific safety specification on the project and is committed see that this forms an integral part of the project. It is our intention to make this specification part of other Contractors and Suppliers operating procedures.

### PE1.7 		Application of the Health and Safety Specification

#### Compensation of Occupational Injuries and Diseases Act, Act No. 130 of 1993 (COIDA)

The letter of good standing will be available on site for reference purposes as proof of good standing.

The COMPANY shall ensure all Contractors also comply with the above requirements defined in the COIDA.

#### Occupational Health and Safety Policy

The COMPANY Health and Safety Policy is attached for reference purposes. (Annexure A)

#### Hazard Identification Risk Assessment

The Contract Manager shall ensure the Site Agent shall prior to the commencement of any construction work perform Hazard Identification, and the assessed risks shall form part of the health and safety plan applied on site.

A copy of the HRA shall be made available for viewing to the client.

The Site Agent shall ensure that all HRA’s conducted will be conveyed to all personnel and contractors through the site training programme and that these training sessions will be presented by the competent person regarding the hazard and related work procedures before any work commences.

The HRA Team that will be established will comprise members as follows:

Health and Safety Representative(s),

Health and Safety Committee Member(s)

Management Representative / Site Agent

Attached in the form of Annexure C and D, the Hazardous Task Identification and (HTI) and format of the Risk Assessment (RA) is included.

Method statements form part of the Risk Process and will conducted in accordance with the Risk Process described above.

Based on the activities carried out on all projects Hazard Investigation and Risk Assessments (HRA’s) will be done. Examples of which are:

Site Establishment

Demolition works

Excavation

Concrete works

Lifting operations

Hand held tools

Motorised Equipment

#### Health and Safety Committee

The Project shall convene a health and safety committee meeting monthly. All members required to be in attendance shall be notified of such meeting by means of a formal agenda.

The Site Agent shall ensure an attendance register and minutes are kept for auditing purposes, and that a copy of the minutes be circulated to all members in attendance well before convening the next meeting and within 7 days, a copy of the minutes will be forwarded to the project engineer.

Members of the committee shall include the following and are not limited to:

Safety Consultant. (When available)

Contractor’s site representative. (Supervisory level)

Contractor’s site representatives. (Operating level)

Project Engineer nominated representative. (Co-opted status)

#### Health and Safety Training

Training of personnel is a legal requirement and a necessity and is acknowledges as such. The Training Planning Matrix shall be provided upon request.

Induction Training

Induction training shall be attended with the Client as well as the The COMPANY Induction programme requirements and records of attendance kept to prove the same.

The COMPANY Induction format is attached for reference purposes. (Annexure E)

Awareness Training

Weekly awareness training shall be conducted using the The COMPANY Toolbox Talk documents, which shall be conducted by the site supervisors. (Annexure F)

Competency

Training identified through the Risk Assessment Process and conducted through this process shall be kept on file as proof of competency and training. (This may include operators)

First Aid and Health & Safety Representative Training

All safety representatives elected and designated, including first aiders, shall be trained should they not already be in possession of a valid certificate of training proving competence.

General Record Keeping

The Site Agent shall ensure that all the Health and Safety records, required by both the Occupational Health and Safety Act, 85 of 1993 and Regulations are kept for reference purposes and auditing.

Further to the requirements set out above, the Site Agent will also maintain records that may be defined through the risk assessment process, for auditing purposes.

In accordance with the requirements set out in the Construction Regulations 2003 and the requirement set out in Client Specification the Site Agent shall ensure that a copy of all Health and Safety records generated during the course of construction, be handed over to the Project Engineer upon completion of construction.

Statistics

The Site Agent shall ensure injury and incident records (Near Hits, First Aid, Medical cases, Disabling Lost Time Incidents), training etc. referred to above are kept on site.  All documents shall be made available to the client for inspection including the Department of Labour’s Inspectors as required by the Occupational Health and Safety Act, 85 of 1993.

The statistics formula as listed below shall be adhered to.

DIFR (Disabling Injury Frequency Rate)     DI’s x 1 000 000

Man-hours

DISR (Disabling Injury Severity Rate)        Days Lost x 1 000

Manhours

General Inspection, Monitoring and Reporting

The COMPANY shall comply with the requirements set out by the client. We have attached a safety management plan upon which the dates of inspections and training and awareness will be entered, conducted and monitored.

The COMPANY shall keep all records of inspections and investigations undertaken during the contract for the specified legal period as defined in the OHSA and Regulations.

Internal Audits

Internal audits shall be conducted a minimum once per month by the project engineer, as well as the appointed safety consultant.

The Results shall be tabled and discussed at the Health and Safety Committee meetings.

The Audits to be conducted by the appointed safety consultant shall be conducted on the audit schedule attached as per Annexure G.

Records of the audits shall be forwarded to the Project Engineer and shall be filed on site for reference purposes.

#### Incentives

No incentive scheme is being identified unless required by the client.

#### Penalties

Non-compliance with the client safety specifications can result in work stoppages and possible expulsion from site until the problem has been remedied including costs.

#### Emergency Procedures

The Site Agent shall make available to the Project Engineer a detailed Emergency Plan to tie into the evacuation plan already in place on the client’s premises.

First Aid Box and Contents

The Site Agent shall ensure that all working areas area adequately provided with first aid attendants whether there are fifty (50) employees or less engaged on the contract. The First Aid attendant shall be trained in accordance with the requirements set out in the OHSA with recognised and accredited service providers as defined above.

Proof of training attended (certificate) shall be attached to the written acceptance of appointment. It will be the first aid attendant’s responsibility to ensure the contents of the first aid boxes are monitored and inspections recorded on the contents of the first aid box register.

The first aid box shall be adequately stocked by The COMPANY at all times and will be accessible to all.

Accident and Incident Reporting and Investigation

Should accident investigation need to be conducted, the Project Manager shall appoint a competent person in writing to conduct the said investigation. The procedure to be followed will be in accordance with the OHSA requirement on the Annexure 1 – Recording and Investigation of Incident form.

The Site Agent shall ensure that the results of all investigations are communicated to the employees engaged through incident recall and prescribed meetings. The Site Agent shall ensure that the investigations are kept for record purposes in accordance with the prescribed requirements set out in the OHSA and the company specific procedures.

Should there be an incident, the Project Engineer shall be notified within 48-hours if required by the client, of the occurrence. It is acknowledged that the client reserves the right to participate in all investigations into accidents or incidents.

Hazards and Potentially Hazardous Situations

The Site Agent shall ensure that all other contractors or contractors are warned of hazardous or potentially hazardous situations, which may prevent them from effectively performing their duties, which includes the placement of adequate warning signs.

#### Personal Protective Equipment and Clothing

The COMPANY shall comply with OHSA requirements to provide PPE. 

The Site Agent shall through the Risk Assessment process identify the specific PPE needs per activity and then issue the PPE accordingly. (Reference to the OHSA General Safety Regulation 2 – Employer to provide Personal Protective Equipment) 

Should PPE be lost or stolen, then the employee will be issued with a new set of PPE.

Should PPE be worn out or damaged, the user shall return the worn or damaged PPE and will be issued with a replacement set. Training in the use of this shall be provided.

Overalls and hardhats shall be identifiable. (Principal Contractor different from the contractors)

PPE shall be provided to visitors as well.

#### Safety Signage

The Site Agent in conjunction with the appointed safety consultant shall assess the Health and Safety Signage requirement in conjunction with the Risk Assessments conducted and will place the signage at strategic positions on the site works.

The COMPANY shall also maintain the signage to ensure its effectiveness at all times and under all conditions. Signage, which cannot be repaired, shall be replaced.

#### Permits

The COMPANY shall ensure that access to site works is restricted to construction personnel.

All attempts will be made to restrict spectator access.

Access to the site shall be by the Project Engineers (Clients) authorisation on the prescribed form. (Permits and ID cards shall be issued by the client)

Special permits for hot work and isolation permits shall be applied for to the Project Engineer prior to commencing with the activity.

#### Contractors and Suppliers

The Site Agent shall enter into an Agreement with Mandatary in terms of Section 37(2) of the Occupational Health and Safety Act, 85 of 1993, with all contractors appointed by The COMPANY is entered into.

The Contracts Manager will ensure the contractors are issued with the Client Safety Specification where reasonably practicable including any the COMPANY contractor pack for the project, should they not be contained in the Client Safety Specification.

The COMPANY shall assist and ensure the contractors engaged comply with all of these requirements and adhere to the requirements set out in the OHSA. Contractors will be stopped from working in the event of unsafe conditions and activities being observed.

All contractors shall be covered by the COMPANY Safety Plan and will be issued the same.

#### Health and Safety in Practice

Excavations

The Site Agent shall ensure that all activities involving excavations, shoring, dewatering or drainage, a safe working procedure is submitted to the project engineer for approval prior to work commencing. Excavation work exceeding the specified depth as stipulated in the OHSA regulations, shall comply with the following requirements:

- The excavations are inspected before the shift starts, after heavy rain (inclement weather) and after any major condition which may affect the excavations stability and the findings are to be recorded and kept;

- All excavations regardless of the depth shall be adequately barricaded to prevent persons falling into the excavation;

- The safe working procedure shall be communicated to all employees who may be effected by the work; and

- The safe working procedures shall be enforced and maintained by the appointed excavation supervisor at all times.

- For high-risk activities, all personnel working in the excavation shall be attached by means of a lifeline.

- Material excavated shall be removed from the point of excavation.

- Ensure stability of adjoining structures.

Demolition

No demolition work is being envisaged on this project.

Explosives and Blasting

No blasting activities are envisaged on this project.

Stacking of Materials and Housekeeping

The Site Agent shall ensure that all stacking will be supervised by a person competent to supervise over the activities, and that clearly defined and allocated storage areas are provided for and identified, and that materials being stored within this area are stacked in accordance with sound stacking principles of sort-by-sort, access to be maintained, level surface, and the height will not exceed three times the base width.

Housekeeping shall be maintained in accordance with the client requirements at all times.

#### Hazardous Chemical Substances

The Site Agent shall ensure the necessary training and information regarding the use and storage of HCS is provided, and that the use and storage of HCS is carried out as prescribed by the HCS Regulations.

Furthermore, the Site Agent shall ensure that all chemicals brought to site have a Material Safety Data Sheet (MSDS) and the users are made aware of the Occupational hazards and precautions that need to be taken when using the chemical.

The First Aider shall be made aware of the MSDS and how to treat HCS incidents appropriately.  Access to all HCS records shall be afforded to the project engineer at all times.

Fuel / Diesel

Bulk storage areas shall be demarcated, secured and sign posted with the relevant warning pictograms.

Bulk storage areas shall be bunded.

Re-fuelling shall be conducted in designated re-fuelling areas only.

Spill-kits shall be available at all times in these designated areas.

The surface of the bunded areas and walls shall be of impermeable material.

The bunded area shall be sloped towards a collection pit.

Asbestos

No asbestos is to be used on this Project.

#### Plant and Machinery

Construction Plant

All plant shall comply with the OHS Act requirements in relation to operation and maintenance thereof.

Service and maintenance of the vehicles shall be of a high standard at all times.

All plant shall subject to design be fitted with back-up alarms and audible indicating devices.

The COMPANY shall ensure that all construction plants moving parts are adequately protected.

Pre-start inspections shall be conducted on all motorised equipment daily, deviations of such inspections shall be recorded.

Construction plant identified for use shall be operated by a trained and authorised operator.

All construction plant shall be operated under the direct supervision of a person competent to identify potential hazards in the work he is conducting.

Work involving the use of construction plant shall be conducted in accordance with an approved Risk Assessment.

The Site Agent shall ensure all operators are equipped with the necessary PPE namely; safety shoes, overall, safety glasses, and gloves.

Plant shall be fitted with an extinguisher where practicable.

Washing shall be conducted in the designated washing areas.

The COMPANY shall ensure the all equipment moving to and from site is adequately secured, and that all contractors abide by this requirement.

Transport of Personnel

Safe vehicular transport shall be provided for personnel working on the project to the workplace, which shall include proper seating, side restraints and cover.

No personnel shall be permitted to travel on any plant or equipment on the site works.

Road safety principles shall be adhered to on and off site.

Vessels under Pressure (VuP) or Gas Bottles

The COMPANY shall ensure they comply at all times with the requirements of Vessels under Pressure Regulations, with specific reference to the following:

Ensuring all Equipment owned and hired-in Vessels under pressure, comply with the 36-month pressure vessel inspection, and a certificate of testing is available on site.

Ensuring that all personnel who shall use this equipment are competent and trained.

Ensuring the users of this equipment are issued with the required PPE.

Ensuring the area is adequately identified as a noise area and warnings are posted.

Ensuring daily pre-start inspections are carried out on all the equipment and the findings recorded.

Ensuring the correct fire prevention and fighting equipment is available at all times.

Noise levels where possible shall be kept within reasonable operating norms.

Fire Equipment

The Site Agent shall ensure the following all fire equipment to be used on site comply with the following:

Extinguishers shall be placed in positions to ensure fast and easy access is maintained at all times.

Placement of all extinguishers shall be depicted with the required pictograms.

Extinguishers shall be serviced once annually, and after discharge or visible signs of depressurisation.

The Site Agent shall ensure all employees are adequately trained in the safe use of the extinguishers.

The Site Agent shall ensure a person is appointed to inspect the extinguishers on a monthly basis and the results of which are to be entered into a register designed for that purpose.

Hired Plant and Machinery

The Site Agent shall ensure the following criteria is adhered to when considering hired plant and machinery:

Only approved hire companies shall supply equipment to the site.

Hired plant shall be checked for safety compliance prior to being accepted for use on site.

Should hired equipment be accompanied by an operator, The COMPANY shall ensure that the operators competency be verified and the operator undergo an induction training session.

The Site Agent shall ensure the operators of hired plant attend weekly toolbox talks in conjunction with The COMPANY site personnel.

The Site Agent shall ensure that all operators are equipped with the required PPE before commencing work on site.

Scaffolding / Working at heights / Fall Protection

Work involving scaffolding and work at heights shall comply with the requirements set out in the Construction regulations 2003 pertaining to these activities with reference to the SABS 085 code of practice.

Fall protection planning shall be done in conjunction with the risk assessment process.

All scaffold shall be erected under the control of a person trained and appointed to conduct such scaffold erection.

Falsework / Formwork for Structures

Work involving scaffolding and work at heights shall comply with the requirements set out in the Construction regulations 2003 pertaining to these activities with reference to the SABS 085 code of practice.

Lifting Machinery and Tackle

The Site Agent shall ensure that the use of Lifting Machinery and Tackle is done in accordance with the requirements of the Regulations, which include but is not limited to the following:

Lifting machinery and tackle to be used on site shall be marked with the Maximum Mass Load (MML), which is the safe limit in which the equipment may be used.

Inspections on Lifting Machines and Lifting Tackle shall be inspected once per month on the register provided and the findings recorded.

Daily pre-start checks shall also be conducted on all Lifting Machinery and Tackle.

Records shall be kept of all lifting machinery and tackle inspections and Load Tests.

Load tests shall be conducted a minimum of once per annum, and a certificate of compliance shall be kept on record.

A valid logbook shall be maintained for all lifting machinery, which will comply with a minimum six-monthly service and maintenance.

Lifting machinery shall be operated under supervision at all times with a trained banksmen who shall inspect all tackle before each lift.

All lifting equipment operators shall be trained once every two years and a copy of such training shall be attached to the appointment, which is to be made on site.

The Operators shall be tested for medical fitness.

Ladders and Ladder Work

The following requirements shall be complied with regarding Ladders and Ladder work:

Ladders shall be clearly numbered, and inspected on the register provided.

A competent person shall be identified and appointed as the ladder inspector.

Where aluminium ladders cannot be used, then wooden ladders shall be straight grained, unpainted to allow for proper inspection of the grain for cracking.

Ladders shall be secured at the top and chocked at the base to prevent slipping.

Where chocking of the base is not possible, then the user shall ensure that the ladder is held in position by another employee when ascending the ladder.

Ladders shall be inspected a minimum once per month by the person appointed as the ladder inspector.

Proper storage shall be provided for all ladders when not in use.

General Machinery

In accordance with General Machinery Regulation 2(1), The COMPANY shall:

Ensure a competent person be appointed as defined in the above clause from the Occupational Health and Safety Act, 85 of 1993 and Regulations, to service and maintain all machinery in use on site.

The COMPANY shall appoint additional competent persons to assist the competent person mentioned above in accordance with General Machinery Regulation 2(7)(a), as and when required.

The COMPANY shall ensure that records are maintained of all services conducted.

Lighting and Power

The Site Agent shall ensure lighting circuits and power circuits are fitted with suitable earth leakage systems in accordance with the client, which will include the following activities:

Earth leakage system will be tested monthly.

Malfunctions shall be repaired immediately or replaced.

Lighting shall be so positioned as not to interfere with construction activities.

Portable Electrical Tools / Explosive Power Tools

The Site Agent shall ensure the following procedure is adhered to regarding Portable Electrical Tools and Explosive Powered tools:

Minimum compliance with legislation.

Only competent persons shall be permitted to conduct routine and monthly inspections on the equipment.

Persons competent to inspect the equipment shall be appointed in writing.

Persons who are trained to operate such equipment shall be appointed and shall be the only authorised person to operate the equipment.

The Site Agent shall ensure operation of the equipment is in accordance with the approved Risk Assessment and Safe Working Procedure set out.

All users shall undergo regular awareness training to ensure compliance.

The Site Agent shall ensure the required PPE and clothing is provided and maintained.

(v)	Public Health and Safety

In the interests of public safety, The COMPANY shall ensure that all persons who may be affected by the work being conducted on site are informed and kept aware of the dangers, which may arise from the work being conducted on site.

This awareness shall be in the form of posters and inductions for visitors to site and warning signs.

(w) 	Night Work

Night work shall only be conducted upon approval of the project engineer, with the same safety standard being applied for these activities as with day work activities.

(x) 	Facilities for Safe Keeping / eating areas

The COMPANY shall ensure that adequate facility is provided for the personnel on site. The area shall provide the following:

Sufficient seating;

Seating under cover;

Protected change room;

Toilets.

Hand wash facility.

Potable water.

No food preparation shall be conducted on site and designated eating areas will be made to allow adequate seating.

Waste bins shall be strategically placed and cleared regularly.

ANNEXURE A (Safety Policy)

ANNEXURE B (HTI)

ANNEXURE C (Risk Assessment)

ANNEXURE D (Safety Induction)

ANNEXURE E (Toolbox talks)

ANNEXURE F (Audit Schedule)

## PARTICULAR SPECIFICATION PF

VALVES

PF 1	GATE VALVES

Gate Valves shall bear the official mark of SABS and be SABS approved. They shall comply with SABS 664 for waterworks pattern valves of the types, classes and sizes listed in the Schedule of Quantities and shall be provided with the following:

|  | Description | Specification |
| --- | --- | --- |
| 1 | Flanges | Double flanged, to be in accordance with and drilled off-centre to SABS 1123, Table 1600, 2500 or 4000 as scheduled. |
| 2 | Spindles | Non rising, bronze or stainless steel with spindle nut either bronze or gunmetal |
| 3 | Handwheels | Direction of rotation for opening valves shall be clockwise when viewed from the top and appropriate wording must be embossed at the top indicating direction of “close” and “open” with arrow heads |
| 4 | Tests | Valves to be subjected to “closed end” and “open end” pressure tests to one and half times the working pressure. Valve body shall be tested to twice working pressure. Under all the tests, no leakage to occur |
| 5 | Paint | As in PF4 |
| 6 | Other | - Type B gunmetal trim - Valves should permit repacking of the gland whilst valve is under pressure - Factory test certificates to be provided with each valve - Rates in the schedule of quantities to include requirements to comply with specification |

PF 2	REFLUX VALVES

Reflux valves shall, except where otherwise specified, be double flanged single door swing type and shall be fitted with gun metal seats and bronze hinge and clack pins.  In the case of reflux valves to be mounted horizontally, the design shall be such that the gate rests against the seat in the absence of flow or of differential pressure, without the aid of springs or external counterweights.  Reflux valves shall comply with the requirements of SABS 144 for working pressures as required for each application, but not less than 1600 kPa working pressure.

PF 3	AIR VALVES

PF 3.1	General

The materials and workmanship employed in the manufacture of air valves shall be of a similar standard to that set out in SABS 664 for waterworks pattern gate valves and they shall be provided with individual test certificates for each valve from the manufacturer; all valves are to be inspected, and the hydraulic tests witnessed, by an Inspector to be appointed by the Engineer, and the tendered rates for the valves shall include for making arrangements for independent inspections.   The Inspectors' fee and recoverable expenses will be for the account of the Employer, fees and expenses arising from abortive or repeat visits due to non-compliance with the specified requirements will be for the Contractor's account and will be deducted from amounts due to the Contractor.

PF 3.2	Types of Air Valves

Air Valves shall be standard types (epoxy coated flanges; stainless steel sleeve, bolts, nuts, studs etc), of the double orifice type, and shall be equal or similar to the "Vent-O-Mat" (RBX series: 50 mm dia valves: 050 RBXc2511; 80 mm valves: 080 RBXc1601) type in which a small orifice, manufactured from Grade 316 stainless steel and having a minimum orifice size of 2,0 mm diameter, shall be capable of releasing accumulations of air at all pressures throughout the specified working pressure range and shall be drop-tight at 0,5 Bar.   The large orifice shall be suitable for admitting or expelling large quantities of air during emptying and filling of the pipeline.  The opening of the valve (to atmosphere) shall be enclosed by a stainless steel mesh which has been fixed into the valve body to prevent the entry of small insects or vermin into the valve.

All welding of stainless steel shall be carried out in workshops dedicated to the fabrication of stainless steel products.   Care shall be taken that the correct welding rods and approved welding procedures have been used for each application, and the Engineer shall have the right to request a certificate from the manufacturer in which the weld procedures used for the manufacture of valves supplied are stated.

All welds and weld beads, internal and external, shall be smoothed down by grinding and buffing.    All stainless steel shall be pickled and passivated before the valve is assembled and tested.

PF 3.3	Testing

Each air valve is to be subjected to the following tests at the factory:

(a)	First, fill the valve with water and apply the factory test pressure through the inlet of the valve.   Under this condition there shall be no weeping from any part of the valve.

(b)	Second, drain the valve and refill the valve with water and apply the maximum working pressure through the inlet of the valve and maintain for at least five minutes.   Under this condition there shall be no loss of water from the valve.

(c)	Third, gradually reduce the pressure applied under (b) above to atmospheric pressure, empty the valve and refill slowly expelling the air through the valve until it is full of water.   Raise the pressure to the minimum working pressure, maintain that pressure for at least five minutes and again there shall be no loss of water from the valve.

(d)	Fourth, maintain the minimum working pressure applied in (c) above, isolate the water inlet and introduce small amounts of compressed air into the valve without lowering the pressure in the valve.   The lower float shall drop away from the upper float when sufficient air has accumulated in the valve.   As soon as the accumulated air in the valve has discharged through the small orifice, the valve shall again close to a watertight condition.    This process shall be repeated for at least five different pressures which are equally spaced between the specified minimum and maximum operating pressures, and the valve shall close automatically when all the air has escaped without any dribbling and shall have a drop-tight shut-off.

PF 3.4		Table of Particular Requirements for Air Valves

| Scheduled Items |  |  |  |
| --- | --- | --- | --- |
| Nominal diameter (mm) | 80 | 80 | 25/50 |
| Class | 40 | 25 | 16 |
| Flange Size and Rating | SABS 1123 Table 4000 | SABS 1123 Table 2500 | SABS 1123 Table 1600 |
| Flange Drilling | SABS 1123 Table 4000 | SABS 1123 Table 2500 | SABS 1123 Table 1600 |
| Factory Test Pressure (metres head of water) | 800 | 500 | 320 |
| Field Test Pressure (metres head of water) | as for pipeline | as for pipeline | as for pipeline |
| Working Pressure (metres head of water) : |  |  |  |
| (a) Maximum | 400 | 250 | 160 |
| (b) Minimum | 10 | 10 | 10 |

PF 4	PAINTING OF VALVES

PF 4.1	The cleaning and painting of valves as specified hereunder is to be carried out at the factory prior to despatch to site.

PF 4.2	All cast iron surfaces of every valve shall be prepared for painting to a thoroughly clean condition free of all grease and deleterious matter.    Steel surfaces shall be prepared in accordance with Swedish Standard SIS 05 5900 for a Sa 2.5 finish.

PF 4.3	Internal surfaces shall then be treated with two coats of Copon Hicote 151E or other approved non-toxic epoxy resin paint to give a total minimum dry film thickness of 160 micrometres; both coats being applied within 48 hours of commencement of painting.

PF 4.4	External surfaces shall, immediately after cleaning, be treated with one of the following alternative paint systems:

(a)	System 1 - for valves situated in underground chambers or exposed conditions.

Apply three coats of an approved epoxy coal tar paint to give a minimum total dry film thickness of 240 micrometres; all three coats being applied within 72 hours of commencing the first coat.

(b)	System 2 - for valves situated in pump stations etc.

Apply one coat of zinc chromate primer followed by one coat of undercoat tinted where necessary, and a final coat of best quality gloss enamel.    The total dry film thickness of the system shall be not less than 200 micrometres.

PF 4.5	Non-ferrous metal or stainless steel surfaces shall not be painted.

PF 4.6	After erection on site all valves shall be cleaned and the paint work refurbished where necessary to restore the condition to that at the time of leaving the factory.

PF 5	PAYMENT

The prices quoted for all valves are to include for independent factory testing of valves, which test will be witnessed by Inspectors appointed by the Engineer.

PARTICULAR SPECIFICATION: PES

ENVIRONMENTAL SPECIFICATION

PS EMP	ENVIRONMENTAL MANAGEMENT PLAN

The Environmental Management Plan and specifications are included under this section and must be adhered to in all respects.

The rates and prices tendered by the Contractor shall be deemed to include all costs for conforming.  The following specifications must be adhered to in all respects:

PS EMP1

No natural vegetation, trees or crops may be damaged by the Contractor without the written approval of the Engineer. The Contractor must keep the site neat and free of refuse, etc. to prevent possible damage to crops or livestock.

The Contractor's construction activities shall be performed by methods that will prevent the entrance of, or accidental spillage of solid matter, debris, contaminants and other pollutants and wastes into streams and water-courses. Any dewatering for earthworks or structure foundations adjacent to or encroaching on streams or water-courses shall be conducted in a manner to prevent muddy or contaminated water from entering streams or water-courses by means of the construction of intercepting and bypassing ditches, barriers, ponds and other approved means.

Construction activities shall be performed in a manner to keep dust nuisance to a minimum by means of the application of sufficient water or other efficient measures wherever and as often as may prove necessary.

The cost for complying with the requirements regarding protection of the environment specified above shall be included in the rates tendered in the Schedule of Quantities for the various items of work and no additional payment will be made in this regard. The Engineer will be entitled to retain an amount of money, should a dispute between property owners and the Contractor arise. The balance of this money will be released as soon as the dispute is resolved. Should any of the above mentioned items not be complied with, the Engineer reserves the right to appoint another Contractor to rectify these matters. Costs for this work will be deducted from the payment of the Contractor for this Contract.

In order to reduce and control the release of airborne pollutants the Contractor shall ensure that:

- No fires are lit on Site to dispose of waste or for cooking.

- All loose material that could be blown about or into neighbouring properties by wind is secured.

- The spraying of formwork oils, paints and other toxic substances is limited to the application area.

PS EMP2

The Site Agent shall ensure that his team, including sub-contractors, comply with the environmental management requirements of this Contract.

PS EMP3

The Contractor may be required to submit a Construction Method Statement at the Site handover.  Activities having an effect on the environment must be addressed in this Construction Method Statement.  A list of possible activities is included below.

Possible activities having an effect on the Environment:

1.	Collection, storage and disposal of solid waste

2.	Collection, storage and disposal of liquid waste

3.	Protection of indigenous plant species

4.	Protection of natural water sources from liquid and solid wastes

5.	Control of noise and dust

6.	Security on site

7.	Control of veld fires

8.	Temporary storage of spoil, disposal of excess spoil and unsuitable materials and the importation of earthworks materials

9.	Site clearance prior to construction

10.	Felling of trees

11.	Habitat restoration

12.	Site reinstatement, removal of site offices and final site clearance

PS EMP4

In the event that the Contractor fails to comply with the Environmental Management Specifications, included in the Contract Documents, the following penalties will be imposed per incident: -

Unauthorised damage or removal of trees                                                                       R2 500,00

Failure to keep soil types separate during excavation and backfilling                             R1 000,00

Failure to provide adequate portable chemical toilets                                                      R 500,00

Failure to comply with solid waste disposal requirements                                               R1 000,00

Failure to clean up litter at the end of each working day                                                 R1 000,00

Failure to comply with dust prevention requirements                                                      R1 500,00

Failure of Contractor and/or materials supplier to cover vehicle                                     R 500,00

Failure to comply with noise, light or air pollution requirements                                     R 500,00

Spillage of hazardous substances                                                                                 R1 000,00

The Engineer will notify the Contractor of a breach of specification and supply a time period within which remedial action will need to be carried out.  Should the time period elapse then the penalty will be imposed and the sum deducted from the following month’s certificate.

At the time of tender the Contractor shall nominate two people who will be responsible for ensuring that the Contractor’s team and sub-contractors comply with the environmental management requirements of this contract.  While the positions are only part time, these staff members will be called upon from time to time to deal with any events that are not in compliance with the specifications.

- SECTION 4A: SITE ESTABLISHMENT AND PRELIMINARY ACTIVITIES

| 4A.1 Access to Site Sound environmental principles must be followed whilst establishing access to the site. As much as possible, use should be made of the existing roads instead of creating new ones. | A.1.1 Routing a) The contractor must take into account any limitations identified and recommendations made during the environmental duties when deciding on an access route to construction site. b) The location of all underground services and servitudes must be identified and confirmed. c) Choice of access routes should take into account minimum disturbance to residents and businesses neighboring the site. A.1.2 Haulage Roads a) All roads for construction access must be planned and approved by the Engineer and ECO ahead of construction activities. They should not be created on an ad-hoc basis. b) Roads must follow natural contours to reduce stormwater erosion. c) Roads must have as little cut and fill as possible. d) Road widths and the radii of curves are to be reduced. e) No trees/shrubs/groundwater may be removed or vegetation stripped without the prior permission of the Engineer/ECO. f) Agreed turning areas for haulage vehicles are to be formalized and used by the Contractor. No turning maneuvers other than at the designated places shall be permitted. g) Contractors shall construct formal drainage on all temporary haulage roads in the form of side drains and mitre drains to prevent erosion and point source discharge of run-off. h) Scour check walls must be constructed in the side drains as follows: Gradient of Road; Scour Check Spacing. <4%; Not required. 5%; 20m. 8%; 10m. 10%; 5m. i) Scour checks can be constructed from rocks available onsite or using driven wooden pegs. Smaller rocks must be placed on the invert of side drain upstream and downstream of the scour checks. j) Haulage roads must allow for the natural flow of water k) All stream/rivers crossing and temporary bridges shall be built to the Engineer’s approval. A.1.3 Survey Points a) Roads or trails that are cut to provide temporary access for survey work must be minimized. b) Marking of survey points must be done with the Engineer’s approval. c) Vegetation clearing must be kept to a minimum during survey operations | - Monitor Engineer (E)/ Environmental Control Officer (ECO) E Engineer (E)/ Environmental Control Officer (ECO) N/A Use Existing access roads N/A N/A N/A E E/ECO E N/A E N/A - Monitor N/A N/A N/A | - Frequency Prior to moving onto site. Prior to moving onto site. Prior to moving onto site N/A N/A N/A N/A Prior to moving onto site. During construction period Prior to moving onto site. N/A N/A N/A N/A - Frequency N/A N/A N/A |
| --- | --- | --- | --- |
| 4A.2. Setting up Construction Camp Careful planning of the construction camp can ensure that time and costs associated with environmental management and rehabilitation are reduced | A.2.1 Layout a) Choice of site for the Contractor’s camp requires the Engineer’s permission and must take into account location of local residents and /or ecologically sensitive areas, including flood zones and slip/unstable zones. A site plan must be submitted to the Engineer for approval. b) The construction camp may not be situated on a floodplain or on slopes greater than 1:3. c) If the Contactor chooses to locate the campsite on private land, he must get prior written permission from both the Engineer and the landowner. d) In most cases, on-site accommodation will not be required. The construction camp can thus be comprised of: - Site office - Ablution facilities - Designated first aid areas - Eating areas - Staff lockers and showers (where water and waterborne are available) - Storage areas - Batching plant (if required) - Refueling areas (if required) - Maintenance areas (if required) - Crushers (if required) e) Cut and fill must be avoided where possible during the set-up of the construction camp. f) The size of the construction camp should be minimized (especially where natural vegetation or grassland has had to be cleared for its construction). g) Adequate parking must be provided for site staff and visitors. h) The constructor must attend to drainage of the campsite to avoid standing water/or sheet erosion. A.2.2 Ablutions a) Temporary chemical toilets must be provided by a company that has been approved by the Engineer. The toilets must be available for all site staff, both at the campsite, and on the site agreed by the Engineer. Toilets should be no closer than 50m from any of the two natural watercourses. b) The construction of “long drop” toilets is forbidden. c) Under no circumstances may open areas or the surrounding bush used as a toilet facility. A.2.3 Provision for Camp Waste Disposal a) Bins and / or skips shall be provided at convenient intervals for disposal of waste within the construction camp. b) Bins should have liner bags for efficient control and safe disposal of waste. c) Recycling and the provision of separate waste receptacles for different types of waste should be encouraged. | E/ECO E/ECO E E E E/ECO E ECO ECO ECO Monitor ECO ECO ECO ECO | During surveys and preliminary investigations and prior to moving onto side. During surveys and preliminary investigations. During surveys and preliminary investigations. During site setup During site setup. During site setup. During site setup. On a weekly basis. During site setup. Ongoing Frequency Ongoing. During site set-up and ongoing. Ongoing. During site set-up and ongoing. |
| 4A.3. Establishing Storage Access Storage areas can be hazardous, unsightly and can cause environmental pollution if not designed and managed carefully. | A.3.1 General Substances and Materials a) Choice of location for storage areas must take into account prevailing winds, distance to water bodies and general on-site topography. b) Storage areas must be designated, demarcated and fenced if necessary. c) Storage areas should be secure so as to minimize the risk of crime. They should also be safe from access by children/animal etc. d) Fire prevention facilities must be present at all storage facilities. e) If electrical equipment for substations is stored on site a firebreak will be around the storage area. f) Burning of fire breaks is to be carefully planned and managed with the assistance of the nearest Fire Department A.3.2 Hazardous Substances and Materials a) Definition of hazardous substances/materials are those that are potentially: poisonous, flammable, carcinogenic or toxic. b) Some examples of hazardous substances/materials: - Diesel, petroleum oil, bituminous products - Cement - Solvent based paints - Lubricants - Explosives - Drilling fluids - Pesticides, herbicides - LPG c) Material Safety Data Sheets (MSDSs) shall be readily available on site for al chemicals and hazardous substances to be used on site. Where possible and available. MSDSs should additionally include information on ecological impacts and measures to minimize negative environment impacts during accidental release or escapes. d) Hazardous storage and refueling areas must be bunded with an impermeable liner to protect groundwater quality. The Contractor shall submit a method statement to the Engineer for approval. e) Fuel tanks must meet relevant specifications and be elevated so that leaks may be easily detected. f) Storage areas containing hazardous substances/ materials must be clearly signed. g) It is very important that the proximity of houses, schools etc is taken into account when deciding on storage areas for hazardous substances. h) Residents living adjacent to the construction site must be notified of the existence of the hazardous storage area. i) Staff dealing with these materials/substances must be aware of their potential impacts and follow the appropriate safety measures. j) Contractors shall submit a method statement and plans for the storage of hazardous materials and emergency procedures. | Monitor ECO ECO ECO ECO N/A N/A E/ECO E/ECO ECO ECO ECO ECO ECO | Frequency During site set-up. During site set-up. During site set-up. During site set-up. N/A N/A Ongoing During site set-up. During site set-up. During site set-up. During surveys and preliminary investigations. When moving onto site or as the relevant materials arrive onsite. During staff induction and ongoing as necessary. Prior to establishment of storage area. |
| 4A.4. Materials Management Sourcing Materials must be sourced in a legal and sustainable way to prevent off-site environmental degradation. | A.4.1 Sources of Materials a) Contractors shall prepare a source statement indicating the sources of all material (including topsoil, sands, natural gravel, crushed stone, asphalt, clay liners etc), and submit these to the Engineer for approval prior to commencement of any work. b) Where possible, a signed document from the supplier of natural materials should be obtained confirming that they have been obtained in a sustainable manner and in compliance with relevant legislation. c) Where materials are borrowed (mined), proof must be provided of authorization to utilize this material from the landowner /mineral rights owner and the Department of Mineral and Energy. | Monitor E/ECO ECO ECO | Frequency On award of contract On receipt of natural materials. On receipt of borrowed materials. |
| 4A.5 Education of Site Staff on General an Environmental Conduct These points need to be mde clear to all staff on site before the project begins. | A.5.1 Environmental Education and Awareness Ensure that all site personnel have a basic level of environmental awareness training. The Contractor must submit a proposal from this training to the ECO for approval. Topics covered include: - What is meant by “environment”. - Why the environment needs to be protected and conserved. - How construction activities can impact on the environment. - What can be done to mitigate against such impacts. - Awareness of emergency and spills response provisions. - Social responsibility during construction e.g. being considerate to local residents It is the Contractor’s responsibility to provide the site foreman with no less than 1 hour’s environmental training and to ensure that the foreman has sufficient understanding to pass this information onto the construction staff. a) Translators are to be used where necessary. b) The Engineer/ environmental control officer should be on hand to explain more difficult/ technical issues and to answer questions. c) The use of pictures and real-life examples is encouraged as these tend to be more easily remembered. d) Use should be made of environmental awareness posters on site. e) Construction workers should be made aware that they are not to make excessive noise (e.g. Shouting / hooting) when site is near commercial residential areas. f) The need for a “clean site” policy also needs to be explained to the construction workers. A.5.2 Workers Conduct on Site A general regard to the social and ecological well-being of the site and adjacent areas is expected of the site staff. Workers need to be made aware of the following general rules: a) No alcohol/drugs to be present on site. b) No firearms allowed onsite or in vehicles transporting staff to/ from site, (unless used by security personnel). c) Prevent excessive noise. d) Prevent unsocial behaviour. e) Bringing pets onto the site is forbidden. f) No harvesting of firewood from the site or form the areas adjacent to it. g) Construction staff are to make use of the facilities provided for them, as opposed to ad-hoc alternatives. (e.g. fires for cooking; the use of surroundings bush as a toilet facility are forbidden). h) Trespassing on private /commercial properties adjoining the site is forbidden. i) Driving under the influence of alcohol is prohibited. j) Other than pre-approved security staff, no workers shall be permitted to live on site. | Monitor ECO ECO ECO ECO ECO ECO ECO ECO ECO | Frequency During staff induction and ongoing. Frequency Prior to moving onto site. Ongoing. Ongoing. Ongoing. Ongoing. During staff induction, followed by ongoing monitoring. Induction, ongoing monitoring. During staff induction, followed by ongoing monitoring. |
| 4A.6. Dust/ AIR Pollution Establishment of the camp site, and related temporary works can reduce air quality | a) Vehicles traveling along the access roads must adhere to speed limits to avoid creating excessive dust. b) Camp construction / haulage road construction – areas that have been stripped of vegetation must be dampened periodically to avoid excessive dust. c) The Contractor must make alternative arrangements (other than fires) for cooking and /or heating requirements. LPG gas cookers may be used provided that all safety regulations are followed. | Monitor ECO ECO E | Frequency Ongoing. Ongoing- more frequently during dry and wind conditions. Ongoing. |
| 4A.7. Soil Erosion The description of vegetation during preliminary activities on site greatly increases the risk of erosion. | a) The time that stripped areas are left open to exposure should be minimized wherever possible. Care should be taken to ensure that lead times are not excessive. b) Wind screening and stormwater control should be undertaken to prevent soil loss from the site. c) Procedures that are in place to conserve topsoil during the construction phase of the project are to be applied to the set-up phase i.e. topsoil is to be conserved while providing access to the site and setting up the camp. | - Monitor E E ECO | - Frequency During surveys and preliminary investigations. During site set-up. During site set-up. |
| 4A.8. Stormwater Serious financial and environmental impacts can be caused by unmanaged stormwater | a) To prevent stormwater damage, the increase on stormwater run-off resulting from construction activities must be estimated and the drainage system assessed accordingly. A drainage plan must be submitted to the Engineer for approval and must include the location and design criteria of any temporary stream crossing (sitting and return period etc.) b) During site establishment, stormwater culverts and drains are to be located and covered with metal grids to prevent blockages if deemed necessary by the Engineer. (e.g. due to demolition work). c) Temporary cut off drains and berms may be required to capture stormwater and promote infiltration. | E E ECO | During surveys and preliminary investigations. During site set-up. During site set-up. |
| 4A.9. Water Quality Incorrect disposal of substances and materials and polluted run-off can have serious negative effects on groundwater quality. | a) Storage areas that contain hazardous substances must be bunded with an approved impermeable liner. b) Spills in bunded areas must be cleaned up, removed and disposed of safely from the bunded area as soon after detection as possible to minimize pollution risk and reduced bunding capacity. c) A designated, bunded area is to be set aside for vehicles washing and maintenance. Materials caught in this bunded area must be disposed of to a suitable waste site or as directed by the Engineer. d) Provision should be made during site set up for all polluted run-off to be treated to the Engineer’s approval before discharged into the stormwater system (This will be required for the duration of the project). | Monitor E E/ECO E/ECO E/ECO | Frequency During site set-up. During site set-up and as often as possible on an ongoing basis. During site set-up. During site set-up, to be monitored weekly. |
| 4A.10. Conservation of the Natural Environment The wetland and Indigenous forest in the project area require particular attention | A.10.1 Fauna and Flora a) No indigenous vegetation/trees may be cleared/removed without prior permission from the ECO. b) The forest and wetland in the area need to be protected. The ECO must mark limits around the forest and wetland before the Contractor any work in the vicinity of the forest. c) Care must be taken to avoid the introduction of alien plant species to the site and surrounding areas. (Particular attention must be paid to imported material). d) Disturbance to birds, animals and reptiles and their habitats should be minimized wherever possible. A.10.2 Sensitive Habitats A thirty-meter buffer zone (or a suitable width) from the edges of the wetland should be determined by a wetland ecologist and demarcated by the contractor. No development activity is to occur within the buffer zone. Temporary bonnox type fencing should be used and should be moved in phases as the construction progresses from one area to the next. | - Monitor N/A E/ECO ECO E/ECO N/A | - Frequency N/A. During site set-up. Ongoing in campsite, haulage areas. During surveys and preliminary investigations and ongoing. N/A`. |
| 4A.11. Set up of Waste Management Procedures | a) The excavation and use of rubbish pits on site is forbidden. b) Burning of waste is forbidden. c) A fenced area must be allocated for waste sorting and disposal. d) Individual skips for different types of waste (e.g. “household” type refuse, building rubble, etc) should be provided. | ECO ECO ECO ECO | Ongoing. Ongoing. During site set-up. During site set-up. |
| 4A.12. SOCIAL impacts – Visual & Noise It is important to take notice of the needs and wishes of those living or working adjacent to the site. Failure to do say can cause disruption to work and increase costs in the form of delays. | A.12.1 Public Participation a) During the set up phase of the project, the Contractor needs to make contact with those people that are Interested or Affected by the development (I&AP’s). b) These people will usually have been identified by the environmental consultant that was assigned to the project. If this wasn’t the case, the I&AP’s can be identified as those who either: - Live close to the site - Work close by to the site - Will have their services /infrastructure affected by the project - Have a general interest in the project - The Councilor for the ward in which the construction is taking place A.12.2. Noise Impact a) Construction vehicles are to be fitted with standard silencers prior to the beginning of construction. b) Equipment that is fitted with noise reduction facilities (e.g. Side flaps, silencers etc) will be sued as per operating instructions and maintained properly during site operations. A.12.3 Visual Impacts a) Storage facilities, elevated tanks and other temporary structures onsite should be located such that they have as little impact on local residents as possible. b) In areas where the visual environment is particularly important (e.g. along commercial/ tourism routes), the site may require screening in the form of shade cloth or other suitable materials prior to the beginning of construction. c) Special attention should be given to the screening of highly reflective materials on site. | Monitor E ECO ECO ECO E/ECO E/ECO ECO | Frequency Prior to moving onto site. Prior to moving onto site Prior to moving onto site. Ongoing. During surveys and preliminary investigations and site set-up. During surveys and preliminary investigations and site set-up. During site set-up. |
| 4A.13. Cultural Environment | Prior to the commencement of construction, all staff need to know what possible archaeological or historical objects of value may look like, and to notify the Engineer / Contractor should such an item be uncovered | ECO | During site set-up and ongoing. |

| 4A.14. Security and Safety | A.14.1 Fencing a) Securing the site in order to reduce the opportunity of criminal activity in the locality of the construction site. b) The sites should be fenced and manned to control the access of people. c) Potentially hazardous areas such as trenches are to be demarcated and clearly marked. A.14.2 Lighting Lighting on site is to be set out to provide maximum security and to enable easier policing of the site, without creating a visual nuisance to local resident or businesses. A.14.3 Risks Associated with Material on Site a) Material stockpiles or stacks, such as, pipes must be stable and well secured to avoid collapse and possible injury to site/ local residents. b) Flammable materials should be stored as far as possible from adjacent residents/b businesses. c) Fire fighting equipment should be present onsite at all times as per OHSA. d) Obstruction to drivers’ line of site due to stockpiles and stacked materials must be avoided, especially at intersections and sharp corners. e) No materials are to be stored in unstable or high-risk areas such as in floodplains or on steep slopes. f) All I&AP’s should be notified in advance of any known potential risks associated with the construction site and the activities on it. Examples of these are: - Stinging of power lines - Blasting - Earthworks/earthmoving machinery on steep slopes above houses/infrastructure - Risk to residences along haulage roads/ access routes | Monitor E E ECO E/ECO ECO ECO ECO ECO ECO ECO | Frequency During site set-up. During site set-up. During site set-up. During site set-up. Ongoing. Ongoing. Ongoing. Ongoing. Ongoing. 24hrs prior to the activity in question |
| --- | --- | --- | --- |

SECITON 4B: MANAGEMENT OF CONTRUCTION ACTIVITIES AND WORKFORCE

| 4B.1. Access to Site | B.1.1 Haulage Roads a) Contactors shall ensure that all side an mitre drains and scour check walls on access and haul roads are functioning properly and are well maintained. B.1.2 Maintenance of Access a) Contractor should ensure that access roads are maintained in good condition by attending to potholes, corrugations and stormwater damage as soon as these develop. b) If necessary, staff must be employed to clean surfaced roads adjacent tot construction sites where materials have been split. c) Unnecessary compaction of soils by heavy vehicles must be avoided; construction vehicles must be restricted to demarcated access, haulage routes and turning areas. d) Cognisance of vehicles weight/ dimensions must be taken when using access constructed out of certain materials. e.g. paved surface/ cobbler entranceways. | - Monitor E E ECO ECO E | - Frequency Weekly and after heavy rains Weekly inspection. When necessary. Ongoing. Ongoing. |
| --- | --- | --- | --- |
| 4B.2. Maintenance of Construction Camp | B.2.1 Surfaces a) The Contractor must monitor and manage drainage of the camp site. To avoid soil erosion. b) Run-off from the campsite must not discharge into neighbours’ properties. B.2.2 Ablution a) Chemical toilets are to be maintained in a clean state and should be moved to ensure that they adequately service the work areas. b) The Contractor is to ensure that open areas or the surrounding bush are not being used as a toilet facility. B.2.3 Camp Waste Disposal a) The Contractor shall ensure that all litter is collected from the work and camp areas daily. b) Bins and/or skips should be emptied regularly and waste should be disposed of at a registered landfill site. Waybills for all such disposals are to be kept by the Contractor for review by the Engineer /ECO. c) A registered chemical waste company is to be used to remove waste from chemical toilet on site. B.2.4 Eating Areas a) Eating areas should be regularly serviced and cleaned to ensure the highest possible standards of hygiene and cleanliness. b) All litter throughout the site should be picked up and placed in the bins provided. B.2.5 Housekeeping a) The Contractor shall ensure that his camp and working areas are kept clean and tidy at all times | Monitor E E ECO ECO ECO ECO ECO - Monitor ECO ECO E/ECO | Frequency Ongoing. Ongoing. Weekly inspection. Weekly inspection. Ongoing. Weekly. Ongoing. - Frequency Daily Daily. Weekly monitoring |
| 4B.3. Staff Conduct | B.3.1 Environmental Education and Awareness a) The Contractor must monitor the performance of construction workers to ensure that the points relayed during their induction have been properly understood and are being followed. If necessary, the ECO and /or a translator should be called to the site to further explain aspects of environmental or social behaviour that are unclear. B.3.2 Worker Conduct on Site a) The rules explained in the worker conduct section (see section A.5.2 of this EMP), must be followed at all times. | Monitor E/ECO ECO | Frequency Ongoing monitoring. Ongoing. |
| 4B.4. Dust/ Air Pollution Main causes of air pollution are dust from vehicle movements and stockpiles, vehicle emissions and fires | a) Vehicles traveling to and from the construction site must adhere to speed limits so as to avoid producing excessive dust. b) A speed limit of 30km/hr must be adhered to on all dirt roads. c) Access and other cleared surfaces must be dampened whenever possible and especially in dry and windy conditions to avoid excessive dust. d) Where dust is unavoidable in residential or commercial areas, screening will be required utilizing wooden supports and shade cloth. e) Vehicles and machinery are to be kept in good working order and to, meet manufactured specification from safety, fuel consumption etc. f) Should excessive emissions be observed, the Contractor is to have the equipments seen to as soon as possible. g) No fires are allowed on site except for burning of firebreak. h) Stockpiles may cause dust and so must be managed in by the guidelines in Materials Management in section B.9.1 | Monitor E E E E ECO E E E | Frequency Ongoing. Ongoing. Ongoing. As directed by Engineer. Ongoing. As directed by the Engineer. Ongoing Ongoing. |
| 4B. 5 Soil Erosion | B.5.1 Topsoil Stripping and Stockpiling Once an area has been cleared of vegetation, the top layer (nominally 150mm) of soil should be removed and stockpiled in a designated area. B.5.2 Exposed Surfaces The full length of the works shall not be stripped of vegetation prior to commencing other activities. The time that stripped areas are exposed shall be minimized wherever possible. a) Top-soiling and revegetation shall commence immediately after the completion of an activity and at an agreed distance behind any particular work front. b) Stormwater control (See B6) and wind screening should be undertaken to prevent soil loss from the site. c) Side tipping of spoil and excavated materials shall not be permitted – all spoil material shall be disposed of as directed by the Engineer. d) Battering of all banks shall be such that cut and fill embankments are no steeper than previous natural slopes unless otherwise permitted by the Engineer. Cut and fill embankments steeper than previous ground levels shall be re-vegetated immediately on completion of trimming or shall be protected against erosion using bioengineered stabilization measures. Deep-rooted vegetation such as Vetiver grass is effective to stabilize steeper embankments, | - Monitor ECO E/ECO ECO E E ECO | - Frequency Ongoing. Ongoing. As each activity is completed. Ongoing. Ongoing. As the cut and fill activity is completed. |
|  | e) All embankments, unless otherwise directed by the Engineer, shall be protected by an off drain to prevent from cascading down the face the embankment and causing erosion. | Monitor E | Frequency Immediately after the creating of the embankment/ stripping of vegetation. |

| 4B.6. Stormwater Measures in this section are aimed at reducing the erosive potential of stormwater | B.6.1 General Principles: a) The Contractor shall not in any way modify nor damage the banks or bed of streams, rivers, wetlands, other open water bodies and drainage lines adjacent to or within the designated area, unless required as part of the construction project specification. Where such disturbance is unavoidable, modification of water bodies should be kept to a minimum in terms of: - Removal of riparian vegetation - Opening up of the stream channel b) Earth, stone and rubble is to be properly disposed of so as not to obstruct natural water pathways over the site. i.e.: these materials must not be placed in stormwater channels, drainage lines or rivers. c) There should be a periodic checking of the site’s drainage system to ensure that the water flow is unobstructed. d) The use of high velocity stormwater pipelines should be avoided in favor of open, high friction, semi-permeable channels wherever feasible e) A number of smaller stormwater outfall points should be constructed rather than a few large outfall points. f) Stormwater outfalls should be designed to reduce flow velocity and avoid stream-bank and soil erosion. | - Monitor ECO E E/ECO E/ECO E/ECO E/ECO | - Frequency Ongoing. Monitoring throughout the duration of the project. Monthly checking As directed by Engineer As directed by Engineer |
| --- | --- | --- | --- |
|  | B.6.2 Stormwater Detention Ponds a) Detention ponds should be vegetated either with wetland vegetation or grass from the Revegetation Specification. The detention ponds must not block the water flow, but should encourage spreading of the flow over wider areas to reduce velocity and encouraged infiltration. b) Peak stormwater discharge from the site/area should not be increased with development of the site/area. Stormwater should be detained on site through the use of stormwater detention ponds wherever possible. A series of detention ponds may be required where flow volumes are high. B6.3 Un-channeled Flow a) During construction unchanneled flow must be controlled to avoid erosion. Where large areas of soil are left exposed, rows of straw/hay or bundles of cut vegetation should be dug into the soil in contours to slow surface wash and capture eroded soil. The spacing between rows will be dependent on slope. b) Where surface run-off is contracted (e.g. along exposed roadways/tracks), flow should be slowed by contouring with hay bales or bundled vegetation generated during site clearance operation. If the area must be used for construction vehicles, berms may be used instead. The berms must at least 30cm high and well compacted. The berms should channel concentrated flow into detention ponds or areas protected with hay bales for flow reduction and sediments capture. | - Monitor ECO E/ECO E/ECO - Monitor E/ECO | - Frequency On completion of detention ponds As directed by Engineer and ongoing monitoring As surfaces become exposed - Frequency Ongoing |
| 4B.7. Water Quality Soil erosion and sediment is detrimental to water quality. Mismanagement of polluted run-off from vehicle and plant washing and wind dispersal of dry materials into rivers and watercourses are detrimental to water quality. | a) Mixing /decanting of all chemicals and hazardous substances must take place either on a tray or on an impermeable surface. Waste from these should then be disposed of to a suitable waste site. b) Every effort should be made to ensure that any chemicals or hazardous substances do not contaminate the soil or ground water on site. c) Care must be taken to ensure that run-off from vehicle or plant washing does not enter the groundwater. Wash water must be passed through a three-chamber SOG trap prior to being discharged as effluent to a regular municipal sewer. d) Site staff not be permitted to use any stream, river, other open water body or natural water source adjacent to or within the designated site for the construction or related activities. Municipal water (or another source approved by the Engineer) should instead be used for all activities such as washing of equipment or disposal of any type of waste, dust suppression, concrete mixing, compacting etc. e) Emergency contact numbers in should be listed and openly displayed in order to speedily deal with spillages and contamination of aquatic environments should it occur. | - Monitor ECO ECO ECO ECO E/ECO | - Frequency Regular monitoring. Regular monitoring. Regular monitoring Regular monitoring. As the need arises |
| 4B.8. Conservation of Natural Environment The patch of forests specifically identified in the EMP should be avoided altogether. The buffer needs to be upheld at all cost. | B.8.1 Fauna and Flora As the work front progresses the Contractor is to check that any vegetation clearing has the prior permission of the ECO. a) Only trees that have NOT been marked beforehand are to be removed. b) Gathering of firewood, fruit, medicinal plants, crops, or any other natural material on site or in areas adjacent to the site is prohibited. c) The hunting of birds and animals on site and in surrounding areas is forbidden. d) Snares and traps on site and in surrounding areas are forbidden. e) Immediate revegetation of stripped areas and removal of aliens by weeding must take place. This significantly reduces the amount of time and money that must be spent on alien plant management during rehabilitation. f) Alien vegetation encroachment onto the site as a result of construction activities must be controlled during construction. | Monitor E N/A ECO ECO ECO ECO ECO | Frequency Ongoing. N/A Ongoing. Ongoing. Ongoing Ongoing. Twice – monthly monitoring. |
|  | g) Where possible, cleared indigenous vegetation should be kept in a nursery for use at a later stage in the rehabilitation process. | - Monitor N/A | - Frequency N/A |
| 4B.9. Materials Management | B.9.1 Stockpile Management a) Stockpiles should not be situated such that they obstruct natural water pathways. b) Stockpiles should not exceed 2m in height unless otherwise permitted by the Engineer. c) If stockpiles are exposed to windy conditions or heavy rain, they should be covered either by vegetation or cloth, depending on the duration of the project. Stockpiles may further be protected by the construction of berms or low brick walls around their bases. d) Stockpiles should be kept clear of weeds and alien vegetation growth by regular weeding. 9.2 Handling of Hazardous Materials a) All concrete mixing must take place on a designated, impermeable surface. b) No vehicles transporting concrete to the site may be washed on site. c) No vehicles transporting, placing or compacting asphalt or any other bituminous product may be washed on site. d) Lime and other powders must not be mixed during excessively windy conditions. e) All substances required for vehicle maintenance and repair must be in sealed containers until they can be disposed or /removed from the site. f) Hazardous substances / material are to be transported in sealed containers or bags. g) Spraying of herbicides/ pesticides should not take place under windy conditions and must comply with OHSA specs and other chemical handling laws h) The emergency numbers should be consulted should any accident /spillages of hazardous substances and /or materials take place. The Contractor is to outline a method statement for the dealing of accidents /spillages of hazardous materials. This statement must be handed to the Engineer as well as to DWAF should the incident occur near to a body of water. | Monitor E/ECO E ECO ECO ECO ECO ECO ECO ECO E/ECO ECO ECO | Frequency Location as directed by the Engineer. As this becomes necessary. Monthly monitoring Ongoing monitoring. Ongoing monitoring. Monthly Ongoing monitoring. Ongoing monitoring. Ongoing monitoring Ongoing monitoring |
| 4B.10. Waste Management Definition: “Refuse” refers to all construction waste (such as rubble, asphalt milling, cement, bags, waste cement, timber, cans, other containers, wire and nails) household and office waste | B.10.1 On-Site Waste Management a) Refuse must be placed in the designated skips/ bins, which must be regularly emptied. These should remain within demarcated areas and should be designed to prevent reuse from being blown out by wind. b) In addition to the waste facilities within the construction camp, provision must be made for waste receptacles to be placed at intervals along the work front. c) Littering on site is forbidden and the site shall be cleared of litter at the end of each working day. d) Recycling is to be encouraged by providing separate receptacles for different types of waste and making sure that staff are of their uses. - Waste disposal - Non-hazardous Waste All waste must be removed from the site and transported to a landfill site which must be identified prior to commencement of work. a) Waybills proving disposal at each shall be provided from the Engineer’s inspection. b) Construction rubble shall be disposed off in pre-agreed, demarcated spoil dumps that have been approved by the Engineer, or at disposal sites. c) Waste from chemical toilets should be disposed of regularly and in a responsible and in a responsible manner by a registered waste contractor. Care must be taken to avoid contamination of soils and water, pollution and nuisance to adjoining areas. - Hazardous Waste a) Hazardous waste disposal must be carried out by an approved waste Contractor. Waybills for this should be provided. b) A sump (earth or other) must be created for concrete waste. This is to be de-slugged regularly and the cement waste is to be removed to a tip site as approved by the engineer and ECO. | - Monitor ECO ECO ECO ECO ECO E/ECO ECO ECO E/ECO ECO | - Frequency Ongoing monitoring Ongoing monitoring Ongoing monitoring Ongoing monitoring. Checked at each site meeting. Ongoing monitoring Monitored weekly and at the start of builders’ holidays. Ongoing During establishment and ongoing Ongoing |
| 4B.11. Social Impacts Regular communication between the Contractor and Interested and Affected Parties (I&AP’s) is important for the duration of the contract | B.11.1 Disruption of Infrastructure and Services a) Contractor’s activities and movement of staff to be restricted to designated construction areas. b) Should the construction staff be approached by members of the public or other stakeholders, they should assist them in locating the Engineer or Contractor, or provide a number on which they may contact the Engineer or Contractor. c) The conduct of the construction staff when dealing with the public or other stakeholder shall be in a manner that is polite and courteous at all times. Failure to adhere to this requirement may result in the removal of staff from site by the Engineer. d) Disruption of access for local residents must be minimized and must have the Engineer’s permission. e) The Contractor is to inform neighbours in writing of disruptive activities at least 24 hours beforehand. This can take place by way of leaflets placed in the postboxes giving the Engineer and Contractor’s details or other methods approved by the Engineer. B.11.2 Visual Impacts a) Lighting on the construction site should be pointed downwards and away from oncoming traffic and nearby houses. b) The site must be kept clean to minimize the visual impact of the site c) If screening is being used, this must be moved and re-erected as the work front progresses. B.11.3 Noise a) Machinery and vehicles are to be kept in good working order for the duration of the project to minimize noise nuisance to neighbours. b) Notice of particularly noisy activities must be given to residents/ businesses adjacent to the construction site. Example of these include: - Noise generated by jackhammers - Blasting - Drilling - Dewatering pumps c) Noisy activities must be restricted to the times given in the Project Specification or General Conditions of Contract. | - Monitor E E/ECO E E E/ECO ECO ECO ECO ECO E/ECO E/ECO | - Frequency Ongoing. Ongoing. Ongoing. Ongoing. At least 24 hrs prior to the activity taking place. Ongoing. Ongoing- weekly monitoring. Ongoing. Ongoing. At least 24 hrs prior to the activity taking place. |
|  | B.11.4 Communication with Interested and Affected Parties (I&AP’s) a) The Engineer and Contractor are responsible for ongoing communication with those people that are interested in /affected by the project. b) A complaint register should be housed at the site office. This should be in carbon copy format, with numbered pages. The Contractor must account for any missing pages. This register is to be tabled during monthly site meetings. c) I&AP’s need to be made aware of the existence of the complaints book and the methods of communication available to them. d) Queries and complaints are to be handled by: - Documenting details of such communications - Submitting these for inclusion in complaints register. - Brining issues to Engineer’s attention immediately - Taking remedial action as per Engineer’s instruction e) Selected staff are to be made available for formal consultation with I & AP’s in order to: - Explain construction process - Answer questions | - Monitor E/ECO ECO E/ECO ECO ECO | - Frequency Monthly Monthly Ongoing. Ongoing Ongoing on a monthly basis and when required |
| 4B12. Cultural Environment | a) Possible items of historical or archaeological value include old stone foundations, tools, clayware, jewellery, remains, fossils etc. b) Should something of this nature be uncovered, the Research and Professional Services Division of AMAFA should be contacted and work should be stopped immediately. AMAFA’s head office is in Ulundi and their office in Pietermaritzburg will address any queries within KZN. The facilitator should be contacted on telephone no. 033-3946543, fax 033-3426097. | E/ECO | As required. |

SECTION 4C: POST CONSTRUCTION ACTIVITIES

| 4C.1. Construction Camp | a) All structures comprising the construction camp are to be removed from site. b) The area that previously housed the construction camp is to be checked for spills of substances such as oil, paint etc. and these should be cleaned up. c) All hardened surfaces within the construction camp area should be ripped, all imported material removed, and the area shall be top-soiled as regressed using the guidelines set out in the revegetation specification that form part of this document. d) The Contractor must arrange the cancellation of all temporary services. | - Monitor E E E E | - Frequency Project completion Project completion Project completion Project completion |
| --- | --- | --- | --- |
| - 4C.2 Vegetation | a) All areas that have be disturbed by construction activities (including the construction camp area) must be cleared of alien vegetation. b) Open areas are to be re-planted c) All vegetation that has been cleared during construction is to be removed from site or used as much as per the revegetation specification, (except for seeding alien vegetation). d) The Contractor is to water and maintain all planted vegetation until the end of the defects liability period and is to submit a method statement regarding this to the Engineer. | E E E E | Project completion Project completion Project completion Project completion |
| 4C.3 Land Rehabilitation | a) All surfaces hardened due to construction activities are to be ripped and imported materials thereon removed. b) All rubble is to be removed from the site to and approved disposal site or approved by the Engineer. Burying of rubble onsite is prohibited. c) The site is to be cleared of all litter. d) Surfaces are to be checked for waste products form activities such as concreting or asphalting and cleared in a manner approved by the Engineer. e) All embankments are to be trimmed, shaped and replanted to the satisfaction of the Engineer. f) Borrow pits are to be closed and rehabilitated in accordance with the DME-approved management plan for each borrow pit. The Contractor shall liaise with the Engineer regarding these requirements. g) The Contractor is to check that all watercourses are fee from building rubble, spoil materials and waste materials. | ECO ECO ECO ECO E/ECO E ECO | Project completion Project completion Project completion Project completion Project completion Project completion Project completion. |
| 4C.4 Material and Infrastructure | a) Fences, barriers and demarcations associated with the construction phase are to be removed from the site unless stipulated otherwise by the Engineer. b) All residual stockpiles must be removed to spoil or spread onsite as directed by the Engineer. c) All leftover building materials must be returned to spoil or spread on site as directed by the Engineer. d) The Contractor must repair any damage that the construction works has caused to neighbouring properties. | - Monitor E E ECO E | - Frequency Project completion Project completion Project completion Project completion |
| - 4C.5 General | a) The Engineer, ECO and the Contractor need to approve all remediation activities and to ensure that the site has been restored to a condition approved by the Engineer. b) Temporary roads must be closed and access across these blocked. c) Access or haulage roads that were built across watercourses must be rehabilitated by removing temporary bridges and any other materials placed in / or near to watercourses. Revegetation of banks or streambeds must be as necessary to stabilize these and must be approved by the Engineer. d) All areas where temporary services were installed are to be rehabilitated to the satisfaction of the Engineer. | E/ECO E/ECO E/ECO E/ECO | On completion of the construction & maintenance phases On completion of construction On completion of construction On completion of construction |

SECTION 5. CONCLUSIONS AND RECOMMENDATIONS

The sensitive environment along the pipe line route is the patch of indigenous forest located at the start area of the project. This forest needs to be avoided by all means. Other construction impacts are minimal and of low significance. Should the EMP be adequately implemented, potential impacts could be further reduced. The concluding recommendations are:

- Contractors need to follow the environmental management plan;

- The development needs to benefit the community in a tangible manner, and therefore, attempts need to be made to integrate community needs and aspirations into the implementation processes of the development;

- The contractor needs to show concerns for health in general and the health safety of the employees in particular;

- Where appropriate, the contractor must use local labour as much as possible;

- In terms of the National Environmental Management Act 107 of 1989 everybody is required to take reasonable measures to ensure that they do not pollute the environment. Reasonable measures include informing and educating employees about the environmental risks of their work and training them to operate in an environmentally acceptable manner;

- Furthermore, in terms of the Nation Environmental Management Act 107 of 1998 the cost of repair for any environmental damage shall be borne by the person responsible for the damage.