# Annex A –

|  | TECHNICAL SCHEDULES A & B FOR 240-56030406 |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | RING MAIN UNITS FOR SYSTEMS WITH NOMINAL VOLTAGES FROM 3.3 KV TO 33 KV |  |  |  |  |
|  | SHORT DESCRIPTION: GENERIC RMU TECHNICAL SCHEDULE |  |  |  |  |
|  | Schedule A: Purchasers specific requirements |  |  |  |  |
|  | Schedule B: Guarantees and technical particulars of equipment offered |  |  |  |  |
|  | 2 | 3 |  | 4 | 5 |
|  | Sub-clause | Description |  | Schedule A | Schedule B |
|  | Item Description | RMU 11kV 630A200A 2R1B N/E CST I/D D8060 |  |  |  |
| 1 |  | Ratings |  |  |  |
| 1.1 |  | Nominal voltage | kVrms | 3.3, 6.6, 11, 22 or 33 | ________ |
| 1.2 | SANS 1874 4.2.1 | Rated power-frequency voltage | kVrms | 12, 24 or 36 | ________ |
| 1.3 | SANS 1874 4.2.2 | System frequency | Hz | 50 | ________ |
| 1.4 |  | Number of phases |  | 3 | ________ |
| 1.5 |  | System voltage range | pu | 0.9 to 1.1 | ________ |
| 1.6 | 240-56030406 3.2 & SANS 1874 table 1 | Rated lightning impulse withstand voltage | kVpeak | 95, 125 or 170 | ________ |
| 1.7 | SANS 1874 4.2.3 | Rated short-duration power frequency withstand voltage [50Hz: 1 min] | kVrms | 28, 50 or 70 | ________ |
| 1.8 | SANS 1874 4.7.1 | Rated normal current of busbars | A | 630 or 1250 | ________ |

| 1.9 | SANS 1874 4.4.1.3 | Rated normal current of switch dis-connector | A | 630 | ________ |
| --- | --- | --- | --- | --- | --- |
| 1.10 | SANS 1874 4.6.1.3 | Rated current of circuit breaker | A | 630 or 200 | ________ |
| 1.11 | SANS 1874 4.2.4.1 | Rated short-time withstand r.m.s. current (3 seconds) | kArms | 20 or 16 | ________ |
| 1.12 | SANS 1874 4.2.4.3 | Rated short-time withstand r.m.s. current (3 seconds) of earthing switches | kArms | 20 or 16 | ________ |
| 1.13 | SANS 1874 4.2.4.1 | Rated peak withstand current | kApeak | 50 or 40 | ________ |
| 1.14 | SANS 1874 4.2.6 | Rated short circuit breaking current of the circuit breaker | kArms | 20 or 16 | ________ |
| 1.15 | SANS 1874 4.2.7 | Rated short circuit making current | kApeak | 50 or 40 | ________ |
| 2 |  | Design |  |  |  |
| 2.2 | SANS 1874 4.18 | Irrespective of the inland or coastal rating the RMU enclosure shall be suitable for coastal applications |  | All RMUs shall be suitable for Coastal applications | xxxxxxxx |
| 2.3 | SANS 1874 4.3.2 | Extensible unit required? |  | No | xxxxxxxx |
| 2.4 | SANS 1874 4.3.3.3 | Degree of protection offered (RMU): |  |  |  |
|  | SANS 62271-200 | a) moving parts |  | IP 2X | ________ |
|  | SANS 62271-200 | b) live parts |  | IP 2X | ________ |
|  | SANS 876 | c) cable boxes |  | IP 3X | ________ |
| 2.5 | SANS 1874 4.3.5 | Type of cable test facilities offered? |  | Yes | xxxxxxxx |
|  | SANS 1874 4.3.5.4 | Cable test facilities interlocked? |  | Yes | xxxxxxxx |
| 2.6 | SANS 1874 4.3.9.1 | Interlock with remote equipment required? If yes, state details: | Y/N | No | ________ |
|  |  | a) type of interlock required |  | N/A | ________ |
|  |  | b) auxiliary supply details |  | 20 or 16 | ________ |

|  |  | c) interfacing details of remote equipment |  | N/A | ________ |
| --- | --- | --- | --- | --- | --- |
| 2.8 | SANS 1874 4.3.9.2 | Interlocking facilities offered |  | N/A | xxxxxxxx |
| 2.9 | SANS 1874 4.3.10.2 | Insulating medium |  | xxxxxxxx | ________ |
| 2.10 | SANS 1874 4.3.10.2 | Minimum maintenance free period | yrs. | 30 | ________ |
| 2.11 | SANS 1874 4.3.10.3 | Interrupting technology (switch dis-connectors) |  | xxxxxxxx | ________ |
| 2.12 | SANS 1874 4.3.10.3 | Interrupting technology (circuit breaker) |  | xxxxxxxx | ________ |
| 2.13 | SANS 1874 4.3.14.1 a) | IAC required for RMUs -AFLR in accordance with SANS 62271-200? |  | Yes | xxxxxxxx |
| 2.14 | SANS 1874 4.3.14.1 | IAC required for the RMUs (AB - FLR in accordance with SANS 62271-200 & SANS 62271-202)? |  | Yes | xxxxxxxx |
| 3 | SANS 1874 4.4 | Switch-disconnectors |  |  |  |
| 3.1 | SANS 1874 4.4.1.1 | Class of switch dis-connector (min) |  | E2-M1 | ________ |
| 3.2 | SANS 1874 4.3.5.1 & 24056062752 .3.1.1 a) | Cable test facility to be independent of cable termination enclosure? |  | Yes | ________ |
| 3.3 | SANS 1874 4.3.5.4 | Cable test facilities interlocked? |  | Yes |  |
| 3.4 | SANS 1874 4.4.2.2 / 4.9.2 | Provision for remote tripping and closing required (i.e. remote control via RTU)? | Y / N | N | xxxxxxxx |
| 3.5 | SANS 1874 4.4.2.2 / 4.9.2 | Details of remote opening and closing offered |  | N/A | ________ |
| 3.6 | SANS 1874 4.4.2.2 / 4.9.2 | Provision for remote indications and alarms required (i.e. via RTU)? | Y / N | N | xxxxxxxx |
| 3.7 | SANS 1874 4.6.2.18 | Provision for hand-held remote control unit (open, close and earth) required? |  | Yes | ________ |
| 3.8 | 240-56030406 3.4b) and 3.25a) | Type of plug-in connector to be supplied |  |  | ________ |
| 3.9 | 240-56030406 | Pins for trip control function |  | C and D | ________ |
| 3.10 | 240-56030406 | Pins for close control function |  | A and B | ________ |
| 3.11 | 240-56030406 3.25 | Details of provisions offered for hand-held remote control unit | 24V/110V | Yes | ________ |
| 3.12 | SANS 1874 4.9.1.4 | Accuracy class and burden (VA) of CT offered (if applicable) |  | N/A | xxxxxxxx |
| 3.13 | SANS 1874 4.9.1.6 / 4.9.2 | Provision for communication with an RTU (i.e. remote analogue indication)? |  | No | xxxxxxxx |
| 3.14 | SANS 1874 4.9.1.7 | Type of electronic ammeter/multi-meter offered |  | xxxxxxxx | ________ |
| 4 | SANS 1874 4.8 | Cable termination enclosure of the switch dis-connector functional units |  |  |  |
| 4.1 | 240-56030406 3.13 | Spacing between bushing centres (min) | mm | 105 mm or 90 mm | ________ |
| 4.2 | 240-56030406 3.13 | Spacing between outer bushing centres and enclosure side wall (min) | mm | 55 mm or 50 mm | ________ |
| 4.3 | SANS 1874 4.8 | Distance from bushing centre line to cable support clamp (min). The cable support clamp shall be mounted above any bottom enclosure mounted plates for 3 core cable termination applications. For 1 core cable termination applications where bottom plates are required to be mounted above the cable clamps for Internal Arc venting compliance, the plate shall be positioned to meet the SANS 876 requirement for a 22 kV voltage rating single core cable termination to be fitted. | mm | 800 | ________ |
| 4.4 | SANS 1874 4.8 | Bushings horizontally positioned? | Y/N | YES | ________ |
| 4.5 | SANS 1874 4.8.4 | Type of bushing |  | EN 50181 C-type interface | ________ |
| 4.6 | SANS 1874 4.11.4 | Cross sectional area of earthing bar (min) | mm2 | 120 | ________ |

| 4.7 | SANS 1874 4.8.6 | Type of cable support clamp |  | SANS 876 / |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | D-DT-8019 / 24056062752 | ________ |
| 4.8 | 240-56030406 3.13 g) | Size (range) of cable support clamp (3 Core Cable applications) | mm | 50-100 | ________ |
| 4.9 | 240-56030406 3.13 g) | Size (range) of cable support clamps (3 * 1 Core Cable applications) | mm | 25-55 | ________ |
| 5 | SANS 1874 4.6 | Circuit-breakers for tee-offs |  |  |  |
| 5.1 | SANS 1874 4.6.1.1 | Class of circuit-breaker (min) |  | E2-M1 | ________ |
| 5.2 | SANS 1874 4.6.1.3 | Rated normal current of the circuit-breaker (200A/630A). | A | 200A / 630A | ________ |
| 5.3 | SANS 1874 4.3.5.1 | Cable test facility to be independent of cable termination enclosure? | Y/N | Not mandatory (if available to be supplied) | ________ |
| 5.4 | SANS 1874 4.6.3.3 / 4.9.2 | Provision for remote tripping and closing, and the opening for the inline dis-connector required (i.e. remote control via RTU)? | Y/N | No | xxxxxxxx |
| 5.5 | SANS 1874 4.6.3.4 | Details of remote tripping and closing, and the opening for the inline dis-connector where applicable offered. |  | xxxxxxxx | ________ |
| 5.6 | SANS 1874 4.9.2 | Provision for remote indications and alarms required (i.e. via RTU)? | Y/N | No | xxxxxxxx |
| 5.7 | 240-56030406 3.4 | Provision for hand-held remote control unit (trip and close) required? | Y/N | Yes | ________ |
| 5.8 | 240-56030406 3.4 b) | Type of plug-in connector to be supplied |  | ITT Cannon type CA 3102 A 14S-2 or equivalent | ________ |
| 5.9 |  | Pins for trip control function |  | C and D | ________ |

| 5.10 |  | Pins for close control function |  | A and B | ________ |
| --- | --- | --- | --- | --- | --- |
| 5.11 | 240-56030406 3.4 | Details of provisions offered for hand-held remote control unit | 24V/110V | xxxxxxxx | ________ |
| 5.12 | 240-56030406 3.10 b) | Second Trip Coil required and Voltage | Y/N V | No _______ | xxxxxxxx xxxxxxxx |
|  |  | Protection relay Requirements |  |  |  |
| 5.12 | 240-56030406 3.6.1 | Self-Powered Protection Relay (SPR) required. | Y/ N | Y | xxxxxxxx |
| 5.12.1 | 240-56030406 3.6 | Protection functional requirements satisfied, i.e. functions, setting ranges, characteristic curves etc. (provide technical manual). |  | xxxxxxxx | ________ |
| 5.12.2 | 240-56030406 3.6.1.1 c) | Details of provisions made to ensure minimum earth fault pick-up current of 40 A. |  | xxxxxxxx | ________ |
| 5.12.3 | 240-56030406 3.6 & 3.6.1.3 | CT ratio required if different to that specified (SPR). | A | ________ | xxxxxxxx |
| 5.14 | 240-56030406 3.6.1.3 | Protection CT: type, class and ratio | T_ C_ R | xxxxxxxx | ________ |
| 5.15 | 240-56030406 3.6 & 3.6.1.2 a) | Detail the supply requirements to power up SPR for single and Three Phase conditions | A | xxxxxxxx | ________ |
| 5.16 | 240-56030406 3.6.2 | SPR to include additional functionality for communication of Analogues to IRTU | Y/N | N | xxxxxxxx |
|  |  | Protection IED required for IRTU application. | Y/N | N | ________ |
|  | 240-56030406 3.6, 3.6.3.1- 3.6.3.12 | Protection functional requirements satisfied, i.e. functions, setting ranges, characteristic curves etc. (provide technical manual). |  | xxxxxxxx | ________ |
|  | 240-56030406 3.7 | Current sensors- type, class and ratio | T_ C_ R_ | xxxxxxxx | ________ |

|  | 240-56030406 3.8 | Voltage sensors- type, class | T_ C_ | xxxxxxxx | ________ |
| --- | --- | --- | --- | --- | --- |
| 6 | SANS 1874 4.8 | Cable termination enclosure of the circuit breaker functional units |  |  |  |
| 6.1 | 240-56030406 3.13d)/ ,e)/ & f) | Spacing between bushing centres (min) | mm | 90 | ________ |
| 6.2 | 240-56030406 3.13d)/ ,e)/ & f) | Spacing between outer bushing centres and enclosure side wall (min) | mm | 55 | ________ |
| 6.3 | SANS 1874 4.8 | Distance from bushing centre line to cable support clamp (min). The cable support clamp shall be mounted above any bottom enclosure mounted plates for 3 core cable termination applications. For 1 core cable termination applications where bottom plates are required to be mounted above the cable clamps for Internal Arc venting compliance, the plate shall be positioned to meet the SANS 876 requirement for a 22 kV voltage rating single core cable termination to be fitted. | mm | 800 | ________ |
| 6.4 | SANS 1874 4.8 | Bushings horizontally positioned? | Y/N | YES | ________ |
| 6.5 | SANS 1874 4.8.4 | Type of bushing |  | EN 50181 C-type interface | ________ |
| 6.6 | SANS 1874 4.11.4 | Cross sectional area of earthing bar (min) | mm2 | 120 | ________ |
| 6.7 | SANS 1874 4.8.6 | Type of cable support clamp |  | SANS 876 / |  |
|  |  |  |  | D-DT-8019 / 24056062752 | ________ |
| 6.8 | 240-56030406 3.13g) | Size (range) of cable support clamp (3 Core Cable applications) | mm | 50-100 | N/A |

| 6.9 | 240-56030406 3.13 g) | Size (range) of cable support clamps (3 * 1 Core Cable applications) |  | Xxxxxxxx | ________ |
| --- | --- | --- | --- | --- | --- |
|  |  | General |  |  |  |
| 7 | SANS 1874 4.7 | Busbars |  |  |  |
| 7.1 | SANS 1874 4.7.2 | Current rating of Busbars | A | 630 | ________ |
| 7.2 | SANS 1874 4.7.2 | Busbars to be extensible left or right? | L / R /NA | N/A | xxxxxxxx |
| 7.3 | SANS 1874 4.7.3 | Method of extending Busbars |  | Xxxxxxxx | xxxxxxxx |
| 7.4 | SANS 1874 4.7.5 | Extensible Busbar insulating medium |  | Xxxxxxxx | ________ |
| 8 |  | IRTU |  |  |  |
| 8.1 | SANS 1874 4.9.2 | RTU to be provided? | Y/N | No | xxxxxxxx |
| 8.2 | SANS 1874 4.9.2.1 | Provision for remote status indications and alarms required? | Y/N | No | xxxxxxxx |
| 8.3 | SANS 1874 4.9.2.1 | Local indications to be provided? | Y/N | No | xxxxxxxx |
| 8.4 | SANS 1874 4.9.2.3 | D.C. voltage? | 110V/24V | N/A | ______ |
| 8.5 | 240-56030406 3.12 a) | External LV supply for RTU? |  | 230V AC | xxxxxxxx |
| 8.6 | 240-56030406 3.12 b) | Dual Phase VT required for LV Auxiliary power supply (in addition to external LV Power supply) | Y/N | No | xxxxxxxx |
|  | 240-56030406 3.12 b) | Details of Dual Phase VT – VA and Voltage Factor | VA & VF | xxxxxxx | ________ |
|  | 240-56030406 3.9 b) | Battery supply specified minimum discharge voltage | V | xxxxxxx | ________ |
|  | 240-56030406 3.9 | Minimum battery capacity after 4 years | % | >80 | xxxxxxxx |
|  | 240-56030406 3.9 | 100% depth of discharge cycles over 4 years | cycles | >200 | xxxxxxxx |
| 9 | SANS 1874 4.10 | Gas requirements |  |  |  |

| 9.1 | SANS 1874 4.10.2 | Expected life before replenishment of gas (minimum) | Years | 30 | ________ |
| --- | --- | --- | --- | --- | --- |
| 9.2 | SANS 1874 4.10.3 & 24056030406 3.13 | Type of gas indication device |  | Density meter | ________ |
| 9.3 | SANS 1874 4.10.5 | Mass of gas: |  |  | ________ |
| 9.3 | SANS 1874 4.10.5 SANS 1874 4.10.6 | a) Busbar chamber | kg | Xxxxxxxx | ________ |
|  |  | b) Other | kg | Xxxxxxxx | ________ |
|  |  | Service offered for replenishment and recovery of gas |  | Xxxxxxxx | ________ |
| 10 10.1 | SANS 1874 4.11 | Earthing |  |  | ________ |
|  | SANS 1874 4.11.1 | Earth fault level and duration | kA-s | 2 kA – 3 s | ________ |
| 11 11.1 |  | Live circuit indication |  |  | ________ |
|  | SANS 1874 4.12.4 24056030406 3.14 | Type of live circuit indication required |  | VDS | ________ |
| 12 | SANS 1874 4.13 | Earth fault indication |  |  |  |
| 12.1 | SANS 1874 4.13.1 | Type of earth fault indicator |  | Self- Powered via internal CT | ________ |
| 12.2 | SANS 1874 4.13.1 SANS 1874 4.13.6 | Earth fault indicator details: |  |  | ________ |
|  |  | a) Cable box location for CT |  | LHS ‘R’ | ________ |
| 12.3 | SANS 1874 4.13.7 | b) Position of ‘remote’ indicator |  | Visible from outside, front of Mini-sub | ________ |
| 12.4 | SANS 1874 4.13.7 | c) Method of protecting indicator against vandalism |  | Welded steel tube | ________ |
| 12.5 | SANS 1874 4.13 | Make of earth fault indicator |  | Xxxxxxxx | ________ |
| 12.6 | SANS 1874 4.13 | Type (model) of earth fault indicator |  | Xxxxxxxx | ________ |
| 13 | SANS 1874 4.17 | Rating plate |  |  | ________ |
| 13.1 | SANS 1874 4.17.1 | Method of attaching rating plate |  | Xxxxxxxx | ________ |
| 14 | SANS 1874 4.18 | Marking and labelling |  |  |  |
| 14.1 | SANS 1874 4.18.1.1 | Method of attaching labels |  | Xxxxxxxx | ________ |
| 14.2 | SANS 1874 4.18.2.1 | Method of fixing and removal of main circuit designation labels for engraving purposes |  | Xxxxxxxx | ________ |
| 14.3 | SANS 1874 4.18.4.4 | Mimic indication system required? | Y/N | Yes | xxxxxxxx |
| 14.4 | SANS 1874 4.18.4.4 | Description of mimic indication system |  | Xxxxxxxx | ________ |
| 14.5 |  |  |  |  |  |
| 14.6 | SANS 1874 4.18 & 24056030406 3.19 | Corrosion protection |  |  |  |
| 14.7 | SANS 1874 4.18 & 24056030406 3.19 | Application with regard to corrosion protection i.e. inland or coastal |  | Coastal | ________ |
| 14.8 | SANS 1874 4.18.9 | Type of material offered: |  |  |  |
| 14.9 | SANS 1874 4.18.9 | a) Ring main unit gas enclosure |  | Xxxxxxxx | ________ |
|  |  | b) Cable termination enclosures and frame |  | Xxxxxxxx | ________ |
|  |  | c) Operating mechanisms |  | Xxxxxxxx | ________ |
| 15 |  | Testing |  |  |  |
| 15.1 | SANS 1874 5.1.3 | Origin of RMU design |  | Xxxxxxxx | ________ |

| 15.2 15.3 15.4 15.5 | SANS 1874 5.1.3 |  | Origin of Vacuum Interrupter design |  | Xxxxxxxx | ________ |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Origin of CT design |  | Xxxxxxxx | ________ |
|  |  |  | Origin of VT design |  | Xxxxxxxx | ________ |
|  |  |  | Origin of IRTU design |  | Item specific | ________ |
|  |  |  | Place of RMU manufacturer |  | Xxxxxxxx | ________ |
| 15.6 15.1 15.2 15.3 | SANS 1874 5.1.3 |  | Place of Vacuum Interrupter manufacturer |  | Xxxxxxxx | ________ |
|  |  |  | Place of CT manufacturer |  | Xxxxxxxx | ________ |
|  |  |  | Place of VT manufacturer |  | Xxxxxxxx | ________ |
|  |  |  | Place of IRTU manufacturer |  | Item specific | ________ |
|  |  |  | Number of RMU units supplied in South Africa |  | Xxxxxxxx | ________ |
| 15.4 | SANS 1874 5.2.3 |  | RMU Internal arc type test details |  | Xxxxxxxx | ________ |
| 15.5 | SANS 1874 5.2 |  | RMU type test reports |  | Yes | xxxxxxxx |
| 15.6 | 240-56030406 3.21 3.22 | and | RMU type test reports and videos |  | Yes | xxxxxxxx |
|  | 240-56030406 3.6.4 e) |  | CT type test reports |  | Yes | xxxxxxxx |
|  | 240-56030406 3.6.5 f) |  | VT type test reports |  | Yes | xxxxxxxx |
|  | 240-64685228 4. |  | SPR Type test report |  | Yes | xxxxxxxx |
|  | 240-64685228 4. |  | Protection IED Type test report |  | Yes | xxxxxxxx |
| 16 |  |  | Spares |  |  | ________ |
| 16.1 | SANS 1874 6.1 |  | List of recommended spares |  | Xxxxxxxx | ________ |
| 17 | SANS 1874 7.2 |  | Documentation |  |  |  |
| 17.1 | SANS 1874 7.2 |  | Drawing numbers submitted: |  | Xxxxxxxx | ________ |

| 17.2 | SANS 1874 7.2 |  | General assembly drawing(s) |  |  |  | Xxxxxxxx | ________ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 17.3 | SANS 1874 7.2 |  | Drawing(s) showing mimic indication system, tee-off operating procedure, other labels & signs |  |  |  | Xxxxxxxx | ________ |
| 17.4 | SANS 1874 7.2 |  | Wiring diagram(s) |  |  |  | Xxxxxxxx | ________ |
| 17.5 | SANS 1874 7.2 |  | Rating plate drawing |  |  |  | Xxxxxxxx | ________ |
| 17.6 | SANS 1874 7.2 |  | Tabulated summary of completed type tests required? |  |  | Y/N | Yes | ________ |
| 17.7 | SANS 1874 7.2 |  | Full set of type test reports required? |  |  | Y/N | Yes | ________ |
| 17.8 | SANS 1874 7.2 |  | Proof of type test laboratory accreditation? |  |  | Y/N | Yes | ________ |
| 17.9 | SANS 1874 7.2 |  | Copy of RMU factory routine test certificate? |  |  |  | Yes | ________ |
| 17.10 | SANS 1874 7.2 |  | Copy of CT and VT factory routine test certificate? |  |  | Y/N | Yes | ________ |
| 17.11 | SANS 1874 7.2 |  | Copies of the latest technical catalogue(s) including SPR and protection relay and/or electronic ammeter/multi-meter technical manual (if applicable)? |  |  | Y/N | Yes | ________ |
| 17.12 | SANS 1874 7.2 |  | Number of installation, operation and maintenance manuals to be provided with the tender |  |  |  | 1 | ________ |
|  | SIGNATURES |  |  |  |  |  |  |  |
|  | Supplier | Name (Print) |  |  | Sign |  |  | Date |
|  | Factory | Name (Print) |  |  | Sign |  |  | Date |
|  | Eskom | Name (Print) |  |  | Sign |  |  | Date |