# Part 3: Scope of Work

| Document reference | Title | No of pages |
| --- | --- | --- |
|  | This cover page | 1 |
| C3.1 | Employer’s Works Information | 299 |
| C3.2 | Contractor’s Works Information (insert at award stage or delete if not applicable) | 1 |
|  | Total number of pages | 299 |

Contents

Part 3: Scope of Work	1

1	Description of the works	9

1.1	Executive overview	9

1.2	Employer’s objectives and purpose of the works	11

1.2.1	Interface with Others	12

1.3	Interpretation and terminology	19

2	Management and start up.	23

2.1	Management meetings	23

2.2	Documentation control	25

2.2.1	Document Control and Configuration Management	25

2.2.2	Plant Coding and Labelling	29

2.3	Health and safety risk management	30

2.3.1	Safety of Worker	31

2.3.2	Fire Protection	31

2.3.3	First Aid	32

2.3.4	Housekeeping	32

2.3.5	Barricading	32

2.3.6	Radiographic Examinations	32

2.3.7	Permit to Work System	32

2.4	Environmental constraints and management	32

2.5	Quality assurance requirements	33

2.5.1	General	33

2.5.2	Quality Management documents requirements	33

2.5.3	Quality Responsibility	34

2.5.4	Inspections	35

2.5.5	Non Conformances and Defects	35

2.5.6	Quality Reporting	36

2.6	Programming constraints	37

2.6.1	Construction Constraints	37

2.6.2	Computerised Planning	38

2.6.3	Planning Methodology and Programme Levels	38

2.6.4	Planning Schedules	39

2.6.5	Time Analysis	41

2.6.6	Reporting on Remaining Duration	42

2.6.7	Actual Dates	42

2.6.8	Progress Reporting during Provision of the works	42

2.6.9	Daily Progress Report	42

2.6.10	Weekly Progress Report	43

2.6.11	Monthly Progress Report	43

2.6.12	Planner Requirements	44

2.7	Contractor’s management, supervision and key people	44

2.8	Invoicing and payment	44

2.8.1	General	44

2.8.2	Foreign Portion Invoicing	45

2.8.3	Import Invoices	45

2.9	Insurance provided by the Employer	45

2.10	Contract change management	46

2.10.1	Contract changes and contract Scope	46

2.10.2	Administrative changes	46

2.10.3	Substantive changes	46

2.10.4	General Principles of contract change management	46

2.10.5	Costs	47

2.10.6	Impact Assessment	47

2.10.7	Project Manager’s right of acceptance of contract changes	47

2.10.8	Contractor’s right of acceptance of proposed changes	48

2.10.9	Emergency Instruction contract changes	48

2.10.10	Authorisation of contract change	48

2.10.11	Communications	48

2.11	Provision of bonds and guarantees	49

2.12	Records of Defined Cost, payments & assessments of compensation events to be kept by the Contractor	49

2.13	Training workshops and technology transfer	49

3	Engineering and the Contractor’s design	50

3.1	Employer’s design	50

3.1.1	Existing Plant	50

3.1.2	Employer’s design requirements of the works	58

3.1.3	Excluded from the works	63

3.1.4	Re-use of existing plant	64

3.1.5	Performance Requirements	64

3.1.6	Operating Philosophies	67

3.1.7	Control Philosophy	80

3.1.8	Reliability Philosophy	80

3.1.9	Employer’s design of the DHP and Hopper control air compressor house building and unitised blower house buildings	81

3.1.10	Updating the Employer’s Design	106

3.2	Parts of the works which the Contractor is to design	106

3.2.1	Mechanical	107

3.2.2	HVAC	114

3.2.3	Electrical	115

3.2.4	Control and Instrumentation	119

3.2.5	Civil engineering and structural works	125

3.2.6	Equipment	127

3.2.7	Compressor House building fire protection and detection	127

3.2.8	Overhead travelling crane for Compressor House	129

3.2.9	Temporary works	130

3.3	Procedure for submission and acceptance of Contractor’s design	130

3.3.1	2D Drawings and 3D Models	131

3.3.2	Design Review Documentation	131

3.3.3	Engineering Change Procedure	133

3.3.4	Process for Submission of Documents	133

3.3.5	Time Required for Acceptance of Designs	133

3.4	Other requirements of the Contractor’s design	134

3.4.1	Process Design Information	134

3.4.2	Ash Specification	134

3.4.3	Effluent Water	137

3.4.4	Precipitator Plant	138

3.4.5	Hopper Aeration System	140

3.4.6	DHP	140

3.4.7	Compressed Air System	141

3.4.8	Conditioning Plant	142

3.4.9	HVAC	142

3.4.10	Additional requirements	142

3.5	Use of Contractor’s design	145

3.6	Design of Equipment	145

3.7	Equipment required to be included in the works	145

3.7.1	Special Tools and Equipment	145

3.8	As-built drawings, operating manuals and maintenance schedules	146

3.8.1	Manuals	146

3.8.2	Operating, Maintenance and Engineering Documentation	147

3.8.3	As-Built Drawings	149

3.8.4	LV Switchgear	150

3.8.5	Motors	151

4	Procurement	153

4.1	People	153

4.1.1	Minimum requirements of people employed on the Site	153

4.1.2	BBBEE and preferencing scheme	153

4.1.3	Skills Development, Local Content and Local Production	154

4.2	Subcontracting	155

4.2.1	Preferred subcontractors	155

4.2.2	Subcontract documentation, and assessment of subcontract tenders	157

4.2.3	Limitations on subcontracting	157

4.2.4	Attendance on subcontractors	158

4.3	Plant and Materials	158

4.3.1	Quality	158

4.3.2	Plant & Materials provided “free issue” by the Employer	158

4.3.3	Contractor’s procurement of Plant and Materials	158

4.3.4	Spares and consumables	158

4.4	Tests and inspections before delivery	158

4.4.1	Inspection and Testing	159

4.5	Marking Plant and Materials outside the Working Areas	159

4.6	Contractor’s Equipment (including temporary works).	160

4.7	Civil and structural contractor/subcontractor CIDB designation	160

5	Construction	161

5.1	Temporary works, Site services & construction constraints	161

5.1.1	Employer’s Site entry and security control, permits, and Site regulations	161

5.1.2	Restrictions to access on Site, roads, walkways and barricades	161

5.1.3	People restrictions on Site; hours of work, conduct and records	161

5.1.4	Health and safety facilities on Site	161

5.1.5	Environmental controls, fauna & flora, dealing with objects of historical interest	161

5.1.6	Title to materials from demolition and excavation	161

5.1.7	Cooperating with and obtaining acceptance of Others	161

5.1.8	Publicity and progress photographs	163

5.1.9	Contractor’s Equipment	163

5.1.10	Equipment provided by the Employer	164

5.1.11	Site services and facilities	164

5.1.12	Facilities provided by the Contractor	164

5.1.13	Existing premises, inspection of adjoining properties and checking work of Others	166

5.1.14	Excavations and associated water control	166

5.1.15	Underground services, other existing services, cable and pipe trenches and covers	166

5.1.16	Control of noise, dust, water and waste	167

5.1.17	Sequences of construction or installation	167

5.1.18	Giving notice of work to be covered up	167

5.1.19	Hook up to existing works	167

5.2	Completion, testing, commissioning and correction of Defects	167

5.2.1	Work to be done by the Completion Date	167

5.2.2	Use of the works before Completion has been certified	168

5.2.3	Materials, facilities and samples for tests and inspections	168

5.2.4	Commissioning	168

5.2.5	Start-up procedures required to put the works into operation	171

5.2.6	Take over procedures	171

5.2.7	Performance tests after Completion	171

5.2.8	Training and technology transfer	174

5.2.9	Operational maintenance after Completion	176

6	Plant and Materials standards and workmanship	177

6.1	Civil Specification	177

6.1.1	Investigation	177

6.1.2	Survey control and setting out of the works	177

6.1.3	SANS 2001 BS1: Site clearance	178

6.1.4	SANS 2001-BE1: Earthworks	180

6.1.5	Building works	182

6.1.6	SANS 2001 CC1: concrete works (structural)	191

6.1.7	SANS 2001 CS1: Structural steelwork	195

6.2	Mechanical engineering works	200

6.2.1	Air and Water Piping	200

6.2.2	Hopper Aeration System	201

6.2.3	DHP (Drawings 0.61/96025, 0.61/96026)	204

6.2.4	Instrument Air System (Drawings 0.61/96027 Sheets 1 – 6, 0.61/96028 Sheets 1 – 3, 0.61/97205)	206

6.2.5	Conditioning Plant (Drawings 0.61/96075, 0.61/96078, 21.61 55242 Rev. 3)	211

6.2.6	Valves	220

6.2.7	Fire Protection and Detection	221

6.2.8	HVAC	224

6.2.9	Fuel Oil Piping	237

6.3	Electrical Engineering Works	239

6.3.1	Voltage Levels	239

6.3.2	Cabling and Racking	239

6.3.3	Low Voltage Switchgear	241

6.3.4	Low Voltage Motors	242

6.3.5	Transformers	243

6.3.6	Lighting and Small Power	244

6.3.7	Earthing and Lightning Protection	244

6.3.8	Essential Power Supplies	245

6.3.9	Variable Speed Drives (VSD’s)	246

6.4	Control and Instrumentation Works	246

6.4.1	Overall System Technical Requirements	246

6.4.2	Control System	250

6.4.3	Field Equipment and Cabling	255

6.4.4	C&I Power Supply Requirements	256

6.4.5	Impulse Piping & Accessories	257

6.4.6	The Simulator Plant Requirements	257

6.4.7	Licenses	257

6.4.8	C&I Training Requirements	257

6.5	Process control and IT works	257

6.6	Constructability, Supportability, Operability, Reliability, Availability and, Maintainability	258

6.6.1	Supportability	258

6.6.2	Reliability, Availability and Maintainability (RAM)	258

6.6.3	Technical Risk Assessments	263

7	List of drawings	265

7.1	Drawings issued by the Employer	265

Appendix A – Required Deliverable for the Contractor	274

Appendix B – Vendor Document Submittal Schedule (VDSS)	275

Appendix C – Limits of Supply and Services (LOSS)	276

Appendix D – Employers RBO Template	277

Appendix E – Applicable Standards	278

Appendix F – Stock Item Forms	283

Appendix G – PM Change Form	284

Appendix H – Master Document list (MDL)	285

Appendix I – Control Philosophy and Functional Description	286

Appendix J – Control and Instrumentation Templates to be used by the Contractor.	287

Appendix K – Terminal Point Register	288

Appendix M – Training Manual Template	289

Appendix N – HVAC Equipment Specification Schedule	290

Appendix O – Detailed Design Report Template	291

Appendix P – Additional Electrical Schedules	292

Appendix Q – CADD Design Tool Deliverable Required from the Contractor	293

Appendix R – Electrical Project Drawings	295

Appendix S – Tutuka Instructions to Tender, DHP Unit 4-6 Field Equipment and DCS	298

C3.2	Contractor’s Works Information	299

# Description of the works

## Executive overview

Tutuka Power Station (P.S.) is situated near the town of Standerton in Mpumalanga, South Africa. The coordinates of the power station are 26°46′43″S, 29°21′07″E. It is a coal fired power station with six (6) generating units of 609 MW each. The first unit was commissioned in July 1985 and has a 50 year life, the decommissioning of the first unit (Unit 1) is expected to be in 2035 and the last unit (Unit 6) decommissioned in 2041.

Tutuka P.S. currently utilises Electrostatic Precipitators (ESP’s) to clean the boiler flue gasses. Each boiler has two (2) ESP casings and both must be in operation to achieve maximum boiler load.

The current design of the ESP’s is not able to meet the future particulate emission licence limits as set by the Department of Environmental Affairs (DEA) of South Africa. To reduce the current particulate emissions and to meet the new licence limits of 50 mg/Nm3 the existing ESP’s will be upgraded with High Frequency Transformers and SO3 injection technologies utilising the existing ESP casings. All the ESP internals will be replaced with new internals.

To support the upgrading of the existing ESP’s and DHP for two units at Tutuka P.S, the following is completed as part of the works:

- Design, supply and installation of a hopper aeration air system.

- Design, supply and installation of instrument air supply system.

- Design, supply and upgrading of the existing DHP.

- Design, supply and upgrading of the ash conditioning plant.

- Construction of the two (2) unitised blower houses.

- Design, supply, installation and construction of the instrument air compressor house.

- Design, supply and install electrical work associated with the upgraded DHP, hopper aeration system, instrument air system and conditioning plant.

- Design, supply and install C& I plant systems associated with the upgraded DHP, hopper aeration system, instrument air system and conditioning plant.

The Contractor scope of work includes but is not limited to:

- The Contractor is responsible for detail design, procurement, manufacture, quality control, corrosion protection, handling, shipment and transport to/from site, all storage requirements, unloading, preservation construction and erection, painting and finishing, installation, commissioning, testing, training, optimisation and handover of the works for a fully operational and functional plant (including; C&I, electrical, mechanical and civil/structural).

- The Contractor is responsible for dismantling, decommissioning and removal of all associated redundant equipment which will not be utilised by the works (including the auxiliary systems such as C&I and electrical) unless otherwise stated. Material and systems are removed to an area specified by the Employer. (Including removal of scrap material).

- The Contractor ensures Integration engineering with other projects executed by Others during the same outages is conducted.

- The works is designed for constructability, supportability, operability, availability, reliability, accessibility and maintainability.  (This includes the development of RAM, FMECA and HAZOP studies).

- The Contractor integrates the works with the existing power station systems and liaises with the original suppliers of the related plant to ensure the compatibility of operation of the existing systems with the works.

- The Contractor develops all engineering calculations, 3D models, inspection/quality reports, construction records, commissioning test reports, and other documentation as specified in the Works Information.

  - The final design submitted by the Contractor is in SmartPlant.

- The Contractor supplies detailed drawings and documentation specified in the Works Information.

- The Contractor develops an Integrated Design Report (IDR) (in the template included in Appendix O) containing all the design information for all disciplines (e.g. Mechanical, C&I, Electrical, Civil, etc.) that is reviewed and accepted by the Project Manager as per the Employers Design Review Procedure 240-53113685.

- The Contractor supplies as a minimum maintenance, operation and training manuals.

- The Contractor develops a maintenance plan for the works documented in the Tutuka P.S. RBO format included in Appendix D.

- The Contractor develops a control and operating philosophy for the works.

- The Contractor provides all documentation/drawings in accordance with the Vendor Document Submittal Schedule (VDSS) which is included in Appendix B.

- The Contractor documents all documentation sent to the Project Manager in the Master Document List (MDL) template as provided by the Employer in Appendix H.

- The Contractor provides technical oversight during fabrication and construction.

- The Contractor provides training to the Employers engineering, operating and maintenance staff including the development of all training materials.

- The Contractor provides any other Plant and Materials or items associated with the works.

- The Contractor supplies and installs AKZ labelling as specified in the Works Information.

- The Contractor provides all Equipment (including scaffolding and cranage) requirements for construction of the works.

- The Contractor reviews and revises the current light up procedures which may require changes to plant settings as a result to the DHP upgrade project. The Contractor submits these to the Project Manager for acceptance.

## Employer’s objectives and purpose of the works

The objectives and purpose of the works are:

- Install a hopper aeration system (including the C&I and electrical systems to support it) to improve the flow ability of the ash from the ESP hoppers.

- The Power Station Load factor for the remaining life of the station is approximately 30% and the maximum ash load per boiler should be 61 tons per hour and the back log recovery is then 80 tons per hour per one boiler. Upgrade the existing DHP with the same technology (En-Masse conveying system), C&I and electrical systems to support it) that can operate at the following capacities:

  - Normal  - 61 Tph

  - Backlog – 80 Tph

- Install twelve (12) new conditioners (including the C&I and electrical systems to support them) in the conditioning plant to improve redundancy (two (2) conditioners per ash bunker to four (4) conditioners per ash bunker). The capacity of each of the conditioners is 200 Tph (wet at a 20% moisture content). All conditioner auxiliaries (e.g. conditioning water supply, etc.) are upgraded such that they are aligned to the new requirements of the conditioners.

- The availability and reliability of the works is maximised. The minimum availability achieved is 98%.

### Interface with Others

The Contractor is responsible for designing the works for interfaces with Others including time considerations. The Contractor provides the Project Manager with requirements such as power requirements, termination interface requirements, and design philosophies in order for him to complete the design and installation of the works.

The interface documentation created by the Employer is used by the Contractor. These include the limits of supply and services (LOSS Diagrams) in Appendix C and Terminal Point Register in Appendix K. Terminal Point Register and Terminal Point Data sheets (if required) are populated by the Contractor and supplied to the Project Manager.

The following is a summary of the interfaces:

Table 1 Summary of Interfaces

| ## System | ## Interface |
| --- | --- |
| Ash bunker venting | The Contractor is responsible for the connection point for the vent pipe to the ash bunker venting dome at the ash bunker roof. |
| Precipitator Hoppers | The Contractor is responsible for any modifications to the Precipitator hoppers for the hopper aeration system, The hoppers are the responsibility of Others. The terminal point at the outlet of the hopper between the Contractor and Others is the hopper outlet chute. The hopper discharge flanges and the slide gate valves are in the Contractors scope. |
| Fire Water | The Contractor is responsible for connecting all new fire hydrants and sprinklers to the existing fire ring main. The Contractor is responsible for the construction and modifications required to the existing fire ring main to ensure that the new fire hydrants and sprinklers are integrated with the existing fire ring main. |
| Building Management System (BMS) | The Contractor is responsible for the fire detection system design and PA/telephone system in the new blower and instrument air compressor houses and all the interfaces to the existing BMS (Building Management System) |
| Precipitator hoppers blower houses | The blower houses for the precipitator hoppers aeration air systems is constructed by the Contractor but is designed by the Employer. The HVAC, earthing and lightning protections are designed by the Employer and supplied and installed by the Contractor. The overhead crane girder and lighting and small power is designed, supplied and installed by the Contractor. |
| Hoppers/Conditioners common Instrument air compressor house | The instrument air compressor house for the ash hopper aeration air supply valves controls and ash conditioner instrument compressed air systems is designed, supply, installed and constructed by the Contractor. The HVAC and earthing and lightning protection are designed by the Employer and supplied and installed by the Contractor. The overhead crane girder and lighting and small power is designed, supplied and installed by the Contractor. The ash hoppers/conditioners instrument compressed air equipment (including cabling and cable racking) is designed, supplied, installed by the Contractor. |
| Electrical | The Contractor is to design, select, supply, install, terminates the MV transformer and terminates all cables on the primary side of the MV to LV transformer. The Contractor pulls all cables to the respective MV supply points. The termination on the MV switchgear is conducted by the Contractor. |
| Control and Instrumentation (C&I) | The Contractor provides all instruments, drives and actuators, switchgear interfacing, LCS, local PLC’s, junction boxes where necessary as well as field cabling and terminates field cabling in the localised junction boxes/enclosures for Unit 1 - 3 and interfaces with Others to realise a complete functional system The Contractor provides all instruments, drives and actuators, switchgear interfacing, LCS, local PLC’s where necessary as well as field cabling and terminates field cabling in the localised junction boxes/enclosures, installs and pulls trunk cabling up to DCS including the termination and logic implementation at the new DCS cubicles provided by the Contractor for Unit 4 – 6. The Contractor designs and implements a HMI mimics and ensures correct interface to the PIS for Unit 4 – 6. The Contractor provides all instruments, drives and actuators, switchgear interfacing, LCS, local PLC’s where necessary as well as field cabling and terminates field cabling in the localised junction boxes/enclosures, installs and pulls trunk cabling up to new DCS including the termination and logic implementation at the new DCS cubicles provided by the Contractor for the common plant (OPCR). The Contractor designs and implements a HMI mimics and ensures correct interface to the PIS for common pant (OPCR). The Contractor is responsible for the C&I interface of the water supply effluent plant system to the water treatment plant control room. The Contractor provides all instruments, drives and actuators, switchgear interfacing, LCS where necessary as well as field cabling for the water supply effluent plant system. The Yokogawa DCS version upgrade to reversion 6 that would enable the expansion of the control system is planned for execution on 03/10/2022 and the completion date is 27/03/2023. |
| Potable water | The Contractor is responsible for connecting to the outlet of the existing potable water tank and routing a potable water pipeline to the DHP blower house and Instrument air compressors. The Contractor also provides a tapping point for Others at the DHP hoppers Blower and Instrument air houses. |
| Demineralised Water | The Contractor is responsible for connecting to the outlet of the existing demineralised water manifold, supplying an isolation valve and routing a demineralised water pipeline to the ash hoppers and conditioner instrument air compressor house. The Contractor also provides a tapping point for Others at the Instrument Air Compressor house. |
| DHP Venting system | The Contractor is responsible for the DHP and ash conditioning venting systems from the plant to the ash bunkers. |
| Bunker Aeration System | The Contractor includes the air requirements for the bunker aeration system in the ash bunkers aerations system blowers. The Contractor to supply and install one additional aeration air blower with its piping and controls. The Contractor is responsible for the aeration pads and the piping supplying air to the conditioners. |
| Ash bunker | The ash bunker structure falls within the scope of the Contractor. All modifications required to the bunker, (including any modification to any of the cast in flanges on the roof) are the responsibility of the Contractor. The level sensors (including its cast in flange) are the responsibility of the Contractor. The cast in flange for the outlet to each conditioner is the responsibility of the Employer, the slide gate mounted to the cast in flange is the responsibility of the Contractor. |
| Conditioner Conveyor | The Contractor is responsible for the conditioner conveyor with its moving heads and bottom chutes, which feed the downstream conveyors. |
| Conditioning/Scrubbers Water Supply | The conditioning water is supplied from the Tutuka P.S, effluent sump. The effluent water suction manifolds, pumps, discharge manifolds, common piping, flow meters and valves are the responsibility of the Contractor and the piping interfacing to the outlet flanges of the effluent water sump and isolating valves are the responsibility of the Contractor The conditioner emergency potable water supply is supplied from the Air Heater Washing Potable Water Tank, the isolation valve on the existing potable water piping, where it ties into the conditioning water supply piping is the responsibility of the Contractor. The ash conditioner effluent water supply and water flow rate controls for the ash conditioners and scrubbers are the responsibility of the Contractor. |
| Pipe Supports | The Contractor supplies the pipe supports for all the Precipitator hoppers aeration air piping, instrument air pipes and valves towards each pneumatic actuators for the hopper aeration air supply, conditioners water supply, conditioners aeration air supply, air scrubbers water supply, conditioner instrument air supply, conditioner airslides, blower houses fire protection systems, instrument air compressor house fire protection systems and for the DHP venting system. The Contractor prepares the pipe support for the DHP hoppers aeration air piping and pipe clamps (and indicates the type of pipe clamps and connection bolts utilised) |
| Earthing | The Contractor is responsible for all earthing of the works as per the scope of the works and connecting it to the existing earth mat (see drawing 0.61/97195-2) of the station. The existing earthmat for the station will remain the responsibility of the Employer. The Contractor installs the earth mat for the 2 x ash hoppers blower houses. The Contractor installs an earth bar where he/she will interface with to earth the compressor equipment installed in the compressor house. |

## Interpretation and terminology

The following abbreviations are used in this Works Information:

| Abbreviation | Meaning given to the abbreviation |
| --- | --- |
| AAGC | Air Activated Gravity Conveyors |
| ABD | Availability Block Diagram |
| AC | Alternating Current |
| AFC | Approved For Construction |
| AHU | Air Handling Unit |
| AKZ | Anlangenkennzeichnungs |
| BMS | Building Management System |
| BTU | Battery Tripping Unit |
| DB | Dry Bulb |
| DC | Direct Current |
| DCS | Distributed Control System |
| DEA | Department of Environmental Affairs |
| DHP | Dust Handling Plant |
| C&I | Control and Instrumentation |
| CM | Configuration Management |
| CSF | Condensed Silica Fume |
| CSIR | Council for Scientific and Industrial Research |
| CW | Cooling Water |
| ESP | Electrostatic Precipitator |
| FA | Fly Ash |
| FAT | Factory Acceptance Test |
| FFP | Fabric Filter Plant |
| FMECA | Failure Mode, Effects and Criticality Assessment |
| GA | General Arrangement |
| GGBS | Ground Granulated Blast - Furnace Slag |
| GGCS | Ground Granulated Corex Slag |
| GO | General Outage |
| GPR | Ground Penetrating Radar |
| GPS | Global Positioning System |
| HAZOP | Hazardous Operation |
| HDPE | High Density Polyethylene |
| HMI | Human Machine Interface |
| HVAC | Heating, Ventilation and Air Conditioning |
| I/O | Input/Output |
| I.D. | Internal Diameter |
| ID | Induced Draft |
| IDR | Integrated Design Report |
| IED | Intelligent Electronic Device |
| ITP | Inspection and Test Plan |
| LAN | Local Area Network |
| LoSS | Limits of Supply and Services |
| LP | Low Pressure |
| LV | Low Voltage |
| m.a.m.s.l | meters above mean sea level |
| MDL | Master Document List |
| MDT | Mean Down Time |
| Mf | moisture free |
| MTBF | Mean Time Between Failure |
| MTTF | Mean Tim to Failure |
| MTTR | Mean Time to Repair |
| MV | Medium Voltage |
| MW | Mega Watt |
| N/A | Not Applicable |
| NB | Nominal Bore |
| OBL | Outside Battery Limits |
| O.D. | Outside Diameter |
| OEM | Original Equipment Manufacturer |
| OHS | Occupational Health and Safety |
| OPCR | Outside Plant Control Room |
| PA | Public Announcement |
| P&ID | Piping and Instrumentation Diagram |
| PF | Pulverised Fuel |
| PIS | Plant Information System |
| PM | Planned Maintenance |
| PMCC | Pensky–Martens Closed-Cup |
| Pr Eng | Professional Engineer |
| P.S. | Power Station |
| PVC | Polyvinyl Chloride |
| QA | Quality Assurance |
| QC | Quality Control |
| QCP | Quality Control Plan |
| RAM | Reliability, Availability and Maintainability. |
| RBO | Reliability Based Optimisation |
| RH | Right Hand |
| RPM | Revolutions per Minute |
| SCBC | Self Contained Battery Chargers |
| SWL | Safe Working Load |
| Tph | Tonnes per hour |
| UHMWPE | Ultra High Molecular Weight Polyethylene |
| UPS | Uninterruptible Power Supply |
| VDSS | Vendor Document Submittal Schedule |
| VSD | Variable Speed Drive |
| WB | Wet Bulb |

The following definitions are used in this Works Information:

| Term | Definition |
| --- | --- |
| Ash Product Flow Control Valve | The category of Ash Valves are all types of valves which operate (open or close) while in direct contact with fly ash with aeration air, this excludes slide gate valves, ball valves and butterfly valves.. |
| Blower Train | The Blower Train consists of the blower as well as all of the blower auxiliaries such as air heaters, silencers, filters, pressure relief systems, cooling systems, etc. |
| Compressor Train | The Compressor Train consists of the compressor as well as all of the compressor auxiliaries such as air dryers, silencers, filters, pressure relief systems, cooling systems, water traps etc. |
| Clearing | Clearing refers to the clearing and removal of all vegetation, including trees and shrubs to a height not exceeding 300 mm above the surrounding ground level including all loose vegetation. |
| Cold Commissioning | The period when individual items of the installation, electrical systems, control and instrumentation systems are checked and tested. |
| Conditioning System | The Conditioning System consists of conditioner, drive and ash vapour scrubber and conditioner conveyor. |
| Conveying Stream | A Conveying Stream consists of hopper chain conveyors which collects all the fly ash from all the ash hoppers and transfer it to the selected transfer chain conveyors and then the bucket elevator transfer this fly ash to the selected ash bunker compartment. |
| Dust Cover | The Dust Cover is a steel box fitted with skirting, which covers a conveyor belt between feed points to allow for any dust generated in the feeding process to settle and not be discharged to the surrounding area. |
| Grubbing | Grubbing refers to the removal and disposal of roots and stumps of trees and vegetation already cleared. |
| Sample | Samples are physical examples to illustrate materials, plant or workmanship, and to establish standards by which the work may be judged. |
| Sm3 | Sm3 refers to the volume of air at a temperature of 20°C and a pressure of 1 atm. |
| Special Tool | A Special Tool is regarded as any tool that is non-standard which would be required to be specially constructed for a specific purpose and is not commercially available. |
| Topsoil | Topsoil refers to the top 300 mm of the soil profile irrespective of the fertility appearance, structure, agricultural potential, fertility and composition of the soil. |
| DHP Blower House C&I Equipment room | This room houses C&I equipment such as remote I/O panels and it should be part of the boiler controls. |

# Management and start up.

## Management meetings

Meetings are held monthly between the Project Manager and the Contractor and any person instructed by the Project Manager to attend. The Contractor is represented at each meeting by the duly authorised member of the staff.  Additional ad hoc meetings may also be called to address urgent issues.

The Project Manager, as and when necessary, requires the Contractor to attend meetings with Others performing work onsite and during the same outage

The venue for these meetings is as determined by the Project Manager.  The Project Manager writes the minutes of meetings and circulates to attendees within five working days.

Any action of the Project Manager and the Contractor implied in the minutes of meetings is confirmed by a separate formal communication between the Project Manager and the Contractor.

The Contractor reports the overall progress and as a minimum requirement, the following is addressed:

- Contractor’s current activity progress and planned finish dates

- Contractor’s planned start and finish dates for the works

- Contractor and Project Manager’s programme agenda, current and projected manpower by class

- Health, safety and quality issues

- The progress of any other relevant activities

- Discussion on any technical and commercial issues

- Problem areas or concerns

Regular meetings of a general nature may be convened and chaired by the Project Manager as follows:

Table 2 :  Meetings Schedule

| Title and purpose | Approximate time & interval | Location | Attendance by: |
| --- | --- | --- | --- |
| Overall contract progress and feedback (from Contract Date to execution commencement ) | Monthly | Venue determined by the Project Manager | Project Manager, Contractor, Supervisor, and Others as determined by the Project Manager |
| Interface Meetings (including integration meetings with Others) | Weekly | Venue determined by the Project Manager | Project Manager, Contractor, Supervisor, Planners and Others as determined by the Project Manager |
| Planning Meetings (including integration meetings with Others) | Weekly | Venue determined by the Project Manager | Project Manager, Contractor, Supervisor, Planners and Others as determined by the Project Manager |
| Technical meetings | As and when required | Venue determined by the Contractor, Project Manager or the Employer | Project Manager and relavent parties. |
| Safety Meetings | Monthly | Venue determined by the Project Manager | Project Manager, Contractor, Supervisor Safety Officers and Others as determined by the Project Manager |
| Outage meetings (including integration meetings with Others) | Daily During outage | Venue determined by the Project Manager | Employer, Contractor, Supervisor, and Others as determined by the Project Manager |

Meetings of a specialist nature may be convened as specified elsewhere in this Works Information or if not so specified by the Project Manager/Supervisor are convened at times and locations to suit, the nature and the progress of the works. Records of these meetings are submitted to the Project Manager by the person convening the meeting within five days of the meeting. People attending meetings must have authority to make decisions and execute the decision.

All meetings are recorded using minutes or a register prepared and circulated by the person who convened the meeting.  Such minutes or register is not used for the purpose of confirming actions or instructions under the contract as these are done separately by the person identified in the conditions of contract to carry out such actions or instructions.

## Documentation control

### Document Control and Configuration Management

The documentation requirements cover the various engineering stages, from the design stage through fabrication, installation, testing and commissioning and most importantly for the operating, maintenance and training stage of the project.

The Contractor is responsible for the compilation and the supply of the documentation during the various project stages and to provide the documentation programme to link with the milestone dates.  Documentation and drawings are programmed for delivery to meet the milestone dates and in accordance with the agreed VDSS, attached in Appendix B.

The Contractor  provides the configuration management plan that will be implemented in line with the ISO 10007 Guidelines for Configuration Management. The CM plan should reflect where configuration management is in the project structure, a technical document and record management procedure as well as a change management procedure they will be using.

#### Documentation Pre-submission

The Contractor is responsible for the submission of the Vendor Documentation Submittal Schedule (VDSS) which lists all documentation deliverables for all work done by the Contractor as per the Works Information. The Employer in the Works Information lists minimum documentation deliverables which are utilised by the Contractor to develop/update the VDSS. The VDSS links with the completion of work as per the activities in the Accepted Programme and is submitted by the Contractor to the Project Manager for review and acceptance. Should the programme be revised, the updated VDSS must be submitted as per the revised programme.

#### Process for Documentation Submission

The layout and format of all documentation deliverables are in accordance with the Gx Projects Documentation Deliverable Requirements Specification (240-65459834) and Engineering Drawing Standard – Common Requirements (240-86973501). All documentation submitted are accompanied by the completed transmittal note with the following fields as a minimum: (Refer to 240-71448626 - Project Plant Specific Technical Documentation Transmittal Template.)

- Name of the Package

- Name of Contractor

- Transmittal Number

- Contractor Details

- Date of Submission

- Description of document

- Document Number

- Document revision

- Document type

- Document media type

- Number of copies

- Purpose of submission

- Document PBS

- Signed by and date

For review purpose, all documentation is submitted, by the Contractor, in native electronic format (as well as PDF) as described in Gx Projects Documentation Deliverable Requirements Specification (240-65459834), and all drawings as prescribed in the Engineering Drawing Standard – Common Requirements (240-86973501), Final documentation is submitted in both electronic (both PDF and native format) and hard copies to the Project Documentation Centre. The Contractor is to supply four (4) hard copies and electronic copies of all drawings, specifications, operating manuals and instructions that are required to maintain and operate the assembly prior to commissioning of the plant submission of documentation deliverables must be in accordance to the task completion or no later than 14 calendar days after completion of task as stipulated in the agreed VDSS Appendix B. The Contractor submits a sample of the incoming document transmittal note as stated in Section 2.2.1.2 Process for Documentation Submission.

The Contractor submits all documentation to the Project Manager as well as the Project’s Documentation Centre in the following media:

#### Electronic copies are submitted to Eskom Documentation Centre through the project’s email address (tutukaffp@eskom.co.za). The email subject as a minimum has the following: (Station_Project Name_Discipline_Subject).

#### The project’s Document Controller is copied on submission. Electronic copies that are too large for email is delivered on CD/DVD, large file transfer protocol and/or hard drives to the Project Documentation Centre.

#### All the submission by the Contractor are accompanied by the Transmittal note.

#### The Contractor signs and sends the transmittal note sent by the Project Manager back to him within 2 working days.

#### Documentation Recording

The Employer in the Works Information lists minimum documentation deliverables which are utilised by the Contractor to develop/update the VDSS. The Contractor develops; documents and maintains the Master Document List (MDL) with all the metadata which will be sent to the Project Manager as per the MDL template provided by the Employer in Appendix H.

The Contractor submits the MDL to the Project Manager on a monthly basis (10th of every month) for tracking purposes irrespective of whether there are updates or not. The MDL is a revisable document and it includes list of drawings and documents and contains the following minimum information for each document.

#### Date of submission

#### Transmittal number

#### Transmittal title

#### Document Title

#### Document number (Both Employer’s and Contractor’s)

#### Document Type

#### Revision number

#### Document Approval Status

#### Document Approval Date

#### Document Authorisation Status (i.e. Accepted With Comments, Not Accepted with Comments, Accepted)

#### Document Authorisation/Accepted Date

#### Transmittal Reason for Issue

In addition, the Contractor is provided with the following documents which must be adhered to:

#### Documentation Management Review and Handover Procedure for Gx Coal Projects (240-66920003).

#### Project Documentation Deliverable Requirement Specification (240-65459834).

#### Technical Documentation Classification ad Designation Standard (240-54179170).

#### Project / Plant Specific Technical Documents and Records Management Procedure (240-53114186)

#### Abbreviation Standard for Labelling of Plant at Power Station (GGS0443)

#### SmartPlant for Owner Operators (SPO) Documentation Metadata Standard (240-58552870)

#### SmartPlant Data Take-On Guideline (240-96659378)

#### Documentation Review and Turn-around

The Project Manager has a maximum of ten (10) calendar days to review and consolidate review comments for documentation submitted by the Contractor. The Contractor also has a maximum of (5) calendar days to respond and / rectify as per the comments by the Employer.

### Plant Coding and Labelling

Tutuka AKZ Coding Manual (15ENG MN-675) is used for coding of all Plant and Materials. AKZ coding is applied from the design stage and cross referenced accordingly (as a unique identification) to all documentation such as arrangement drawings, schematics, wiring diagrams, instructions and manuals and where practical to spare parts lists/manuals. References to specific Plant and Materials are accompanied by the relevant AKZ code for that item of the works.

#### The Contractor is responsible for the coding of all the works as set out in this document as well as equipment and components as per Employers coding standards, and the Contractor is responsible for supplying Project Manager with all the relevant documents/drawings. The Project Manager red lines all drawings/documents supplied with the codes generated by the Contractor.

The Contractor is fully familiar with the standards and concepts of the coding system as applied by the Employer. Contractor updates the drawings/documents upon receiving the red lined ones from the Project Manager. The Project Manager reviews the documents/drawings to ensure issued codification is incorporated correctly by the Contractor. The Project Manager accepts the documents if satisfied.

The Contractor ensures that the codes are applied in a uniform and consistent way and that all accepted codes allocated remains unique.

The Contractor provides the Project Manager with the following:

Outline drawings, P&I diagrams and equipment lists.

- In respect of items procured by the Contractor from another manufacturer or vendor, the Contractor provides the name of the actual manufacturer and his coded drawing or reference numbers and relevant technical data for identification purposes.

#### Plant Labelling

It is the responsibility of the Contractor to manufacture and install labels. Labels are manufactured and installed according to the Tutuka AKZ Plant Labelling Guideline (240-62937990, Rev 1).

Labelling includes the relevant AKZ code with English descriptions. The Contractor submits his approved Label Schedule/List spread sheet to the Project Manager for verification and acceptance, 60 days before commencement of manufacturing.  The label schedule includes the label information such as the AKZ code, full label description, positioning and designation.

The Contractor submits the sample of a manufactured label to the Project Manager to verify and check whether they conform to the Employers standard. If the manufactured labels are accepted by the Project Manager the Contractor continues with the manufacturing of labels.

Abbreviations to descriptions on the labels are generally not acceptable. Where abbreviations are unavoidable, due to the limited number of characters that can be engraved/etched on labels, the abbreviations are submitted to the Project Manager for acceptance.

All plant labels are installed on the Plant and Materials and the installation accepted prior to the commencement of commissioning and safety clearance.

## Health and safety risk management

- The Contractor at all times complies with applicable statutes and Eskom’s Business requirements which include but not limited to the following:  Occupational Health and Safety Act Number 85 of 1993 and its Regulations, Eskom SHEQ Policy, Standards, Procedures, Guidelines and Specifications.

- The Contractor ensures safety awareness at all times through continuous training.

- The Contractor is responsible for the supervision of his employees, agents and sub-contractors at all times, and takes full responsibility and accountability in ensuring that they are competent, compliant and aware of the legal requirements and other applicable requirements, and also executes the works in accordance with Construction Regulation, 2014 or as amended from time to time.

- The Contractor ensures that all statutory appointments and appointments required by any Eskom Policy, standard and procedure are recorded in writing and that all its appointees and/or agents fully understand their responsibilities and are trained and competent to execute their duties.

- The Employer, or any person appointed by the Employer, may, at any stage during the term of the contract:

  - Conduct health and safety audits by a competent person regarding all aspects of compliance with the SHEQ requirements, at any off-Site place of work, or the Site establishment of the Contractor.

  - Refuse any employee, sub-contractor or agent of the Contractor access to the premises if such person has been found to commit an unsafe act or if any work is found not to be compliant or authorized.

  - Issue the Contractor with a STOP WORK ORDER should the Employer become aware of any unsafe working procedure or condition, or any non-compliance.

- The Contractor immediately reports all incidents, as well as any threat to safety and health, of which he becomes aware at the Site, to the Project Manager.

- The Contractor agrees that the Employer is relieved of any and all of its responsibilities and liabilities in terms of the Occupational Health and Safety Act no 85 of 1993 in respect of any acts or omissions of the Contractor, and the Contractor’s employees, agents or sub-contractors, to the extent permitted by the Occupational Health and Safety Act no 85 of 1993.

- The Contractor provides a health and safety plan based on the Employer’s Safety, Health and Environmental Specification, GCD/TUT/SHE06.

- All persons entering the Site undergo the Employer’s safety induction course.

- The designer of the works is mandated to comply with section 6 of the construction regulations.

- In the event of any one of the following incidents occurring, an investigation shall be initiated and the Contractor status will be subjected to reconsideration by Supplier Status Committee:

- a supplier has one or more work-related fatalities within a financial year or the period of the project for contracts of less than one year;

- a supplier experiences three lost-time incidents in the same financial year;

- a supplier has three major SHE non-conformances raised in the same financial year;

- a supplier has had two or more contraventions of environmental legislation, including noncompliance with a condition contained in an environmental approval;

- the contractor has been issued with a compliance notice issued by a government department, for example, the Department of Labour, Department of Environmental Affairs, Department of Water Affairs, etc.;

- a violation of any of the Eskom Life-saving Rules occurs;

- Fraudulent SHE-related documents are submitted by a supplier.

### Safety of Worker

The Contractor ensures the safety of all persons working on the Site. Any hot work, including welding, is applied for in accordance with the permit to work system. No hot work is allowed on Site unless a hot work permit is granted by the Employer in writing.

### Fire Protection

The Contractor ensures that adequate firefighting apparatus is provided in all applicable areas where the works are being carried out and that his employees are trained in the use of this apparatus.

Fire blankets are fitted over scaffolding planks and platforms whenever hot work is being carried out.

The Contractor takes precautions to prevent any occurrence of fires or explosions while carrying out any work near flammable gas and liquid systems. Any tampering with the Employer’s fire equipment is strictly forbidden. All exit doors, fire escape routes, walkways, stairways, stair landings and access to electrical distribution boards are kept free of obstruction, and are not used for work or storage at any time. Firefighting equipment remains accessible at all times.

In case of a fire, the Contractor immediately reports the location and extent of the fire to the Electrical Operating Desk using the Emergency Number 5400. The Contractor takes the necessary action to safeguard the area to prevent injury and spreading of the fire.

### First Aid

The Contractor provides First Aid services to his employees and sub-contractors. In the case of severe or serious injury, to his employees and sub-contractors the Employer’s Medical Centre and facilities are made available and accessible to such persons, during normal working hours.

### Housekeeping

It is the Contractor’s responsibility to ensure that his working areas within the Site are cleaned daily. All electrical cables and hoses are routed so as not to cross unprotected over floors and walkways. All equipment is packed neatly without interference to access. All excess scaffolding material is removed from Site after the scaffolding has been erected. The Contractor is responsible for the removal of any scrap material to the designated scrap area on a daily basis.

### Barricading

Access to danger zones is restricted using handrail type guards at least 1.2 meters high and able to block access to the danger zone. Symbolic safety signs depicting ‘Danger’ and ‘No entry’ are attached to the guards. This includes access during the taking of X-rays.

### Radiographic Examinations

When radiographic tests are carried out in the plant by Others, the danger area is evacuated with the exception only of authorized radiographic workers, and thereafter barricaded. To ensure that employees and contract staff working in Eskom premises are not exposed to more radiation than is reasonable level, compliance is with the Tutuka Power Station procedure ‘Requirements and Rules for Radiation Protection and Safety of Radiation Sources’, reference number 15MNT MSS PC-1267.

### Permit to Work System

The Contractor allocates personnel to be trained and authorised as Responsible Persons according to Employer’s Plant Safety Regulations (36-681).  The Contractor ensures that an adequate number of its employees are trained and authorised as Responsible Persons and Authorised Supervisors prior to the outage date.  The Contractor ensures that Responsible Persons and Authorised Supervisors are available on Site at all times.

## Environmental constraints and management

The Contractor ensures that all goods, services or works supplied in terms of the contract comply with all applicable environmental legislation including but not limited to the (National Environmental Management Act, 1998 [Act No 107 of 1998]).The Contractor is responsible for keeping the work area and Site clean of any environmental waste.

All waste introduced and/or produced on the Employer’s premises by the Contractor for this contract, is handled in accordance with the minimum requirements for the Handling and Disposal of Hazardous Waste in terms of Government Legislation as proclaimed by the Department of Water Affairs and Forestry and Employer’s environmental requirements (Waste Management Procedure; 32-245 and Management of Waste at Tutuka PS; PS/244/001).

All environmental incidents are reported to the Project manager within 24 hours of such occurrence. All environmental incidents occurring on Site (or on any other places, if any, as may be specified under the Contract as forming part of the Site) are recorded, detailing how each incident was dealt with in an Environmental Incident register.

## Quality assurance requirements

### General

#### The Contractor complies with the Employer’s quality and technical requirements including those listed in the Employers Supplier Contract Quality Requirements Specification document, QM-58 240-105658000.

#### The Contractor submits a QMS as a returnable schedule and uses it for all phases of the Project.  The QMS complies with the requirements of ISO 9001 standard. The Contractor provides evidence of a fully implemented QMS.  The Employer may at his sole discretion carry out an audit on the Contractor, the Contractor’s suppliers and Subcontractors.

### Quality Management documents requirements

The Contractor submits the following documents, within 30 days of the Contract Date, to the Project Manager for review and acceptance and prior to the commencement of work.

The Contractor supplies the Supervisor with a Contract Quality Plan (CQP) which details the Contractor’s organisation, quality assurance and quality control procedures within that organisation specific to this project.  The CQP is aligned to, and reference ISO 10005:2005 QMS, guidelines for quality plans and is in compliance with the guideline in QM-58 240-105658000.  The CQP makes reference to the Contractor’s QMS Procedures to be used in this Contract:

#### The Contractor’s QMS compliance with the requirements of ISO 9001

#### Contractor’s quality manual

#### Contractor’s quality procedures

#### Contractor’s quality forms and work instructions

#### Contractor’s quality system documents referenced in this Works Information

The Contractor supplies the Supervisor with a QCP or ITP for review and acceptance.

The Contractor supplies the Project Manager with a detailed contract organogram showing the quality personnel to be used in the Contract.  The Contractor provides CVs of the quality management employees responsible for quality on Site.

Quality Management employee’s responsibilities include, but are not limited to, the following:

- Implementation of the QMS

- Administration of QA/QC systems

- Verification of approval status of Subcontractor’s QCP and procedures

- On-and -offsite inspections

- Co-ordination, inspection and verification of the Employer’s intervention points

- Review of Contractor testing and inspection documents (procedures, test results)

- Reporting on quality performance

The Contractor submits as a minimum the following documents, as required by the Project Manager;

- Updated QCP register

- Inspection notifications, accompanied by applicable inspection report

- Non-conformance and Defects registers and reports

- Updated Site and off site inspection schedules

- Inspection and or FAT dates

- Inspections completed/outstanding

- Inspection and test reports

- Monthly contract quality progress report

- Data books for the completed work, before commissioning can commence

### Quality Responsibility

- The Contractor is accountable for the quality of the output and liable for any failures.

- The Contractor is responsible for defining the level of intervention of QA/QC or inspections.  These are in line with the Employer’s requirements.

- The Contractor is responsible for defining the level of intervention of QA/QC or inspections to be imposed on his sub-Contractor, suppliers and sub-suppliers and ensures that these are in line with the Employer’s requirements.

- The intervention requirements take into consideration the criticality of the Plant and Materials.

- The intervention points include all witness, hold, verification and review points required by the Supervisor. The Contractor’s failure to allow the intervention points constitutes a non-conformance. (Refer to Section 2.5.4 below).

### Inspections

- The Contractor is responsible for the inspection of all the work that is performed and the Supervisor only verifies that the work is conducted as per works information.

- The Contractor conducts all inspections in accordance with the accepted QCP/ITP.

- The Contractor drafts a QCP or ITP which shows each activity from the Works Information and submits to the Supervisor for acceptance.

- The Contractor provides suitably qualified personnel to conduct on-and-offsite inspections

- The Contractor ensures that all work is inspected and approved before the Supervisor is invited for verification.

- The Contractor provides a minimum of seven (7) days notice for local inspections and 21 working days’ notice for foreign inspections. The notice contains copies of the Contractor’s inspection reports.

### Non Conformances and Defects

Where NCR’s and Defect notifications are issued, the Contractor acknowledges receipt within  14 calendar days from the date of issue of the Non-conformance   and proposes corrective and preventive actions to the Supervisor as per the contract response period. The corrective and preventive actions include the implementation and completion dates.  Progress on all NCR’s and Defect notifications issued to the Contractor is reported to the Supervisor on weekly basis.

#### The Contractor’s quality manager keeps a register of all NCR’s and Defect notifications issued

#### Deviations from the contract are treated as a non-conformance.

#### Records of NCRs and Defect notifications are kept and form part of the data book records.

#### To ensure reduction of non-conformances, the Employer will implement a penalty to the value of R10 000.00 for every five (5) NCR issued during the contract period

During the contract execution phase, the Contractor is monitored by the Supervisor for performance on quality related aspects. The monitoring is in the form of audits and assessments.

### Quality Reporting

The Contractor submits a monthly quality report, on the last working day of the month. The report includes but is not limited to the following:

#### A register of NCRs and Defects

#### Updated QCP / ITP register

#### QA monthly report summary

#### Planned and completed local and foreign inspection dates

#### Completed and outstanding Inspections

#### Audit findings report

#### Preservation, shipping and transportation

The Contractor ensures that all Plant and Materials are preserved in an appropriate manner as described in the Works Information. The Contractor submits the preservation, shipping and transportation procedures to the Project Manager for review and acceptance. The Project Manager may choose to witness the packaging, loading and offloading of the Plant and Materials.

The Contractor ensures that all storage requirements for Plant and Materials as well as the existing equipment are properly implemented to preserve the products against adverse conditions, deterioration, damages, etc. Storage and preservation procedures for the different products are submitted to the Project Manager for acceptance. The Project Manager may request to inspect the stored products at any given point during the storage period.

## Programming constraints

### Construction Constraints

The Employer provides the Key Dates as set out in clause 11.2.(9) of the Contract Data of the Employer, the access dates in clause 30.1 of the Contract Data by the Employer; the interface points identified by the Contractor in the Contractor’s Works Information and requirements set out in the Works Information.

The Contractor submits, as part of his tender response, a Level 3 programme which contains the following as a minimum:

- The Key Dates

- The access dates from clause 30.1 of the Contract Data by the Employer;

- The detail on how the Contractor intends to achieve the Key Dates and the access dates;

- Duration of long lead item

- Total manufacturing and execution durations

- The date of Site establishment;

- Show all the critical paths;

- The Contractor ensures that his programme contains sufficient float in order for the Contractor to add interface and alignment with the Employer and Others;

- Other factors, information, methodologies, detail and dates which the Contractor believes are necessary for achievement of the interface with others; Key Dates, Completion Dates and access dates.

The Contractor submits a detailed programme after Contract award in accordance with time period provided in clause 32.2. This revised programme must contain the following:

- All information required as [stated above];

- the services and work (programs) of all his Subcontractors and suppliers;

- the design schedule;

- the construction schedule;

- the planning schedule;

- the construction and manufacturing schedule;

- the commissioning schedule;

The Contractor submits an updated programme every 2 weeks during design and manufacturing, and twice a week during execution or as agreed to between the Project Manager and Contractor.

The level of detail for each is set out below.

The Contractor submits a single programme that incorporates the services and work (programs) of all his Subcontractors and suppliers. The Accepted Programme clearly indicates interfaces between the Contractor, the Employer, Others and his Subcontractors.

The Contractor ensures that the Key Dates and interfaces with the Employer and Others are incorporated into the Accepted Programme. To improve integration and interfaces with Others and the Employer, the Contractor participates in the integration meetings with the Employer and Others. as required by the Project Manager. The information obtained from these integration meetings are incorporated into the revised programmes submitted to the Project Manager.  The Contractor ensures that all dates, including Key Dates, between the Contractor, the Employer and Others are aligned in the revised programme.

The Contractor’s obligation to meet the Key Dates and Completion Date is not altered by the Contractors obligation to ensure that the Contractor’s programme shows and aligns with the interface requirements set out in the Works Information.

### Computerised Planning

Primavera Project Planner (version 6) has been adopted by the Employer for all planning, progress monitoring and reporting on the project. The Contractor applies it for the planning and control of the works in line with the accepted WBS.  The Project Manager does not accept any programmes, progress reports or other required planning data and information in PDF or any other form except Primavera Project Planner (version 6).

The Project Manager has a Master Programme which incorporates the Contractor’s and Other’s programmes. The Contractor submits updated electronic progress reports, as required by the Project Manager. The updated progress report shows the logic and all filters and layouts used in the programme.

### Planning Methodology and Programme Levels

All planning is done based on the Critical Path Method (CPM). The Contractor’s planning methodology incorporates the compatibility, alignment and interface with others on the project. This is clearly visible to the Project Manager. The Accepted Programme clearly shows the actual critical path.

The following levels of programme are used by the Contractor for dynamic integrated project control:

- Management level programme (Level 1)

- Project level programme (Level 2)

- Control level programme (Level 3)

- Discipline specialty programme (Level 4)

#### Management Level Programme (Level 1)

The management level programme is used to establish work goals and overall time frames for the works.  It is a statement of project objectives recorded in graphic form.  The management level programme defines:

- Established goals or major milestone Key Dates;

- The duration of major operations and their relationship to one another;

- Identified long lead material items;

- Responsibility assignments for accomplishing project objectives.

#### Project Level Programme (Level 2)

A "rolled up" programme from the control level programme is produced. It will be separated by unit, plant area and by activity.

#### Control Level Programme (Level 3)

The project level programme is prepared representing the significant work activities and deliverables associated with the works.  The end product is a time scaled bar-chart schedule developed through use of a logic network.

This programme is separated by unit, by plant area, by phase and by WBS. The work within each plant area is broken down by engineering discipline, procurement of tagged equipment, construction by Contractor, and commissioning and start-up. The control level programme is resource-loaded. It forms the basis for progress measurement, progress curves and histograms for each discipline within a plant area.

#### Discipline Specialty Level Programme (Level 4)

The discipline specialty level programme is developed and maintained by the Contractor and generated for tracking and control of various activities and deliverables for all phases of the project. This programme is formatted as a spread sheet or database report utilizing the WBS structure. The programme represents the day-to-day activities which are work unit based and become summarized in the level 3 activities.

The Contractor provides resource information in a resource histogram reflecting the manpower, Plant and Materials and Equipment. Staffing histograms are required to be submitted based on “equivalent personnel”. Staffing histograms are updated with actual data for each reporting period and re-forecasted as required should significant deviations occur. The Contractor submits a 7 (seven) day working program indicating all the number of shifts.

### Planning Schedules

Long lead manufacturing items and the dates for placing the main subcontracts is identified.  Key contract, program and interface events are identified in the contract program, including dates for access data and release of terminal points that involve the Employer or Others.  The Contractor submits a manufacturing and procurement schedule as per Section 2.6.4.2 of this Works Information and ensures that it aligns with planning, design and construction schedules.  The Contractor ensures that its program fully aligns Others and all interfaces are fully reflected.  Refer to Section 1.6 and Appendix C

The program makes provision for site related preparation such as safety induction, and medical assessments for the entire Contractor’s staff that will be working on Site. The phasing of units is as follows: Design of the DHP for 2 (two) units; and Manufacture the DHP for the first 2 (two) units. Please note that the instrument/control air compressor house, including the compressors design and installation need to serve all six units. Only two hopper blower houses would be design and construct for units 2 and 6. Each of these two units will have one blower house each and each blower house will have two blowers.

#### Design Schedule

The Employer provides the Contractor with a Master Document List (MDL) template as per Appendix H. The Contractor expands on the MDL and includes the submission dates of various revisions for submission of the Contractor’s Design Documents using the Key Date for design freeze as a yardstick. The initial design schedule is a returnable schedule.

The Contractor’s schedule also illustrates the sequence of work for the Project, including sequencing and alignment with design of Others, and the dates for submission of drawings, studies and reports.

#### Procurement and Manufacturing Schedule

The procurement and manufacturing schedule identifies as a minimum:

- Details of orders and target dates;

- Any detailed design required within the manufacturing period;

- Long lead items including imported items;

- Hold points for inspection and acceptance tests and release.

The Contractor ensures that the procurement and manufacturing schedule contains sufficient detail to enable the work to be adequately progressed in order to meet Key Dates and the Completion Date.  The procurement and manufacturing schedule must show alignment, interface and compatibility with the Employer and Others.

#### Construction Schedule

The Contractor submits a construction schedule and finalized resource schedule for review by the Project Manager.  This schedule satisfies the following criteria:

- Contains full details of all terminal point release requirements;

- Identify any erection or commissioning activities that may affect other maintenance and construction activities on the plant;

- Identify when services are required for commissioning purposes;

- Include an outline setting to work and commissioning schedule

The Contractor further submits a construction execution plan that includes man power plans, organization, construction equipment usage, material storage and handling and preparation of construction facilities.

#### Commissioning Schedule

The Contractor develops a detailed commissioning schedule with sufficient detail to enable the works to be adequately progressed in order to meet Key Dates and the Completion Date.  The schedule shows alignment, interface and compatibility with the Employer and Others.

### Time Analysis

The Contractor takes note that, automatic manipulation of 'lags', 'overlaps', 'leads', 'relations' or 'dummies' (with positive, zero or negative duration’s) to cause the float to remain constant when updates are performed is not acceptable.

The Contractor provides the program logic in network format, together with a total float report for acceptance by the Project Manager.

The Contractor ensures that the programme network has no fewer activities than the technical and commercial breakdowns listed in the activity schedule.

The Contractor constructs networks to reflect the possible (not probable) sequences of activities, using resource scheduling to stagger the performance of activities into the most probable sequence.

A single time estimate for the duration of an activity is given assuming 'normal' resources are available as required.  The Contractor estimates activity durations in days or hours as required.Time Reporting

The Contractor extracts and provides a one-week “look ahead window” from the Accepted Programme, that furthermore shows Key Dates which are scheduled for Completion within the next reporting period.

### Reporting on Remaining Duration

The method for reporting on activities in progress is by remaining duration, i.e. the time, in working hours or days as required, needed to complete the activity from the report date.  Once an activity has started, the remaining duration is assessed for each update.

### Actual Dates

The actual starting and completion date of all activities is reported.

### Progress Reporting during Provision of the works

The Contractor submits its progress reports on the last day of each month and if the last day is not a working day, the preceding working day or more often as required and agreed by the Project Manager.  This requirement does not constitute a compensation event.

The Contractor submits, together with the progress reports, a written report containing the following:

- Statement and report on work where delay against the Accepted Programme has occurred (if any), together with the reasons why delay has occurred and a plan denoting the action to be taken and the period of time necessary to recover such delay; any impact that the delay may have on Others or an indication of Others affected by the delay.

- Statement and report on those activities that are currently ahead of programme, any impact on the progress of Others or an indication of Others affected by the delay.

- The impact of any programming changes arising is reflected in revised forecast rate of payment schedules and resource schedules.

### Daily Progress Report

The Project Manager; the Contractor and Others meet daily to report the overall progress of construction activities which identifies the following:

- Any SHE related incidents and remedial actions or plans

- Progress of previous day’s work

- Resources

- Any deliveries of Plant and Materials and Equipment

- The scheduled date of delivery of Plant and Materials and Equipment

- Interface, alignment and compatibility with the Employer and Others

- Contractor’s current activities progress and planned finish dates

- Contractor’s planned start and finish dates for work

- Planned effort for activities

- Actual effort for activities

- Remaining duration for activities

- Percentage progress for activities

### Weekly Progress Report

The Contractor submits weekly progress reports to the Project Manager.  This report is used as a tool for the day-to-day management of the contract.  The content of the weekly report includes the following items:

- Programme summary narrative.

- Progress and performance summaries.

- Completion and Key Date status.

### Monthly Progress Report

The Contractor submits to the Project Manager a written monthly report as provided for in Section 2.6.8 above.  The monthly report contains the following information as a minimum requirement:

- Executive summary (narrative identifying major movement within the reporting period).

- Revised Programme indicating, actual progress of work against last Accepted Programme.

- A one-week look ahead work window.

- Activities completed during current reporting period per discipline, including the activities of the Employer and Others.

- Activities in progress during current reporting period per discipline, including the activities of the Employer and Others.

- Activities undertaken during next reporting period per discipline, including the activities of the Employer and others

- Status overview by unit, by plant area, by phase.

- Key issues/items of concern and corrective actions.

- Progress curves and tabular progress reports.

- Cost and Cash flow.

- Cost curve 'S-curve'.

- Early warning log.

- Compensation event log.

- General planning report (computer generated).

- Critical activities report.

- Key event report (computer generated).

- Report selecting all of the activities of the Employer and Others - (computer generated).

- Updated bar charts.

- Updated resource schedule and histogram (If changed).

- Updated activity schedule

- Forecast rate of payment schedule updated with actual progress.

- Statement and report on activities ahead and behind program;

- Skills development progress report.

- Progress on population of stock item templates

### Planner Requirements

The Contractor’s planner is experienced, qualified and must be dedicated to the Contract/Project to perform the planning and programming requirements in accordance with this section.  During execution, the Contractor provides a full time planner at the Site.

## Contractor’s management, supervision and key people

The Contractor provides the following key people as a minimum:

- Dedicated Project Manager –full time

- Dedicated Project Planner – Full time

- Dedicated Quality Control officers- full time

- Dedicated Site Manager –Full time

- Dedicated Quality Manager- As when required

- Dedicated Quality Control Supervisors- full time

- Dedicated Site Safety Manager- full time

- Dedicated Site Safety Representatives – full time

- Design and Testing Engineers- as and when required

- Commissioning Engineers-  as when required

For the purposes of this project, “dedicated” means that the person is allocated only to this project full time, must not be working on any other contract, must be available during construction phase and must respond promptly to instructions.

In the Contractor’s tender response, the Contractor states how many of the key people are required for the completion of the works.  The Contractor’s pricing for this provision of this activity is stated in such a way that the Employer is able to assess the number of dedicated persons, their job function and the extent of their availability.  If the Employer finds that the key people are not a “dedicated” resource, the Employer makes a pro rata deduction from amount due to the Contractor.

## Invoicing and payment

### General

- Invoice addressed to Eskom Holdings SOC Ltd

- Read “Tax Invoice”

- Company VAT registration number

- Eskom VAT registration Number 474010508

- Invoice Date

- 45 Purchase Order Number

- 50 Goods Receipt Number

- Supplier Name and Address

- Vat to be indicated separately

- Order Numbers to be invoiced separately

- Rate/Activity to be claimed in accordance with contract

- CPA invoice need to be invoiced separately

- Local and foreign invoices to be invoiced separately

- Tax invoice is to be emailed to email address invoicegrpcapitalOTH@eskom.co.za as soon as it is available.

- Incorrect claim (invoices) should be cancelled with a credit note referring to the incorrect invoice and issue a new invoice

### Foreign Portion Invoicing

- Info of foreign beneficiary and foreign Bank account

- Foreign Beneficiary Invoice (foreign Amount) to be attached to local invoice (Also to comply to General requirements)

- Bank Details and IBN No. to appear on invoice

- Rand amount claimed in accordance with contract

- Foreign currency converted at contract rate

- Amount claimed and Rand Amount to appear on invoice

- Import and services to be claimed on separate invoices

- VAT to be claimed separately referring to foreign invoice

- Services to be paid direct overseas and may not be paid into a CFC Account

- Foreign CPA calculations together with index need to be attached.

### Import Invoices

- Import documentation to be attached

- Custom invoice to reflect foreign currency and amount

- Bill of entry

- SARS customs release notification document

- Custom Worksheet

- Bill of lading or Airway Bill

## Insurance provided by the Employer

To be dealt with in accordance with ECC3 Core Clause 87.1, 87.2 and 87.3 and additional requirements are also stipulated in Z Clause.

The insurance policies and procedures forms part of the Contract Data and any reference to this is contained in the Contract Data.

## Contract change management

Changes during a term of the Contract are inevitable and when they occur they need to be managed within the policies and procedures of Eskom. Changes can be minor which are administrative or substantial which may affect the price and delivery.  There are two ways to change a contract:

a)	Bilateral

b)	Unilateral

Bilateral is when both Parties (Contractor and Employer) agree that a change is necessary. The second one is the unilateral whereby the Employer may exercise a right to modify the contract without the contractor’s consent. In case of latter one, the Eskom procurement and supply chain management procedure-32-1034 must be followed.

### Contract changes and contract Scope

Eskom commercial policy requires a competitive process, any change upon the type of goods or services needed must be consistent with what was asked during the tender stage. A contract change needs to be within the scope of what was provided during tender stage. A significant difference will not be allowed because it had not been subjected to fair competition. Transparency is one of PPPFA requirements and as a government owned organisation had to comply with.

### Administrative changes

These are the changes that are within the scope of contract and do not affect the originally signed contract. These changes are typically executed via a unilateral amendment. Examples include:

a)	Changes in address

b)	Correction of typographical errors not affecting the substance of the contract

c)	Changes as permitted by the language of the contract

d)	Changes in personnel assigned to the contract.

### Substantive changes

These are the changes that affect both Parties. They require bilateral amendments. These changes may require one of the Parties to be compensated for such changes. Examples of substantive changes include:

### General Principles of contract change management

2.10.4.1	Engineering change will be dealt with as per 3.3.1. if either party is in doubt about whether a change falls within the definition of engineering change then it will be processed as a contract change.

2.10.4.2	Under this contract change management:

a)	Either party may request a contract change. All changes need to be formally communicated prior to the implementation of that change.

b)	Neither party makes a request that is not made in good faith or for good reasons

c)	The Project Manager assesses and documents the potential impact of a proposed contract change  before presenting it to the Employer’s Compensation Events Committee

d)	The Project Manager has the right to request reasonable amendments to a contract change request.

e)	The Project Manager has the right to reject a change and specify his reasons.

f)	No proposed contract change will be implemented by the Contractor without prior approval of the Project Manager.

g)	If the proposed change is of emergency in nature, approval of emergency instructions will be followed as per paragraph 2.10.7,

h)	Any contract change necessary to comply with a Change in Law will be implemented as set out in paragraph 2.10.3  & 2.10.4.

i)	Until a change is approved, signed and issued to the Contractor, then

i.	Unless the Project Manager expressly agrees otherwise in writing, the Contractor  continues to provide the works in accordance with the signed contract as if the proposed contract change does not apply; and

ii.	Any discussions, negotiations or other communications which may take place between the Project Manager and Contractor in connection with any proposed contract change, including submission of any change communications, is without prejudice to each party’s other rights under this Contract.

j)	The Project Manager notifies in writing the Contractor stating the reasons why the Contractor has not reasonably demonstrated the need or justification for the contract change in connection with the specified event. If the Contractor disputes the notice then the matter is resolved in a risk reduction meeting.

k)	Where the Contractor does not approve a contract change in respect of a specified event, the Contractor notifies his decision within period of reply.

### Costs

a)	Each party bears its own costs in relation to the preparation and agreement of each change request and impact assessment.

b)	All contract changes are calculated in accordance with the principles set out in Price Schedule. Any cost savings resulting from the contract change will be passed on to the Project Manager by way of reduction in the charges.2.10.6 Contract Change Request.

c)	Either party may issue a contract change request to the other party at any time during the term of the contract. The change request is substantially in the form of Appendix 10, and must state a relevant clause and specify if it is categorised as an emergency change.

d)	If the Contractor provides a contract change request, he also needs to provide an impact assessment in terms of cost, schedule, and quality.

### Impact Assessment

a)	Each impact assessment includes (without limitation):

i.	Details of the proposed contract change where the contract change is proposed by the Contractor including the reason for the contract change and

ii.	Details of the impact of the proposed contract change on the contract and the Contractor’s ability to meet its other obligations under this contract, including without limitation changes to:

•	The works information

•	Accepted Programme

•	Other works provided by Others to the Employer including any changes required by the proposed contract change to the Project Manager.

•	Interface

iii.	Details of the estimated cost of implementing the proposed contract change

iv.	A schedule for the implementation, together with any proposals for the testing of the contract change

v.	Where applicable details of how the proposed contract change will ensure compliance with any applicable Change in Law and

vi.	Such other information as the Project Manager may reasonable request in (or in response to) the change request.

b)	The Project Manager reviews the Impact Assessment and responds within the period of reply or as agreed with the Contractor.

c)	If the Project Manager requires further information regarding the proposed contract change so that it may properly evaluate the change request and impact assessment, then with the period of reply or as agreed with the Contractor, the Project Manager notifies the Contractor of this fact and details the further information that is required. The Contractor provides the relevant Impact assessment within the period of reply or as agreed with the Project Manager of such notification. The parties may repeat the process described in this paragraph until the Project Manager is satisfied that it has sufficient information to properly evaluate the change request and impact assessment.

### Project Manager’s right of acceptance of contract changes

Within period of reply of receiving the impact assessment from the Contractor, or further information, the Project Manager evaluates the change request and the impact assessment in  good faith and

a)	Submits all the details of the event to the Secretariat of the Employer’s Compensation Events Committee (CEC) which meets on weekly basis.

b)	Presents the details of the event to CEC

c)	Implements the recommendations of the CEC.

d)	Notifies the Contractor of the rejection of the proposed change. If the Project Manager rejects a proposed change, then he may explain his reasons in writing to the Contractor within period of reply or as agreed with the Contractor.

e)	Require further details on the change request and/or impact assessment in which the Contractor makes changes and respond within period of reply or as agreed with the Project Manager of such request.

f)	If the proposed contract change is recommended by the Compensation Events Committee, the Project Manager notifies the Contractor in writing. The Project Manager  signs off on all deviation to the contract (drawings, specifications and other relevant documents) before the implementation of such deviations may take place

### Contractor’s right of acceptance of proposed changes

The Contractor has a right to reject a proposed change if he believes any proposed contract change which is requested by the Project Manager:

a)	Would materially and adversely affect the risks to the health and safety of any person

b)	Would require the works to be performed in a way that infringes any Law ot

c)	Is technically impossible to implement provided that

i.	The Contractor can demonstrate to the Project Manager that the proposed contract change is impossible to implement

ii.	Neither the Accepted Programme nor the Works Information state that the Contractor have technical capacity and flexibility require to implement the proposed change.

d)	Would materially and adversely affect the Contractor’s ability to deliver the works

e)	Would not be possible to implement before contract completion date.

f)	Would cause the Contractor to breach any of the Insurances

g)	Would cause the Contractor to be in breach of any existing licence, consent or permit

h)	Would require the consent of Others to enable the contract change to be implemented and the Contractor is unable to obtain the consent of the Others.

i)	Would result in additional cost to the Contractor that is not proposed to be paid to the Contractor as part of change

### Emergency Instruction contract changes

a)	The emergency instruction contract change may cover technical, financial, safety and strategic aspects.

b)	The only person who can instruct the Contractor to implement such changes is the Project Manager. Such instructions need to be subsequently followed by a written formal communication.  All changes must be documented and no payment will be made to undocumented change.

c)	The Project Manager is given restricted authority to cover instructions to the Contractor that are of an emergency in nature and which will result in a contract change. Such contract changes are presented to the Compensation Events Committee, by the Project Manager, for its retrospective recommendation and ratification by the Employer.

### Authorisation of contract change

Any proposed contract changes are not authorised and the Contractor does not implement any proposed contract change until the signed letter and other signed documents (e.g. drawings, specifications) are sent to the Contractor.

### Communications

a)	For any contract change communication to be valid, it must be sent to the Contractor as applicable.

b)	All contract change communications may be hand delivered or sent by first class post or facsimile. Contract change communications are deemed to have been received at the following times:

i.	If hand delivered, than at the time of delivery or, if delivered after 16.00 hours on the next Working Day

ii.	If posted first class within South Africa at 10h00 on the second Working Day after it put into the post.

iii.	If sent by facsimile, then at the expiration of four (4) hours  after the time of despatch, if despatched before 15h00 on the next Working Day, and in any other case at 10h00 on the next Working Day following the date of despatch.

- In proving delivery of a contract change communication, it will be sufficient to prove that the delivery was made, or that the envelope containing the contract change communication was properly addressed and posted (by prepaid first class recorded delivery post) or that the facsimile was properly addressed and despatched , as the case may be.

## Provision of bonds and guarantees

The form in which a bond or guarantee required by the conditions of contract (if any) is to be provided by the Contractor is given in Part 1 Agreements and Contract Data, document C1.3, Sureties.

The Employer may withhold payment of amounts due to the Contractor until the bond or guarantee required in terms of this contract has been received and accepted by the person notified to the Contractor by the Project Manager to receive and accept such bond or guarantee.  Such withholding of payment due to the Contractor does not affect the Employer’s right to termination stated in this contract.

## Records of Defined Cost, payments & assessments of compensation events to be kept by the Contractor

The Contractor submits the following for compensation event assessment:

- Quotation indicating Current market rate if not included in the short schedule of cost components

- Labour time sheets

- Early warning to the Project Manager

- Project Manager‘s Instruction

- Percentage fee applied

- CPA Calculation where short schedule of cost components rates were utilised

- Signed Record of decisions (ROD) or design change request form for Engineering design changes

- Revised program where key date and completion date is affected

- Revised program where instructed to accelerate by the Project Manager

- Invoice from supplier and service providers

## Training workshops and technology transfer

The Contractor provides training on the works regarding operating, maintenance and engineering aspects. The Contractor provides training material and a separate training course for operating, maintenance and engineering personnel. For more detailed requirements on the training required refer to section 5.2.9 of this Works Information.

# Engineering and the Contractor’s design

## Employer’s design

The Contractor’s design adheres and takes into account the performance requirements and operating philosophies for each system as described in the Works Information.

### Existing Plant

Existing plant data is provided by the Employer. Where additional information is required the Contractor collects all data for the design, including process and existing plant data and information from the Employer, to enable the completion of the works. The Contractor clarifies and co-ordinates all relevant interfaces that may exist.

The Contractor is responsible to incorporate the information in this section into the design that he conducts.

#### Power Station Systems

- Unit Control System: Tutuka Power Station is currently operating with units 4 - 6 Boiler and Turbine controls, converted to an ABB DCS (Procontrol 14) system.

- Units 1 - 3 have upgraded ABB DCS Turbine controls only, with the remainder using Teleperm C / Iskamatic platform. *

- Outside plant control room has a Yokogawa DCS.

- MV Switchgear OEM: Hawker Siddley *

- LV Switchgear Unit 1 - 3: Siemens

- LV Switchgear Unit 4 - 6: General Electric

- The gas cleaning equipment is Lurgi cold side dry electrostatic precipitators (ESPs) with two (2) parallel steel ESP casings per unit. Each casing has five (5) fields with two (2) chambers per ESP casing, thus twenty (20) storage hoppers.*

- Low Pressure Services:

  - Potable water distribution: A potable water production plant including a water treatment plant is available and provides potable water to Tutuka Power Station.

  - Fire protection system: A pumped fire water main with strategically placed fire hydrants close to all necessary buildings and substations exist along with fire extinguishers in required locations to cater for expected fire loads.

  - Compressed air production: A compressed air system consisting of compressors, air dryers and air receivers is available to supply instrument/control air to units 1 to 6 ash hopper aeration air supply control valves pneumatic actuators and the ash conditioners ash, water and aeration air control valves pneumatic actuators. Only the instrument/control air pipelines to each ash hopper aeration air supply control valves of unit 2 and 6 would be covered in this scope of work, as well as the new pipeline to tie into the existing ash conditioner main control air pipe line. The compressors should be design to supply instrument/control air for all six units precipitators hoppers and 12 ash conditioners.

- * Demarcates project that will be upgraded during the same outage as planned for the works.

#### Hopper Agitation System

Each ESP hopper is fitted with a manual agitation system.

- The manual agitation system for each hopper consists of four (4) chains which are connected to the upper four (4) corners of each of the hoppers.

- The chains are all connected to a handle which is positioned near the outlet of the hopper.

- The handle is able to be moved from the outside of the hopper.

Figure 1 below shows an illustration of the manual agitation system for a single hopper.

Figure 1 Manual Hopper Agitation System

#### Dust Handling Plant

Chain conveyors remove ash from the hoppers and discharge it into the bucket elevators which in turn discharge the ash into the ash bunkers. The ash bunkers are shared between two (2) units, the units that share the ash bunker are.

- Bunker 1 : Units 1 and 2

- Bunker 2 : Units 3 and 4

- Bunker 3 : Units 5 and 6

The layout of the DHP for a single unit is depicted in Figure 2 below.

Figure 2 DHP Layout

##### Chain Conveyors (Drawings 0.61/7777 Sheet 1, 0.61/7778 Sheet 2, 0.61/7779, 0.61/7780, 0.61/7781, 0.61/9303, 0.61/9304, 0.61/9305, 0.61/9306, 0.61/54801, 0.61/57586, 0.61/8991)

- Between the outlet of the hopper and the inlets to the hopper chain conveyors the following equipment is installed.

  - Isolation slide gate (mounted to the outlet flange of the hopper).

  - A weighted single flap valve.

  - A compensator.

- The hopper chain conveyors are elevated on a structural steel support structure.

- The discharge from the hopper chain conveyors to the transfer chain conveyors are fitted with:

  - A manual isolation valve with limits.

  - Motorised double flap valve.

  - A compensator.

- There is a compensator installed on the feed between chain conveyors A1 to A2 and C1 to C2.

- The transfer chain conveyors are supported on structural steel beams positioned on plinths.

##### Bucket Elevators (Drawings 0.61/7782, 0.61/7783, 0.61/9306, 0.61/57586)

- The boot of each of the bucket elevators is positioned in a pit at the base of the ash bunker.

- The bucket elevators are routed up the side of the ash bunker.

- The bucket elevators have two (2) drives at the head end, the drives are:

  - Main drive.

  - Service drive for chain inspections.

- The bucket elevators (A – C) all discharge into a central hopper with a bifurcated chute discharge which can discharge into either ash bunker compartment.

- The bucket elevators, central hopper and bifurcated chute are supported by a structural steel structure installed on the roof of the ash bunkers which includes the crawl beams required for maintenance purposes.

#### Conditioning Plant

Situated below the two (2) compartments of each bunker is the conditioning plant. During commissioning of Tutuka P.S. two (2) conditioners per ash bunker were installed, although each bunker can accommodate a total of four (4) conditioners. A layout of the conditioning plant for each ash bunker is shown in Figure 3 below.

Figure 3 Conditioning Plant Layout for an Ash Bunker

##### Ash Bunker (Drawings 0.61/3648, 0.61/3650, 0.61/14016)

- The ash bunkers are concrete structures.

- All three (3) ash bunkers have the same layout.

- The ash bunker can be broken down into four (4) sections.

  - Ash bunker compartments.

  - Conditioning plant level.

  - Conditioning conveyors level.

  - Bunker aeration system blower level.

- The ash bunker compartments consist of:

  - Two (2) 1 190 m3 compartments.

  - Over/under pressure relief valve on the roof for each compartment.

  - Continuous level detection for each compartment.

  - Vent pipe which connects the ash bunker compartments to ESP inlet ducting of the units on either side of the ash bunkers.

  - Aeration system per ash bunker compartment.

  - Two (2) outlets per compartment to supply conditioners.

    - Only one (1) outlet per compartment is currently in use, the other is blanked.

- Conditioning plant level consists of:

  - Two (2) conditioners, with space allocated for four (4) conditioners.

    - There are four (4) outlets in the conditioning plant floor for the conditioners to discharge to the conditioner conveyor below.

  - Crawl beams for removal and installation of the conditioners.

  - Conditioning water supply piping.

- Conditioning conveyors level consists of:

  - Two (2) conditioning conveyor belts.

    - There are four (4) inlet chutes installed from the conditioners, of which only two (2) are in use, one (1) per conditioner conveyor.

  - There are two (2) emergency off load chutes at the tail end of the conveyor belts (one (1) for each conveyor belt).

- Bunker aeration system blower level consists of:

  - One (1) blower to supply air for the ash bunker aeration system.

  - Conditioner conveyor belt emergency off load chutes.

  - Take-ups for the conditioner conveyors.

- The bucket elevators are routed up the side of the ash bunker.

  - There are structural supports fixed to the side of the ash bunker to support the bucket elevators.

##### Bunker aeration system (Drawings 0.61/13586, 0.61/54822)

- Aeration pads installed in the ash bunker compartments.

- There are blowers installed in each of the ash bunkers, one (1) installed per ash bunker.

  - The blower’s model is Aerzener GMb 15.10.

  - The blowers supply the air required for ash bunker aeration and conditioner feed airslides.

  - The air supply piping for each of the ash bunkers aeration systems are linked.

    - There are two (2) blowers in operation (and one (1) on standby) to supply all the air required by the bunker aeration and the conditioner feed air slides for all three (3) bunkers.

##### Conditioners (Drawings 0.61/54997, 0.61/55955, 0.61/23527 sheet 1 and 2, 0.61/56665, 0.61/57665, 0.61/57664, 0.61/54812, 0.61/54813, 0.61/57592)

- The ash bunker compartments have openings with cast in flanges which are utilised to feed the conditioners.

  - There are two (2) openings per ash bunker but only one (1) is in use while the other is blanked.

- Between the ash bunker outlet and the conditioners the following equipment, in order, are installed:

  - Manual isolation slide gate.

  - Pneumatically actuated butterfly valve.

  - A drop box.

  - A flow control valve.

  - An air slide.

  - A double flap valve.

- The conditioners have two (2) counter rotating shafts which are fitted with paddles.

  - Only one (1) of the counter rotating shafts is driven.

  - Bull gears are utilised to transfer drive for the driven shaft to the non-driven shaft.

#### Conditioning Conveyor Belts (0.61/10310 sheet 1, 0.61/13276 sheet 1)

- The conditioners discharge to the conditioner conveyors through the conditioned ash chutes.

  - There are two (2) conditioner conveyors per ash bunker currently with one (1) conditioner discharging to each conveyor.

    - There are chutes installed to cater for two (2) conditioners discharging to the conditioning conveyors. The inlet for the chute that is not in use is blanked.

  - The conditioning conveyor belts are fitted with a Dust Cover in the area where the ash chutes discharge to the conveyor.

    - The conveyor is only covered for a set distance after the last conditioned ash chute.

  - The conditioned ash conveyors have a:

    - Five (5) roll idler configuration.

    - 45° troughing angle.

    - Moving head with the ability to discharge to both of the transverse ash conveyors.

- The drive is located at the tail end of the conveyor.

- The conditioning conveyors have an operating condition which allows them to operate in reverse.

- The conveyors are equipped with gravity take-ups.

##### Conditioning Water Supply (Drawings 21.61/55241 sheets 1 and 2, 21.61/55242 Rev 0)

- The conditioning water is supplied from the Tutuka P.S. effluent sump.

- There are three (3) 50% conditioning water supply pumps which take suction from effluent sump.

  - The conditioning water from the pumps is designed to flow through a reverse flow self-cleaning filter but this filter has been decommissioned and is currently being bypassed.

- The conditioning water supply system piping is configured in a loop (ring main) reticulation system with a globe valve present in the return line to control the flow thus preventing settling of solids.

- There are tap offs from the supply pipe to supply the conditioners in each of the ash bunkers.

  - The tap forms a reticulation system within the ash bunker and ties up with the return piping.

  - The quantity of water supplied to each conditioner is controlled by a flow control valve.

- Within the conditioner there is a header which is fitted with five (5) 25 mm diameter nipples to introduce the conditioning water to the ash.

- There is an emergency potable water supply from the air heater washing system.

  - The emergency potable water supply ties into the tap off from the conditioner water supply piping to each of ash bunker.

### Employer’s design requirements of the works

The Employer completed engineering studies, to aid in the identification of scope associated with this project. Information and recommendations from the engineering studies are made available throughout the Works Information. The Contractor is responsible to incorporate the requirements in this section into the design that he conducts.

All drawings from the Employers engineering studies for the works are provided for information purposes (unless the Employer is conducting the detailed design) only. It is the responsibility of the Contractor to validate correctness and completeness of drawings for detail design purposes.

#### Mechanical

##### Hopper Aeration System for two units (Drawing 0.61/96022, 0.61/96061, 0/61/96075)

- There are four (4) aeration pads per hopper.

  - Aeration pads are installed in each of the hoppers to aerate the ash.

  - Aeration pads are positioned in the valleys between the hopper walls.

- Each unitised blower house is equipped with two (2) 100% blower trains.  This unitised blower house will only supply aeration air to the relevant Precipitator ash hoppers.

- The blowers are equipped with VSD’s to facilitate variable discharge operating capacities.

- For the hopper aeration piping there is:

  - A single air supply pipeline from the blower trains supplying air to the hopper aeration pads.

  - A ring main is created around each of the hoppers for the air supply for the aeration pads to the specific hopper.

- There are two (2) 100% multiple heating bank air heaters per unit, one (1) for each blower train.

- Flow meters are installed to allow for monitoring of flow to different areas of the system.

##### Dust Handling Plant

- Hopper outlet slide gates valves are lever operated valves.

- The DHP has:

  - The precipitator casings have a total of 40 ash hoppers.

  - Eight hopper conveyors and each hopper conveyor collects ash from five hoppers.

  - Twenty-four double flap valves between the hopper and transfer conveyors.

  - Six transfer conveyors. One transfer route has two transfer conveyors in series.

  - Three bucket elevators. Each transfer conveyor route, feeds the relevant bucket elevator.

  - Ash bunker compartments.

  - Venting pipe lines from the ash bunkers to the bucket elevator boot stations and to the adjacent transfer conveyor discharge ends.

- The ash bunker vent pipe:

  - Vents air into both units’ (on either side of the ash bunkers) flue gas ducting upstream of the Precipitators.

  - Is connected to the other compartment’s vent pipe such that air can be vented from both compartments through one (1) compartment’s vent pipe.

  - The existing openings in the ash bunker roof for the vent pipe are utilised for the new vent pipes.

- The ash bunkers receive ash from the DHPs for the units on either side of the ash bunker.

##### Compressed Air Supply System (Drawings 0.61/96022, 0.61/96027 Sheets 1 – 6, 0.61/96028 Sheets 1 – 3, 21.61/54505, 21.61/55309, 0.61/97205 Sheets 1 – 40, 0.61/96023, 0.61/96083)

- The instrument air compressors are positioned in the DHP common instrument/control air compressor house

- The instrument air compressors supply the instrument air required by the precipitator hoppers aeration system control valves pneumatic actuators and the ash conditioning plant control valves pneumatic actuators.

- The compressed air system consists of:

  - Four (4) instrument air Compressors Trains (two (2) operational and two (2) on standby).

  - One (1) instrument air receiver per instrument air compressor (four (4) in total).

  - One (1) air dryer per instrument air compressor (four (4) in total).

  - Flow measuring devices to indicate the quantity of air supplied to each unit

    - There are flow measuring devices which indicate the quantity of instrument air supplied to each Conveying Stream.

  - The cooling system consists of:

    - Four (4) cooling towers, each capable of carrying 100% of the heat load of the one (1) instrument air Compressor Trains as a minimum.

    - Four (4) 100% pumps, which circulate water through the closed circuit of the cooling system.

    - Automated open circuit water treatment dosing system.

    - Closed circuit water treatment dosing system.

- The compressed air piping is routed as shown in drawing 0.61/96023. Additional information with regards to the routing is shown on drawings 0.61/96083 and 0.61/97205 Sheets 1 to 40.

##### Conditioning Plant (Drawings 0.61/96022, 0.61/96075, 0.61/96078, 21.61 55242 Rev 3)

- There are four (4) new conditioners installed per ash bunker.

- The conditioners fit within the existing infrastructure of the conditioning plant and utilise the existing ash bunker compartment outlets for their feed system and openings in the conditioning plant floor for discharging to the conditioning conveyors.

- The conditioners installed are of the same technology as the existing conditioners.

- The conditioner feed system has the ability to control the quantity of ash which is conveyed to the conditioner.

- There are two (2) online moisture analysers and two (2) mass meters installed per conditioner conveyor.

  - Online moisture analysers and the mass meters are positioned at points on the conditioner conveyor such that the moisture content and quantity of conditioned ash discharged from each conditioner can be measured.

- The conditioning water supply system

  - Pumps supply effluent water to the conditioners via dedicated conditioning water supply piping.

  - There are four (4) electrically driven pumps (two (2) in service and one (1) on standby) for the ash conditioning water supply system and the fourth pump is used for the ash dump dust suppression system, situated inside the neutralisation sump pump building.

  - The new piping follows the existing routing from the discharge of the pumps situated in the neutralisation sump pump building to each ash bunker.

  - The conditioning water supply system is a reticulation system where there is no possibility for particulate carried in the conditioning water to settle.

  - Each ash bunker has a dedicated water supply pipe but the return pipeline is common for all ash bunkers.

  - The conditioning water supply piping splits into the dedicated ash bunker piping from the outlet of the self-cleaning strainer, prior to the self-cleaning strainer the piping is common for all of the ash bunkers.

- The emergency potable water supply to the conditioners is supplied from the Air Heater Washing System.

##### HVAC

- The HVAC in the unitised blower house buildings includes

  - Two (2) 100% redundant axial mounted fans.

  - Louvers

  - Ducting from the exhaust fan of the acoustic hood of the blower to the outside of the blower house with a fan to overcome the pressure drop of the ducting if necessary.

- The HVAC for ash bunker 1 and ash bunker 3 substations includes

  - Two (2) x 100% package type direct expansion temperature control cooling units (1 in service and 1 redundant),

  - Supply and return air duct work with fire dampers at wall penetrations

  - A return air fan.

  - Concrete plinths to position the package units.

  - Steel base frames to position the package cooling units.

- The HVAC in the Hopper aeration instrument air compressor house includes:

  - HVAC cooling system designed by the Employer. (0.61/97200 sheets 1 and 2)

  - HVAC pressurisation system designed by the Employer. (0.61/97200 sheets 1 and 2)

#### Electrical Plant

The electrical systems include but are not limited to the following:

The proposed single line diagram is given in drawings; 0.61/93922, 0.61/1703, 0.61/96067 and 0.61/96069 (Refer to Section 7).  The proposed layout for the respective substations are given in Appendix R.

##### LV Switchgear

- The switchgear IED’s for the Incomers and Bus-sections on the switchgear boards that fall within the scope of this upgrade are free issued by Others.

#### Civil engineering and structural works

The work to be carried out by the Contractor is indicated on the drawings and comprises inter alia the following:

- Construction of six unitised blower house buildings

- Supply, installation and testing of twelve, 7.5-ton SWL underslung electrical hoists including the curved monorail beams for the unitised blower house buildings.

- Construction of a common instrument air compressor house (inclusive of all structural elements inside and outside the building as indicated on the drawings) designed by the Employer to house both the DHP and Ash Conditioners instrument compressed air supply system. Please note that the Contractor is to redesign this compressor house, so that it can house only the four instrument air compressors.

The design of structural systems complies with the codes and standards listed in Appendix E. The Contractor designs for the following construction materials:

| Structural steel | Grade S355JR, SANS 50025-2; Hot rolled products of structural steels – Part 2: Technical delivery conditions for non-alloy structural steels |
| --- | --- |
|  | Cold formed steel limited to purlins, rails and sheeting with a minimum yield stress of 200 MPa and tensile strength of 365 MPa |
| Concrete | Minimum concrete strength is 35MPa for reinforced concrete and 15MPa for mass and blinding concrete. |

### Excluded from the works

The following scope is conducted by Others or the Employer.

#### Mechanical

- Repairs to the ESP hoppers or ESP support structure.

- Hopper continuous level measurement system.

- Removal of the existing hopper agitation system.

#### Electrical

- Supply and programming of IED’s for incomers/bus sections on the new LV switchgear.

- The MV Switchgear supply point and termination required for this project.

- Calculation of protection settings for switchgear.

#### Control & Instrumentation (Units 1 to 3)

The scope of work below is to be completed by Others for Units 1-3:

- New DCS/Marshalling I/O cabinets (included is terminating of trunk cabling).

- DCS Design, Engineering, Control system I/O, programming or software engineering using the logics, control philosophies, and I/O lists.

- Design from trunking cabling including cable trunking, trays and racking between the interface junction boxes/enclosures in the field to the DCS control/marshalling cubicles.

- HMI screens (HMI hardware) in the control.

- Integration of the Contractor’s drawings (Loop diagrams) in the DCS

### Re-use of existing plant

The Contractor submits a tender based on supply and installation of new Plant and Materials.

The following components of existing plant may (but not limited to) be considered to be reused where applicable in the Contractors design,

- Hopper chain conveyor support structure and foundation plinths.

- Hopper and transfer conveyors casings (Note that hopper conveyor casings from the second hopper up to the third hopper would be a bit higher)

- Bucket elevator casings.

- Walkways, handrails and stairs.

- Pipe supports.

- Ash bunker vent pipe from ash bunkers to the precipitator inlet ducts.

- Ash bunker under/over pressure relief valves.

- Ash bunker aeration pad supportive casings.

- Conditioner discharge chutes.

- Earthing straps connected to the existing mats.

- Existing cable racks/trays/manholes.

- Small power and lighting in the existing substations.

- Conditioning plant field equipment equipment/cabling. Six (6) conditioners are currently installed and interfaced with the OPCR DCS

- Conditioning plant monorails and crawl beam cast in plates.

### Performance Requirements

#### Hopper Aeration System

- The hopper aeration system supplies air to fluidise the ash within the ESP hoppers and the ash bunkers to increase its flowability.

- The hopper aeration blowers as a worst case are able to supply sufficient air to all the 40 hoppers for one (1) unit.

- The existing three aeration air blowers supply the aeration system for six compartments of the ash bunkers. The bunker aeration system requires 12.1 m3/min per bunker compartment, but this is reviewed by the Contractor and changed if deemed necessary. The Contractor is to design, supply, install and commission an additional aeration air blower system for the ash bunkers and ash conditioners. There would be then four aeration air blowers, where three blowers are on load and the fourth blower is on standby. The fourth blower should supply aeration air at a rate of 36,3 m3/min.

- The three ash bunker/ash conditioners aeration air blowers should be sufficient to supply aeration air to all six ash bunker compartments and to six ash conditioners.

- The air is supplied to the hoppers and ash bunkers at a minimum temperature of 130°C at the hopper and ash bunker.

#### DHP

The DHP is a En-Masse chain conveyors and bucket elevator system, which collects the fly ash from each ash hoppers and transport and discharge this fly ash into the selected ash bunker compartment. (for all normal ESP operating conditions).

The DHP is required to have a capacity of:

- Normal Operation – 61 Tph

- Backlog Operation – 80 Tph

The ash bunker vent pipe is able to vent all conveying - and aeration air introduced (while both units are operating at backlog capacity) into the ash bunker compartments through a single compartment’s vent pipe and to a single unit’s ESP.

#### Compressed Air System

The control air system consists of four (4) compressors, two (2) in service and two (2) on standby. Each control air compressor has the ability to supply the compressed air required to operate and control the ash conditioning plant and hopper aeration system equipment servicing three (3) of the six (6) units.

Quality of compressed air:

- Pressure dew point			: -30 to -40 °C

- Oil Content				: 5 mg/m3

- Maximum Particle Size			: 15 micron

- Maximum Particle Concentration	: 8 mg/m3

#### Compressed Air Cooling System

The compressors are cooled using a closed loop system which circulates demineralised water treated with corrosion inhibitors through the equipment internals and then to the heat exchanger inside the cooling tower. An open circuit circulates treated potable water.

The cooling system contains:

- Four (4) 100% cooling towers.

- Four (4) 100% cooling water circulating pumps.

- Open circuit water treatment system with four (4) 100% chemical dosing pumps.

- Closed circuit water treatment system with four (4) 100% chemical dosing pumps.

#### Conditioning Plant

- Conditioner capacity		: 75 Tph (wet, at maximum moisture content) – normal

: 200 Tph (wet, at maximum moisture content) – backlog

- Moisture content		: 20% - max.

: 13 – 16% - normal operation

- The ash vapour scrubber is able to clean the air vented from the conditioner in line with the requirements of the specification Hazardous Chemical Substance Substances of the Occupational Health and Safety Act which states that “personal exposure should be kept below both 10 mg/m3 8-hour time-weighted average total inhalable dust and 5 mg/m3 time weighted average respirable dust”

- The conditioning water supply system supplies sufficient water such that six (6) conditioners can operate at maximum capacity, as well as allowing for additional return flow to the sump to ensure that there is no particle settlement in the conditioning water supply piping.

#### HVAC

- The temperature in the bunker aeration substation is designed at 20 ± 2 °C in summer and 20°C in winter.

- The temperature in the blower house is at ambient ± 6 °C

### Operating Philosophies

#### Modes of operation

There are three (3) main operating modes for the works, these are:

- Remote mode

- Local mode

- Maintenance mode.

##### Remote Mode

###### Remote Auto Mode

In this mode the works are controlled from the control room and all plant operations are fully automated with no direct operator involvement.

Start-up sequence:

With all local control stations set to remote auto mode, the system starts automatically in a logical sequence with all protections and interlocks activated. The DCS controls all sequences. In the event of Plant and Materials failing to start or tripping during the run up, the DCS automatically trips the faulty Plant and Materials and inhibit any further sequential starting of Plant and Materials. The DCS does not perform an automatic shutdown sequence of the running Plant and Materials until requested to do so by the operator, unless such auto shutdown/closure is essential to the process control. The DCS at all times signals the status of all drives and generates alarms for any Plant and Materials or primary device which is in a fault or abnormal state.

Shutdown sequence:

Should a fault condition occur in the system whilst the works is in a fully operational/running state, all Plant and Materials stops in the required sequence to ensure a safe shutdown. The controlled shutdown of the system is in sequence to completely clear the system of any ash and leave the system in a “ready” to start condition.

###### Remote Manual

The operator (from the control room) sequentially starts or stops works in sequence to put the works in a fully operational state. The DCS, however, controls all sequence interlocking and protection. As for remote auto mode, the DCS continuously signals the status of the Plant and Materials and generates all alarms.

In the event of midstream Plant and Materials failing to start or tripping due to a fault condition the DCS inhibits any further starting of subsequent Plant and Materials until the fault is cleared. No auto trip sequences are initiated.

##### Local Mode

The purpose of local mode is to allow the works to be operated from local control panels which are installed in close proximity to the works. The control room operator directs the DCS via the keyboard to release works to be operated locally from the local control panel.

The operator (from local control panels) sequentially starts or stops the Plant and Materials in sequence to put the works in a fully operational state. The DCS, however, controls all sequence interlocking and protection. As for remote mode, the DCS continuously signals the status of the Plant and Materials and generates all alarms. In the event of midstream Plant and Materials failing to start or tripping due to a fault condition the DCS inhibits any further starting of subsequent Plant and Materials until the fault is cleared. No auto trip sequences are initiated.

##### Maintenance Mode

The purpose of this selection is to run individual items of the works on permit, out of sequence and production for maintenance requirements. The control room operator directs the DCS via the keyboard to release the Plant and Materials (to be maintained) from any sequence interlocks with adjacent Plant and Materials, i.e. the Plant and Materials in question is started and run up without interfacing with the upstream or downstream Plant and Materials. All Plant and Materials and personnel safety protection systems are fully operational in the maintenance mode.

For the duty and standby units where the standby unit cuts-in automatically on a trip function, there is a facility to rotate the selection of standby and duty units when the maintenance mode is selected.  Where the standby units are available, a system automatically recording running hours of each system, is available.

#### Hopper Aeration System Operating Philosophy

##### General

Each unit has a unitised hopper aeration system that supplies the air requirement for a single unit’s aeration system. The existing ash bunker aeration air blower system supplies air for the ash bunker aeration system and the conditioning plant airslides.

- Each of the aeration systems has one (1) blower and its associated equipment in operation at all times and one (1) blower on standby.

- The blowers for each unit are designated as either the primary or secondary blower, the primary blower is the blower that is normally in operation.

- Once a week the primary blower shuts down and the secondary blower starts up, the secondary blower operates for twenty four (24) hours after which it will shut down and the primary blower will start up.

  - The entire change over process from the primary to secondary blower and visa-versa is achieved automatically by the control system.

  - At no point in the changeover process is there to be a loss of air supply to the hopper aeration, conditioning air slide or bunker aeration systems.

- The air heaters for the hopper aeration system are constructed of multiple banks, each of the banks is able to be activated and deactivated as required to ensure that the temperature of the air supplied to the aeration pads within the hoppers is at the required temperature.

  - The operation of the heater banks are fully automated by the control system.

- The blower house pressurisation system is operational at all times when the blowers are in operation.

  - If a pressurisation fan trips there is an alarm generated in the control room and the standby pressurisation fan automatically starts.

- The flow measured by the installed flow meters is compared against set point values (based on the current operating condition) and if there is a discrepancy between these figures (due to ruptured pads, pipe leaks or closed isolation valve(s)) there is an alarm activated in the control room.

  - There is a range associated with the difference between the expected and actual flow values, activating these alarms to ensure that there are no unnecessary alarms resulting from fluctuating conditions.

##### Start-up

- The blower house pressurisation fans start up prior to the aeration system thus providing suction air for the blowers and air to pressurise the blower house to keep out dust and ash contaminants.

- During start-up of the boiler the hopper aeration system starts.

- The aeration system for the unit is in full operation and operating at the correct temperature before the first ash is deposited within the ESP hoppers.

- The hopper aeration system follows a set automated start up sequence.

- If the hopper aeration system is not available, there are no interlocks that prevent any other plant areas from starting up, apart from the conditioning plant if there is no air supply to the conditioner air slides.

##### Normal operation

Normal operation is defined as when both units that discharge ash into an ash bunker are in operation and both of the aeration systems associated with these units are in operation.

There are two (2) possible normal operating conditions:

  - Normal operating condition 1.

- This operating condition is active when both units’ hopper aeration systems are operational.

- Under this operating condition each aeration system supplies air for:

  - The hopper aeration system for one (1) unit.

  - The aeration system for two (2) ash bunker compartments.

  - One (1) conditioner airslide.

  - Normal operating condition 2.

- This operating condition is active when both units’ hopper aeration systems are operational but there are minimum full ash hoppers.

- The hopper aeration system has different air supply requirements according to the number of full ash hoppers.

  - The change of blower operating capacity is automatically changed by the control system.

- The number of full hoppers are used as the indication to control the aeration air flow from the blowers. The following sequence is activated when the ESP has mimimum full ash hoppers:

  - The DHP continues to operate to empty the hoppers.

  - When all the hoppers are emptied the operator receives a notification in the control room that  the  hopper aeration ring main isolation valves are closed.

  - Once there is now aeration air needed, then the blowers will switch off by its self. This is an indication that all the hoppers are empty.

  - When the blower operating capacity is reduced the set point for the expected flow through the applicable flow meters are automatically adjusted to account for the change in blower operating capacity.

  - If the number of full hoppers increases, then the relevant aerations air valves towards those hoppers opens, then the aeration air blower will start to supply aeration air to those full ash hoppers.

  - If a hopper conveyor trips and it would take a long duration for repairs, then those relevant hopper aeration air valves will close, when this affected hopper conveyor motor is isolated.

  - If this defected hopper conveyor is repaired and the motor power is de-isolated and this conveyor is back in operation, then these hoppers aeration air valves will open.

  - If the whole dust handling plant is switch off, then the hoppers aeration air supplies must closed and the blower on load, should stops.

  - When the dust handling plant is back in operation, the blower operating capacity is increased the set point for the expected flow through the applicable flow meters are adjusted to cater for the change in blower operation, the amount of full hoppers.

For both normal operating condition 1 and 2, the relevant bunker common aeration blowers, supply air to the two bunker compartments aeration system and conditioner air slide for two (2) of the four ash conditioners.

##### Abnormal Operation

Abnormal operating conditions are defined as when any of the following is applicable:

- Two (2) conditioners associated with an ash bunker compartment are required to be in operation simultaneously.

- A hopper aeration system is not available, either due to a failure or due to the unit being shut down with its associated hopper aeration system and the ash bunker requiring to remain in full operation.

There are two (2) possible abnormal operating conditions.

- Abnormal operation 1.

- This operating condition is active when two (2) conditioners are required to be operational which are supplied from a single compartment within an ash bunker.

- Under this operating condition the aeration system supplying air to the specific ash bunker compartment supplies the air required by:

  - The ash bunker common aeration air supply system.

  - The aeration system for one (1) bunker compartment.

  - Two (2) conditioner airslide.

- The selection of this operating condition is fully automated by the control system.

- Abnormal Operation 2.

- This operating condition is active when one (1) of the bunker aeration common air blowers is out of operation, then the standby common aeration air blower will start and supplying the air required for the ash bunker is not available and the ash bunker is required to remain in full operation (two (2) ash bunker compartment aeration system and one (1) conditioner per ash bunker compartment).

- Under this operating condition the operational aeration blower supplies the air required by:

  - The aeration system for two (2) bunker compartments.

  - Two (2) conditioner airslides.

- The selection of this operating condition is manually selected by the operator.

  - When abnormal operation 2 is in operation, abnormal operation 1 is not able to be activated by the control system.

  - The operator is to ensure that all valves are in the correct position to allow for this operation.

##### Controlled Shutdown

The hopper aeration system remains in operation while the unit has full hoppers and the blower will shutting down, once the ESP hoppers have been emptied and the DHP has shut down.

- When shutting down the hopper aeration system follows an automated shut down sequence.

- If the conditioning plant is required to remain in full operation, the ash bunker common aeration air system would be still in operation.

##### Condition monitoring

Local monitoring of the blower system is unitized on a unitized control desk in the unitized control room.

The following indications are provided as a minimum:

- Air delivery pressure.

- Temperature and flow transmitters.

- Lubricating oil pressure.

- Temperature and oil filter pressure drop (if applicable).

- Motor running current (preferably power) and running hours.

- Vibration monitoring.

- Intake filter pressure drop.

- User consumption monitoring using flow transmitters.

- Any other required by virtue of the design.

#### DHP Operating Philosophy

##### General

The DHP has two (2) operating modes:

- Normal operation.

- Backlog operation.

Each DHP Conveying Stream’s operating mode is independent of the other streams for the DHP for a specific unit.

The operating mode of the DHP is determined by the following:

- Under normal operating conditions, with the ESP hoppers operating at a low level (minimum bed depth), two of the three transfer conveyors and bucket elevator routes are running on low speed, with four hopper conveyor discharging into one route. DHP Conveying Stream operates at the normal operation mode.

- When a hopper level rises to a high level set point, then the DHP Conveying Streams on load will be still selected for low speed operation. (Backlog operation)

- If two of the three transfer conveyors and bucket elevator routes are out of operation, then all eight hoppers conveyors need to discharge ash into the one transfer conveyor and bucket elevator stream. This one-route transfer conveyors and bucket elevator will then operate on high speed operations and it would clear backlog conditions. The Unit Controller need to select the relevant transfer conveyors and bucket elevators low speed and high speed operations.

It is possible to have all three transfer conveyors and bucket elevators routes on low or high speed operations.

There is an interlock that limits the number of Conveying Streams that are able to convey simultaneously.

Under normal operation of the DHP, one (1) unit discharges ash into each of the ash bunker compartments. The ash bunker compartment that the DHP discharges to is manually selected by the operator.

- If one (1) of the ash bunker compartments continuous level sensors indicates a high level, the DHP discharging into that specific ash bunker, the feeding routes will stop and the OPCR personal need to select the other ash bunker compartment.

- When both compartments continuous level sensors show a high level then the DHP follows a controlled shut down.

- If a bunker compartment shows a high-high level the DHP discharging to that bunker compartment trips.

##### Start-up

During unit light up the DHP is available when the first mill is put into service and this is the point at which the DHP conveying sequence will start. The start-up sequence is fully automated and should not require any operator intervention for the sequence to be completed successfully.

During unit light up fuel oil is utilised, to convey the ash generated when oil and coal is burnt the DHP operates at an oily ash operating mode that allows for the oily ash to be effectively discharged from the hoppers, chain conveyors, double flap valves and the bucket elevators.

##### Controlled Shutdown / Unit Trip

When a unit is shutdown or trips the DHP remains in operation until all the ESP hoppers are emptied. To ensure that the hoppers are emptied before it is shut down the DHP completes the following steps:

- When the ESP hoppers reach a low level set point as indicated by the hopper low level sensor installed by Others, the DHP Conveying Stream associated with the ESP hoppers runs empty.

- Once the DHP conveyors and bucket elevators are empty, then the unit controller will shut down the hopper aeration air blowers and the DHP.

##### Conveying Stream Trip

- When a Transfer Conveyor and bucket elevator routes trip during conveying, this stream is able to restart under full load condition.

- When a Hopper Conveyor trips during conveying, this conveyor is able to restart under full load condition.

##### Transient Boiler Operation

During transient boiler operation it is possible that the conveying properties of the ash can change, the DHP still has to transport this fly ash under these conditions. Examples of situations when the conveying properties of the ash could change are but not limited to:

- When fuel oil is required to ensure that boiler remains in stable operation.

- When soot blowing is occurring.

- When there is a boiler tube leak.

- Change of ash particle size distribution due to changes in coal quality burnt by the boiler

#### Compressed Air System Operating Philosophy

##### General

During normal operation of the Plant and Materials within the compressed air system:

- Two (2) instrument air compressors are in operation.

  - There are two (2) compressors on standby.

  - When an operational compressor trips a standby compressor automatically starts up.

A rotational running policy is applied to the  instrument air compressors and is determined by the Contractor.

- During the rotation sequence, operating compressors shut down and standby compressors start up following a set sequence.

  - During the rotation the standby compressor starts before the operating compressor shuts down, once the standby compressor is fully operational then the operating compressor can shut down such that it can be placed on standby.

  - The rotation of compressors does not happen simultaneously but is staggered such that at no point are both standby compressors operational due to the rotation sequence.

- The rotation sequence will be achieved fully automatically by the control system, which is based on running hours of the compressors.

The Contractor develops alarms, trips and protections to inform the operator whenever an abnormal operation parameter arises.

- Whenever a low pressure is detected the standby compressors are started.

- When a high pressure is detected operational compressors are shut down.

The Contractor develops a rotational policy between operational and standby cooling towers/ pumps.

- During the rotation the standby cooling tower/ pump starts before the operating cooling tower/ pump shuts down.

- Once the standby cooling tower/ pump is fully operational then the operating cooling tower/ pump can shut down such that it can be placed on standby.

The Contractor ensures that if a cooling pump / tower trips that the standby equipment starts in a sufficient time such the compressors do not over heat.

##### Start-up

- During start-up of an instrument air compressor, the compressor and the auxiliary equipment associated with the compressor including the cooling system starts following an assigned start up sequence.

- During unit start-up, the compressors will supply control air to the ash hopper aeration pads control valves, if there are ash inside the hoppers. The unit controller need to start the DHP chain conveyor system, when the first mill is put into service allowing the DHP to operate at the oily operating mode.

- If multiple compressors are required to start at the same time, only one (1) compressor starts at a time and if required there is a time delay between compressors starting to ensure that the compressor switchgear is not overloaded.

##### Controlled Shutdown

When the DHP shutdown sequence is completed the instrument air compressor supply valves towards the ash hoppers will close and will still supply control air to the ash conditioners.

##### Condition monitoring

Local monitoring for the compressed air system is centralised on a common local instrument panel at OPCR. The following indications are provided as a minimum:

- Inter-stage air pressure and temperature.

- Air delivery pressure.

- Temperature and flow.

- Lubricating oil pressure and temperature.

- Motor running current and running hours.

- Vibration monitoring.

- Surge counter.

- Cooling water inlet.

- Inter-stage and outlet temperature and pressure.

- Intake filter pressure drop.

- Oil filter pressure drop.

- Inlet and blow off valve position.

- Vibration levels.

- Dew point temperatures.

- Bearing temperatures.

- Unit air consumption and ash conditioner control air consumption.

- Any other required by virtue of the design.

#### Compressed Air Cooling System Operating Philosophy

##### General

- Four (4) cooling towers are available and operational (unless maintenance is required on a cooling tower) with two (2) cooling towers being able to carry the heat load of all Plant and Materials within the compressed air system.

- Four (4) cooling water pumps are available with two (2) cooling pumps being able to supply the cooling water for all Plant and Materials within the compressed air system.

- The cooling system starts before the compressors or auxiliaries start.

#### Conditioning Plant Operating Philosophy

##### General

During normal operation:

- There are two (2) conditioners per ash bunker in operation, one (1) conditioner per ash bunker compartment and the other two (2) conditioners are on standby.

- The conditioners operate with both operating conditioners discharging onto one (1) conditioner conveyor as a default but the operating conditioners can also feed onto separate conditioner conveyors when required.

  - During abnormal conditions the operator is able to select that both conditioners servicing one (1) ash bunker compartment are operational at the same time if required.

The conditioners operate at two (2) capacities, defined by the level of the ash bunker compartment that the conditioner services. The level indication is supplied by the existing continuous level sensors installed on each of the ash bunker compartments.

- The conditioners operate at the following operating points when the bunker compartment is at the following levels.

  - Normal operation

    - Bunker compartment level 	: 10% to 40%.

    - Operational capacity		: 75 Tph (wet at 20% moisture content)

  - Backlog Operation

    - Bunker Compartment Level 	: Above 40% bunker level.

    - Operational Capacity		: 200 Tph (wet at 20% moisture content)

- When the backlog operating point is activated the conditioner reverts back to the normal operating point only when the level of the bunker drops below 20%.

- The minimum bed depth of the ash bunker compartments of 10%, is reviewed by the Contractor and changed if deemed necessary.

  - If a change is deemed necessary, the Contractor submits the new defined minimum bed depth and ash bunker operating levels defining the operation of the conditioners to the Project Manager for acceptance.

- Each conditioner is fitted with an ash vapour scrubber which is in operation at all times when the conditioner is in operation.

  - There is an interlock which prevents the conditioners from operating if the ash vapour scrubber is faulty or not available.

  - The ash vapour scrubber units are fully automated.

There are two (2) of three (3) conditioning water supply pumps operating at all times with the third pump on standby. The fourth pump is used for the ash dump dust suppression system.

- The flow of water to each conditioner is controlled by a flow control valve fitted to the water supply to each of the conditioners.

  - The conditioner water flow control valve position has set points for each operating capacity, however its position is adjusted according to the feedback received from the online moisture analysers.

    - An algorithm is developed such that the readings from both mass meters and online moisture analysers are utilised to calculate the output mass and moisture content of ash discharged from both conditioners feeding onto a conditioner conveyor.

- The return water supply piping is fitted with a globe valve which adjusts its position to regulate the backpressure to control the flow and pressure within the conditioner water supply system.

The conditioning plant has an interlock to prevent the conditioners from starting if there is no air supply to the conditioner air slides from the ash bunkers aeration air supply system. If the control air pressure is below 5 bar, then the ash conditioners will shut down. The ash conditioner control valves are using spring to close pneumatic actuators. The conditioning plant also has an interlock to prevent the conditioners from starting if there is low water supply pressure.

##### Start-up

The conditioners have a set start up sequence which is activated when the operator selects a conditioner to start.

- The following conditions need to be satisfied before a conditioner can start.

  - Ash bunker compartment serviced by the conditioner is above a level of 20%.

  - Ash vapour scrubber is operational.

- The conditioner starts at the normal operation set point.

- After a set period of time, when it is confirmed that the conditioner is operating correctly and the water supply is consistently supplying the correct quantity of water to the conditioner, the conditioner operation mode changes to the backlog operation set point if the ash bunker level is above 40%.

- As part of the start-up sequence there is a siren indicating that a conditioner is starting to any personnel in the conditioning plant area.

##### Controlled Shutdown

The conditioners have a set shut down sequence that is followed under all controlled shutdown conditions.

- An automatic wash-down cycle is included as part of the controlled shutdown sequence.

  - During the automated wash-down cycle the conditioner conveyor operates in reverse.

The conditioners automatically shut down when:

- The level of the ash bunker compartment which is serviced by a specific conditioner reaches a level of 10%, as this is the minimum bed depth of the ash bunker compartments.

  - The conditioners shut down following a shutdown sequence (determined by the Contractor) and are placed on standby.

- When the level of the ash bunker compartment reaches a level of 20%, the conditioner that was shut down automatically restarts following the start-up sequence.

#### HVAC

The Plant and Materials within the HVAC system is configured to operate on N+1 mode for redundancy where N is 2 (the number of HVAC air handling units  in service), including automatic change over between the operational and standby units in case of failure of any one (1) unit and at pre-set intervals to allow equal running time between the units.

In case of controller failure each unit is able to run and control the set points on its own. For example, controls are able to switch over operation of the units at specified intervals, for instance once every week to ensure equal operating time of both pumps. Manual override switch is also installed to have any HVAC equipment switched on by maintenance when required.

### Control Philosophy

The Contractor develops and supplies the control philosophy, functional design specification and the logics for all the designs of plant systems such as DHP, aeration air plant system and conditioner/scrubber plant within his scope of work.

### Reliability Philosophy

The Contractor allows for the following in his design

- The installation of the works does not negatively affect current power station performance and reliability (current plant outages and maintenance interventions are utilised in order to keep the plant in good operating condition).

- The works is designed and constructed, by the Contractor, using robust components suitable for operation in power station environment.

- The works reliability is achieved by utilising proven design principles to ensure that components are kept at low stress levels while operating at their design duty.

- Selection of appropriate materials allows the works to function reliably for the service life at the designed operating conditions without distortion, damage, or premature failure due thermal stress, erosion, or corrosion, thus offering high availability.

### Employer’s design of the DHP and Hopper control air compressor house building and unitised blower house buildings

The extent of the Employer’s design is as shown and described in the Employer’s drawings and Works Information which indicates what is to be supplied and built/installed.

Table 3 below highlights design responsibilities and related documentation, for clarity and completeness purposes.

Table 3 shows the items that the Contractor is to design as well as what is designed by the Employer. The matrix is not exhaustive and the extent of the Contractor’s design includes all work which, although not expressly noted, can reasonably be inferred from the Works Information.

Table 3: Design Matrix

| Design stage | Responsible party: |
| --- | --- |
| UNITISED BLOWER HOUSE BUILDINGS |  |
| Architectural and Structural |  |
| Design | Employer |
| Temporary works | Contractor |
| Provision of all as-built information | Contractor |
| Preparation of as-built drawings | Employer |
| Ventilation |  |
| Design | Contractor |
| Temporary works | Contractor |
| Preparation of as-built drawings | Contractor |
| Fire Protection |  |
| Design | Contractor |
| Temporary works | Contractor |
| Preparation of as-built drawings | Contractor |
| Small Power and Lighting, Earthing and Lightning Protection |  |
| Design | Contractor |
| Temporary works | Contractor |
| Preparation of as-built drawings | Contractor |
| DHP HOPPERS CONTROL AIR AND ASH CONDITIONERS CONTROL AIR COMPRESSOR HOUSE BUILDING |  |
| Architectural and Structural |  |
| Design | Contractor |
| Temporary works | Contractor |
| Provision of all as-built information | Contractor |
| Preparation of as-built drawings | Contractor |
| Ventilation |  |
| Design | Contractor |
| Temporary works | Contractor |
| Provision of all as-built information | Contractor |
| Preparation of as-built drawings | Contractor |
| Fire Protection |  |
| Design | Contractor |
| Temporary works | Contractor |
| Provision of all as-built information | Contractor |
| Preparation of as-built drawings | Contractor |
| Small Power and Lighting |  |
| Design | Contractor |
| Temporary works | Contractor |
| Provision of all as-built information | Contractor |
| Preparation of as-built drawings | Contractor |
| Earthing and Lightning Protection |  |
| Design | Contractor |
| Temporary works | Contractor |
| Provision of all as-built information | Contractor |
| Preparation of as-built drawings | Contractor |
| Overhead Crane |  |
| Design | Contractor |
| Temporary works | Contractor |
| Provision of all as-built information | Contractor |
| Preparation of as-built drawings | Contractor |

Note: The Contractor is referred to section 3.8 for explanation of provision of as-built information and preparation of as-built drawings.

The Contractor studies the unitised blower house drawings and submits confirmation with his tender that his process design and Plant and Materials selection conform to the building layout and design, confirmation to be accompanied by proposed plant and rigging methodologies. The Contractor need to design the control air/instrument air compressor house. Where the Contractor proposes modifications to the building’s design this is regarded as an alternative proposal; an alternative proposal is submitted in accordance with the Employer’s Standard Conditions of Tender. (i.e. Submit alternative proposals strictly in accordance with all the requirements of the tender documents, only if a main tender is also submitted). The alternative proposal is submitted with the main proposal together with a schedule that compares the requirements of the proposal documents with the alternative requirements the Contractor proposes.

During his detailed design of the mechanical system, the Contractor submits the size and weight of Plant and Materials selected to the Project Manager for reference against design loads used in the building’s design.

The Employer designed the Compressor house to house the ash conveying air compressors and the control air compressors. The conveying air compressors are not required anymore, but the control air compressors are still required. The Contractor can study these drawings and make proposal how to make the building smaller, so that this building can only host the control air compressors. This redesigned building should host the four control air compressors, four cooling water pumps, four open water circuit treatment chemical dosing pumps, four close circuit water treatment chemical dosing pumps and four cooling towers, next to this compressor house.

#### Blower House Building

The unitised blower house buildings are single storey steel braced portal frame with a dual pitched roof. The walls consist of double skin cavity masonry system, placed on the outside of the steel columns completely encasing the steel frame presenting a smooth masonry exterior. Each building is fitted with two (2) 7.5 ton SWL underslung curved monorail beams.

The unitised blower houses are located within the power island area of the power station between two (2) of the units ID fans. The drawings below show the location of each building and its position relative to existing and future infrastructure.

| Drawing number | Observation |
| --- | --- |
| 0.61/96022 | Location of the blower house buildings on the Power Station |
| 0.61/97384 | Location of the blower house buildings relative to the ID fans, and cable tunnels |

The Employers design is based on a blower with the following properties,

- Length: 3090 mm

- Width: 2850 mm

- Height: 2345 mm

- Weight: 4870 kg (inclusive of, blower, acoustic hood, motor and fluid)

The Contractor’s process design and Plant and Materials selection takes cognisance of the following constraints:

- Not to exceed loads for the ground slab and crawl beams

- Building position, layout and dimensions

- Building height and height to underside of crawl beams

- Door width and height

- Blower house plinths position and dimensions

- Proposed locations and sizes for the inlet fans, outlet louvers, and blower vent pipe openings

- Wall finishes

- Building fire rating (the building is 2 hour fire rated)

#### DHP hoppers and Ash conditioning Control Air/Instrument Air Compressor House Building

##### Structure and Layout

The compressor house building consists of the control air compressor house area, a LV substation, a MV substation and a HVAC room. The building comprises a steel and concrete portal frame structure with an adjacent concrete substation and HVAC room attached to it. The portal frame structure has an overhead travelling crane with a lifting SWL capacity of 6.3 tons and houses compressors, air dryers, pumps, a water tank tower, etc. The concrete part of the portal frame structure has brickwork infill, where the steel part has IBR sheeting covering. The substation building has a double storey reinforced concrete frame with brickwork infill. This attached substation houses the electrical switchgear equipment and the HVAC room houses the mechanical HVAC equipment. This building is constructed on reinforced concrete foundations.

##### Earthing and Lightning Protection

The Earthing and Lightning protection for the control air compressor house is as per drawing number 0.61/97195.

##### HVAC

The overall compressor house HVAC system design (including the local control stations) contained in the works is the responsibility of the Contractor. The design of the following related HVAC is provided as follows:

Table 4: Division of HVAC Work Schedule

| Description of work | HVAC works | HVAC local control station | Integration of Plant and Materials within the HVAC system and local control station into the existing BMS (or DCS) | Fire Detection | HVAC Power Supply and distribution |
| --- | --- | --- | --- | --- | --- |
| - Detailed Design | Contractor | Contractor | Contractor | Contractor | Contractor |
| - Plant and Materials selection; installation and as built drawings; Testing, balancing and commissioning Documentation; Operating Instruction and Maintenance Manuals; and Inspection Record Cards/Checklists | Contractor | Contractor | Contractor | Contractor | Contractor |

###### Plant Selection Criteria

The Contractor selects Plant and Materials which satisfies the following:

- The overall plant performance and efficiency specification.

- The specified reliability; and keep maintenance costs to a minimum.

- Local and statutory authorities and construction requirements.

- Space constraints.

- Local content.

- The specified and applicable standards confirmed in the specification including all the legal requirements in respect of safety and the prevention of environmental pollution.

- Facilitation of efficient manufacture, inspection, transportation, installation, maintenance, cleaning and repairs.

- Safe and satisfactory operation for a life expectancy of at least 20 years for direct expansion system under the conditions prevailing at Tutuka site.

- Prevention of undue stresses being produced by expansion and contraction due to temperature change and other local natural and manmade conditions.

- Plant operation of 365 day per annum, 24hrs per day.

- All materials from which the Plant and Materials are manufactured, is compatible with the intended duty and service conditions. All Plant and Materials are suitably treated and protected from corrosion.

- All electrical Plant and Materials, forming part of the specified Plant and Materials in the HVAC system are sealed against penetration by hose cleaning operations, and be also accessible for repair and maintenance.

All Plant and Materials selected meet the requirements specified in section 3.1.9.2.3

###### Design Conditions

The following design conditions have been used to size and select the Plant and Materials for HVAC system.

###### Outdoor Conditions

As per section 3.4.9

###### Indoor Conditions

The operating hours for the buildings are envisaged to be 24 hours throughout the year.

Table 5: Indoor conditions

| Area | Room Temperature | Relative Humidity | Filtration | Air Movement | Noise Level |
| --- | --- | --- | --- | --- | --- |
| DHP Hoppers Control Air Compressor House C&I Equipment room | 20 ± 2°C | Not Controlled, but monitored | 30-35% efficiency | <0.3 m/s | NC 40 |
| Switchgear room | 20 ± 2°C | Not Controlled, but monitored | 30-35% efficiency | <0.3 m/s | NC 45 |
| Compressor House | +6°C above ambient | Not Controlled, but monitored | 30-35% efficiency | <0.3 m/s | NC 80 |

###### DHP Hoppers & Ash Conditioning Control Air Compressor House Switchgear Rooms Air Handling Unit with Remote Condensing Units

The system is factory assembled, factory charged, factory run, tested of mentioned capacities, air-cooled, direct expansion type air conditioning system consisting of condensing units (outdoor). The system comprises of all accessible compressors, air cooled condenser, steel base for mounting the above components, refrigeration piping/circuit, fittings, valves, refrigerant and oil, controls and ancillaries.

###### DHP Hoppers & Ash Conditioning Control Air Compressor House Switchgear Rooms Air Handling Unit Control Philosophy (Z0419-000132-225)

The HVAC control philosophy can be found in control philosophy for the Tutuka Power Station Pulse Air System with document number Z0419-000132-225 found in Appendix I. The system facilitates the operation and control of individual rooms and is able to cater for partial load of which can be as low as 50% of the total load.

The system is the inverter two (2)-pipe cooling only system and each system/zone is to be based on air cooled outdoor unit/s connected via a single refrigerant circuit, comprising gas and liquid pipework up to indoor units.

The operation of the system is through local common controller to fully control the units and is able to accommodate alarm signals. The controller of the units is set up to control the return air temperature and programmed such that should the temperatures within the respective rooms rise above 28°C or should a fault occur on the running unit, the controller automatically starts the standby unit.

The controller is able to switch over operation of the units at specified intervals, for instance once every week, to ensure equal operating time of both units.  Manual override switches are installed to have any HVAC equipment switched on by maintenance when required.

The controller accommodates fault signals with date and time, which sends a signal to the DCS in case of any failure or other parameter faults on the unit. The common controller indicates the operating status of the unit and malfunction by means of readout displays and audible alarm of the following malfunctions:

- System fault (Signal to be made available to the DCS)

- Loss of Air Flow

- Clogged or Dirty Filters

- High Room Temperature(Signal to be made available to the DCS)

- Low Room Temperature

- High Room Humidity

- AC failure to be connected at the incoming power point of the air conditioning units or isolators on load side of isolator.

The common controller is compatible to connect with Fire Detection System and Building Management System (BMS) of standard makes.

###### FFP and DHP Compressor House Switchgear Rooms Air Handling Unit Alarms

| Description | Tag | Unit | Normal value | LL | L | H | HH |
| --- | --- | --- | --- | --- | --- | --- | --- |
| DHP Hoppers & Ash conditioning Control air Compressor House LV Electrical Room Temperature Tx | 00YB10T001XQ01 | ºC | 20±2 |  |  | 26 | 28 |
| DHP Hoppers & Ash conditioning Control air Compressor House MV Electrical Room Temperature Tx | 00YB20T001XQ01 | ºC | 20±2 |  |  | 26 | 28 |
| DHP Hoppers & Ash conditioning Control air Compressor House C&I Equipment Room Temperature Tx | 00YH11T001XQ01 | ºC | 20±2 |  |  | 23 | 26 |
| DHP Hoppers & Ash conditioning Control air Compressor House HVAC Room Temperature Tx | 00ZC10T001XQ01 | ºC | 20±2 |  |  | 26 | 28 |

###### DHP Hoppers & Ash conditioning Control air Compressor House Switchgear Rooms Air Handling Unit Start Up Sequence

The HVAC sequence of operation is as follows:

- The discharge dampers of the running units are activated in the open position

- Supply air fan of the running units are started

- The complete refrigeration system(s) of the respective running units are started

- The fresh air fans start 5 minutes after the direct expansion air-conditioning units are running

###### Air Handling Unit Requirements

Fan delivery does not decrease more than 10% when filters are dirty, or increase more than 10% when operating under maximum return air conditions.  The operation point is in the stable part of curve.

Fan motor is non-overloading at any operating point between zero external pressures and break off point impeller.

Safety protection is provided for the motors as follows, unless otherwise specified:

- Single phase motors:		Thermal overload protection

- Three phase motors:	 	Combined thermal overload and phase failure protection.

All necessary instrumentation, including  bulkhead plenum lights, inspection and testing provisions (including location) to enable the operator to log performance and identify malfunctioning of equipment, in accordance with trouble shooting instructions, are installed and grouped together in such a way as to facilitate logging with maximum accuracy and reduce operator's time to a minimum.

Unit casing has the following minimum requirements:

- All air handling units are a maximum of 2.1 m high and 1.3 m wide to allow sufficient maintenance access.

- The factory assembled, sectionalised double wall insulated casing provides repair and removal access through easily removable panels to the various unit parts like fan and coils.

- Sealed type bulkhead plenum lights with compact fluorescents are provided in each separate compartment.

- A light switch with pilot light is provided next to the access door leading into the compartment.

- The light fittings and wiring is moisture proof.

- Insulation is in accordance with general insulation requirements.

- Casing construction is in accordance with SMACNA Standards or approved equal.

- Access doors are installed in the casing where shown, and where required for inspection, maintenance and replacement of equipment, instruments and controls.

- Access doors are of the walk in type, minimum 600 mm wide and 2100 mm high, consisting of a double skin insulated door, panel and frame.  The frame is provided with a profiled rubber seal.

- Access doors are of the hinged type and open against the air pressure. The two (2) (minimum) door handles are of robust construction.  An external lock is provided.  The doors are to open from inside and outside.

- Access doors to the spray plenum incorporate a double glazed view window.

- The roof and sides are suitably reinforced to carry the panel's own weight, people traffic and the air pressure differential.

- Unit is airtight and weather proof, suitable for mounting in exposed locations subject to wind, rain and hail.

Unit pre-filter and main filter banks have the following minimum requirements:

- Filter frame is suitable for standard commercial range of filter elements and filter media available.

- Air filter gauges provided for each filter bank.

- Adequate personnel access space is provided for filter removal and replacement.

- The filter elements and filter frame are corrosion protected.  Construction of filter frame and method of holding down filter elements allows no passage of unfiltered air through filter bank.

- Each unit has primary and secondary filters.

- Primary filters on all the units are of the same type and size namely “duplex panel filters” with size 600 mm x 600m x 50 mm deep. These filters have a high dust holding capacity. The primary filters are washable.

- Secondary filters on all the units are of the same type and size namely “glass fibre pocket filters” 600 mm x 600 mm x 600 mm deep. The secondary filters are disposable.

Unit cooling coil section has the following minimum requirements:

- Coil sections have heavy duty coil tracks extending the full width of the unit to provide easy slip in, slip out coils for ease of service and maintenance.

- Piping connections to coils are flanged and are arranged such that independent coil replacement is possible.

- Each coil is provided with its own Type 316 stainless steel drip tray to prevent flooding of lower coils by condensate.

- Cooling coil, connections and return bends are tested to 2000 kPa and rated for operation at 1700 kPa.

- The coil sections have a marine grade (Type 316) stainless steel frame.

Supply fan section has the following minimum requirements:

- The supply fan is of the centrifugal type with backward curved impeller or vane axial type as listed in the schedule.

- The fan motor is suitable for speed control.

- Fan and motor assembly is installed on a steel channel base and isolated from the supporting structure by spring vibration isolators and neoprene pads.

- Bearings are self-aligning, pillow block regreaseable, selected for an average life of 200 000 hours at design operating conditions.

- Fan wheels are keyed to the shaft and designed for continuous operation at the maximum rated fan speed and motor load.  Select fans and shafts operate at least 25% below the first critical speed.  Fan wheels and shafts are statically and dynamically balanced as an assembly. After final assembly, the entire unit is tested for vibration.

- Fans are belt driven with adjustable sheave and have readily adjustable provision to provide variation in centre distance.

- Belts are of the oil resistant type and selected for 10 000 operating hours at a minimum of 1.2 times the motor rating and one (1) slip free start per day.

- The motor is a totally enclosed fan cooled type. The motor starter, motor and drive are selected to ensure slip free starting without unacceptable voltage drop.

- The fan is selected assuming a pressure drop across the filter equal to the average pressure drop caused by the filter in its clean and dirty states and operating at maximum supply air volume.

Automatic dampers have the following minimum requirements:

- The dampers are the opposed blade type and interlinked with a robust geared mechanism.

- The blades are aerofoil section with neoprene blade seal at one (1) edge; not wider than 165 mm; and supported at intervals of not more than 800 mm by maintenance free non lubrication type bearings.

- The operating mechanisms are within the overall size of the damper frame, except for the drive arm and the motor platform.

- The arm is clearly visible and marked "open closed".

- The leakage rate, with the damper in a fully closed position is not to be more than 0.150 m³/s/m² at a pressure differential of 100 Pa.

###### Condensing Unit (Outdoor Unit) Requirements

The condensing units are capable of providing cooling and heating within the ambient range of -5°C to 50°C DB. The system is self-intelligent to run on low outdoor ambient conditions for better power consumption.

The condensing unit is capable of assessing the requirement of liquid refrigerant volumetric flow of the air handling unit at all times by means of a controller and generating the required total volume of refrigerant liquid for supply to the air handling unit.

The condensing unit is a factory-assembled unit housed in a sturdy weather proof casing constructed from rust proof galvanized powder coated steel panels. The unit is completely factory wired tested with all necessary controls. The noise levels of the unit are not more than 70dB (A) measured horizontally 1 m away and 1.5 m above base level. The sound data is measured in accordance with ARI standard 575 or SANS applicable standard.

The compressors are be hermetically sealed inverter driven variable speed type scroll or rotary type, with multiple steps of capacity control capable of changing the capacity in accordance to the cooling or heating load requirement. All condensing units are provided with multiple compressors and are able operate at part load in case of failure to other compressor. The outdoor units are to employ a system of equal run time for all the compressors.

The condensing units are filled with low noise, aero-spiral design fan with grill for spiral discharge airflow to reduce pressure loss and be fitted with DC fan motor to better efficiency. The unit is capable of adequate external static pressure and be designed to operate safely when connected to multiple fan coil units.

The condenser coil is the air cooled type with copper tubes and aluminium fins. The condenser coils are constructed out of copper tubes mechanically bonded to aluminium fins to form a cross fin coil. The surface of the condenser coil is coated with anti-corrosion resin film to prevent deterioration.

The refrigeration circuit has liquid and gas shut off valves or solenoid valves at condenser end. The refrigerant control is through the electronic expansion valve (EEV). The following safety devices are provided as minimum to ensure safe operation of the system:

- High pressure for inverter switch;

- Fan drive overload protector;

- Over current relay for inverter;

- Inverter overload protector;

- Short re-cycling guard timer;

- Fuse crankcase heater, Fusible plug; and

- Auto re-starts on power supply interruption

The units are equipped with a highly efficient oil separation system to ensure stable operation with long refrigerant piping. High efficiency oil separation is fitted to the discharge side of the compressor together with factory oil equalisation system which is factory assembled and tested.

The condensing units are located in open on a terrace with adequate clearance from nearby objects to ensure unobstructed air flow and easy approach for maintenance.

The condensing units are installed onto the concrete plinth or against the outside by means of channel frames with stainless steel bolts/chemical anchors. Vibration eliminators are installed between the condensing unit frames and the supporting brackets.

###### High Wall Mounted Comfort Cooling Units (DHP Hoppers & Ash conditioning Control air Compressor House C&I Equipment Room) Requirements

The Contractor provides high wall mounted comfort cooling units for the Control Air Compressor House C&I Equipment room as detailed by the drawings 0.61/97200 Sheets 1 to 2, 0.61/97205 Sheets 1 to 40 and the specifications in Appendix N. The units are to consist of an indoor unit and matching air cooled outdoor condenser unit from the same manufacturer, including all accessories.

The unit has a rigid steel frame work with cover plates which will accommodate the supply fan and motor, direct expansion cooling coil, control and condensing units.

The indoor unit fan is a line flow fan type and will be able to deliver supply air at three (3) different speeds. Each remote control unit has the facility to adjust the fan speed between low, medium and high. The supply fan motor operates on a single phase power supply and facilitates the three (3) speed operation.

The cooling coil consists of aluminium fins mechanical bonded to copper tubes. The coil accommodates the heat pump facility. This unit is fitted with an anti-freeze stat.

The unit is equipped with a drip tray manufactured from galvanized steel. The condensate is drained to the nearest drain point. The condensate lines are equipped with a water trap and the lines are made of I.D Ø25mm x O.D Ø26mm PVC tubing which are properly secured to the building structure.

The condensing units consist of a compressor, condenser coil, fan, refrigerant accessories and the necessary controls.

The split units are fitted with a controller to fully control the operation of the units and accommodate alarm signals. The controller of the units is to be set up to control on the return air temperature and programmed such that should the temperatures within the respective rooms rise above 28°C or should a fault occur on the running unit, the controller automatically starts the standby unit.

The controller switches over operation of the units at specified intervals, for instance once every week, to ensure equal operating time of both units.  Manual override switch is installed to have any HVAC equipment switched on by maintenance when required.

The controller accommodates fault signals with date and time, which will send a signal to the DCS in case of any failure or other parameter faults on the unit. The common controller indicates the operating status of the unit and malfunction by means of readout displays and audible alarm of the following malfunctions:

- System fault (Signal to be made available to the DCS)

- Loss of Air Flow

- Clogged or Dirty Filters

- High Room Temperature (Signal to be made available to the DCS)

- Low Room Temperature

- High Room Humidity

- AC failure to be connected at the incoming power point of the air conditioning units or isolators on load side of isolator.

###### Refrigerant

The Contractor supplies refrigerant gas, R410A or equivalent gas. The entire condensing and evaporative units are factory assembled and tested and come with an initial charge of R410A or equivalent gas from the factory. Any additional refrigerant required is added onsite during the execution and guarantee period, by the Contractor.

###### Refrigerant Piping

The Contractor supplies and installs the refrigeration piping system in accordance with the drawings 0.61/97200 Sheets 1 to 2.

New refrigerant piping is used for this installation and the Contractor allows for adequate piping in both sizes of refrigerant piping. Each refrigerant pipe set is installed in its own trunking. The trunking is cleaned after the completion of the installation. The Contractor ensures that the installation on the inside of the building is neat and of good workmanship nature.

The refrigerant piping on the outside of the building is installed in galvanized trunking of at least 100 x 76mm. The galvanized trunking runs the entire outside distance from the condenser unit to the indoor unit and no refrigerant piping or drain piping is visible inside the room.

Refrigerant piping between indoor and outdoor units located above false ceilings are supported along its entire length by a galvanised perforated cable tray of sufficient size to allow pipe work to be neatly laid out and insulated. The cable tray is supported clear of fixing surface by galvanised brackets allowing air space between cable tray and mounting surface.

Where piping and insulation is exposed to damage, a galvanised sheet metal cover having a minimum thickness of 0.8mm is neatly formed and secured to the cable tray brackets.  Joints are lapped by a minimum of 30mm and to have a minimum clearance of 10 mm over insulation.

The suction line pipe size and the liquid line pipe sizes are selected according to the manufacturers specified outside diameter. All refrigerant pipes are properly supported and anchored to the building structure using steel hangers, anchors, brackets, and supports which are fixed to the building structure by means of inserts or expansion shields of adequate size and number to support the load imposed thereon.

The refrigerant piping interconnecting to indoor & outdoor units is made out of hard/soft copper tubes, in brazed construction. The refrigerant line sizing is designed to achieve minimum pressure drop and avoid oil return problem. The pipe sizes and connections are designed such that the evaporator units do not face back pressure due to the functioning of the evaporator next to it.

All refrigerant piping for the air-conditioning system is constructed from soft seamless piping up to 19.1 mm and hard drawn copper refrigerant pipes for above 19.1 mm with copper fittings and silver soldered joints.

The refrigerant piping arrangements are in accordance with good practices within the air conditioning industry, and include charging connections, suction line insulation and all other items normally forming part of proper refrigerant circuits.

The thickness of copper piping is not less than that mentioned below:

Table 6: Thickness of refrigerant copper piping

| Pipe Size (OD) in mm | Wall thickness in mm |
| --- | --- |
| 54.10 | 1.5 |
| 41.28 | 1.3 |
| 34.93 | 1.3 |
| 28.58 | 1.2 |
| 22.22 | 1.0 |
| 19.05 | 1.0 |
| 15.88 | 1.0 |
| 12.7 | 0.8 |
| 9.52 | 0.8 |
| 6.35 | 0.8 |

The refrigerant piping suspended from the roof slab are supported by trapeze hangers manufactured from galvanised mild steel angle iron, suspended from the slab by threaded rods. The threaded rods are screwed into expanding anchors in the slab. The refrigeration piping running along the walls are clamped to cable tray sections fixed to the wall. The maximum support spacing for refrigerant piping is as follows:

Table 7: Maximum Support Spacing for refrigerant piping

| Pipe Size (OD) in mm | Maximum Support Spacing (mm) |
| --- | --- |
| 15.9 | 1500 |
| 15.9 to 25.4 | 2000 |
| 25.4 to 41.3 | 3000 |
| 41.3 and up | 4000 |

The refrigerant piping system is selected to satisfy the following:

- To minimise loss of lubricating oil from compressor at all times.

- To ensure lubricating oil return to compressor, at the same rate at which it leaves under all load conditions.

- To prevent lubricating oil being trapped in system.

- To prevent liquid refrigerant from entering the compressor during operation and shutdown.

- For minimum pressure drop and noise generation.  The suction, discharge and liquid lines are to be sized so that the pressure drops do not cause a change in saturation temperature of refrigerant greater than 1.1 °C in each respective line.

- For handling the specified capacities from 100% down to minimum load at specified suction and discharge/condensing temperature.

Refrigerant piping accessories and connections are selected to ensure no leakage from refrigerant piping system during its operational life.

Refrigerant piping system is complete with all necessary isolating valves to enable repairs and maintenance to be carried out on any one section of the system.

The refrigerant accessories are connected and installed into the refrigerant piping system such that, either a sub component replacement or total removal and reinstallation of the accessory does not take longer than two (2) hours by qualified refrigeration mechanics.

The refrigeration piping system, including accessories, thermal insulation, hangers, supports and vibration isolators are selected and installed to give a minimum working life of fifteen (15) years under normal building service conditions.

All joints in copper piping are sweat joints using low temperature brazing and or silver solder. Before joining any copper pipe or fitting, its interiors are thoroughly cleaned by passing a clean cloth via wire or cable through its entire length. The piping is continuously kept clean of dirt etc. while constructing the joints. The entire refrigerant piping system is subjected to a leak pressure test with a suitable gas, e.g. clean dry air or nitrogen.  It is permissible to add system refrigerant to enable leakages to be more easily detected.

Prior to carrying leak pressure test, the Contractor verifies by examination of the various parts of the components of the system that the test pressure to which they were subjected at the manufacturer's works, are adequate for the required duties.

The Contractor incorporates a safety valve or rupture disc in the piping system. Rupture discs are to have a specified and certified bursting pressure at a specified temperature and marked accordingly on the disc.

The system complies with the Safety Code for Refrigerant Piping ASA B31.35–1962, with the requirements of ASME, with Occupational Health and Safety Act as amended, and with local authority’s by laws.

The refrigeration piping is stored and handled on site to prevent dirt from entering piping system.  Open ends are plugged.

Where required for connection to gauges and control devices, tubing not larger than nominal 10 mm may be type K soft (annealed) with flared tube fittings suitable for high pressure.

Accessories connected to copper tubing have solder type ends or flanged ends and soldered flange adaptors.

Piping is installed so as to allow for expansion and contraction. Suction and discharge lines are installed so that the first point of support is six (6) pipe diameters in each of three (3) directions from the unit.

System vibration isolation is in accordance with Sound and Vibration Control requirements.

Thermal insulation of suction line is in accordance with insulation requirements.

Piping is installed parallel or perpendicular to building construction, while maintaining the required gradients.

All necessary pressure gauges are installed in refrigerant lines to check pressures and temperatures for load monitoring function of various accessories and possible blockages of strainers.

Isolate accessories requiring regular inspection, cleaning and removal by shut off valves to enable this without pump down of the entire refrigeration system.

Liquid receivers have the following minimum requirements:

- Each receiver has sufficient capacity to hold all refrigerant in the system to which it is connected, except that in plants having two (2) or more separate refrigerant circuits cross connected by pump out piping.

- The receiver has sufficient capacity to hold all refrigerant in the largest circuit. Receiver capacity is based on not over 85% of its internal volume being occupied by liquid. Receiver has liquid level indication.

Liquid suction interchanger has the following minimum requirements:

- Heat exchangers for field assembled systems are the standard products of a reputable manufacturer.  Field fabrication of heat exchangers is not permitted.

- Heat exchangers for field assembled systems are the shell and tube, shell and coil or double tube type. Tubes are seamless copper, plain or with integrally formed fins.  Shells are welded steel, conforming to the requirements of the latest edition of the Mines and Works Act or the Machinery, Factories and Building Work Act and Regulations, covering pressure vessels. Gas passages are arranged so as to prevent trapping of oil.  Refrigerant driers have the following minimum requirements:

- Refrigerant driers for field assembled systems are the angle type with removable cartridges that can be renewed without disturbing pipe connections. Driers have brass or steel bodies and solder joint connections. Bonnets are flanged and bolted. Cartridges are charged with dry silica gel or activated alumina, held securely in place without restraining normal expansion, and provided with suitable means for distributing the refrigerant evenly through the charge. Unless otherwise indicated driers are installed in liquid lines close to the receiver outlets and be provided with valves on the inlet and outlet connections.  Valve by-passes are also provided unless the driers are of a type guaranteed by the manufacturer to operate indefinitely without dusting of the desiccant or appreciable increase in pressure drop.  A liquid sight glass and moisture indicator of the colour change type is installed in the liquid line, close to each drier.

- Select each drier so that the pressure drop through the drier does not exceed 14 kPa when operating at full connected evaporator capacity.

- Drier cartridges are not installed until after pressure and vacuum tests have been completed but immediately prior to charging

Thermostatic Expansion Valves have the following minimum requirements:

- In field assembled systems, each evaporator circuit is provided with a thermal expansion valve of the gas charged type.

- Valves have external equalizer connections, external superheat adjustments with seal caps and solder joints or flanged pipe connections.

- Valves move from fully open to fully close with not more than 3 °C superheat change. Superheat setting is 6 °C at full load. Each valve is provided with an external strainer, regardless of any internal strainer that may be incorporated in the construction. Strainers are specified under "Refrigerant Strainers".

Oil Separators have the following minimum requirements:

- Each reciprocating compressor having suction and/or liquid mains more than 15 m long is equipped with a discharge line oil separator.

- Separators are made of welded steel and have an effective impingement type separating element, an oil sump and a float operated return trap connected to them to return oil to the compressor automatically.

Refrigerant stop and shut-off valves have the following minimum requirements:

- Refrigerant stop valves generally are back seating key operated, sealed cap type.  Valves which are opened and closed in regular operation to have pack-less type hand wheels.

Refrigerant strainers have the following minimum requirements:

- Refrigerant strainers are of the angle type, cleanable without disturbing pipe connections. 40 mm NB strainers and smaller have brass bodies and solder joint connections. 50mm NB strainers and larger have brass or rust proofed steel or iron bodies and flanged connections.  Connections are flanged and bolted.

- Screens are bronze with perforations not larger than 0.25 mm for liquid lines and 0.5 mm for gas lines. The free area of each screen is not less than 5 times the area of the strainer inlet pipe.

Charging valves are located in the liquid line between the receiver shut-off valve and expansion valve.

Provide external gauge connections at inlet and outlet of condenser, evaporator coil and compressor to enable evaluation of system pressures at commissioning and for normal maintenance inspections.

All gauges are connected to the refrigerant piping system through isolating shut off valves.

Liquid indicators are sight glass - double port with seal cap type - of full size in the main liquid line before the thermostatic expansion valve.

The solenoid valves have manual override to enable the system to continue to operate in case of solenoid coil failure.

Vibration Isolators (flexible connectors) have the following minimum requirements:

- Suction and discharge lines from the compressor are fitted with flexible connectors of the bronze braided hose type, having sweat-ends, to fit over copper tubing having the same size as the line in which they are installed.

- Locate flexible connector as close as possible to the compressor and parallel to the compressor shaft. It is not subjected to compression or extensions.

- For refrigeration installation utilising a remote air cooled or evaporative condenser, hot gas mufflers are used to remove pulsations from the hot gas discharge and thereby reduce noise and vibration from the piping system.  The hot gas muffler is installed to prevent accumulation of oil.

The complete refrigeration piping system is pressure tested with dry nitrogen and a leak test is carried out. Test pressure is maintained for 24 hours with no loss in pressure. Complete system is evacuated and proved to be free of moisture. The system stands for a minimum of 12 hours with no change in vacuum. The system is liquid charged on high side following purging of connections to the estimated total charge. Minor adjustment to the charge is carried out during the 12 hour test run. The following method is recommended for pressure leak testing:

- Use a mixture of nitrogen & trace refrigerant in conjunction with one of the following suitable leak detection methods: Acceptable leak test methods include, Liquid submersion testing, soap bubble leak detection, fluorescent leak detection & electronic leak testing or any acceptable standard.

- Pressurise the complete system with dry nitrogen & leak test using any acceptable method.

- Having ensured there are no leaks using a) or b) above, the system is pressurised to a safe test pressure. Observe over a period of time, relative to the size of the system that no pressure drop occurs, having due regard to temperature variation throughout the system.

- After determining that there are no refrigerant leaks when the system is pressurised, the system is evacuated to remove moisture & air. Evacuation must be deep evacuation method, or triple evacuation using dry nitrogen only as the moisture absorber (to be witnessed by Supervisor).

- DEEP VACUUM METHOD: Pull a deep vacuum to a pressure of less than 13 Pa absolute (100 microns of mercury). After isolation the vacuum pump, allow the system to stand for 60 minutes to ensure the vacuum is maintained at or below 16 Pa absolute (120 microns of mercury), OR

- TRIPLE EVACUATION METHOD: Use a vacuum pump to pull a vacuum to a pressure of at least 260 Pa absolute (2,000 microns of mercury). Break the vacuum with dry nitrogen & allow the system to stand. Re-evacuate the system & repeat the procedure twice more, breaking the vacuum each time with dry nitrogen.

- The final evacuation is held for 12 hours with no loss of vacuum. After the system has been evacuated the vacuum pump is isolated from the system and as guide, with constant ambient conditions’ the vacuum does not rise above 13 Pa absolute (100 microns of mercury) in 1 hour. A greater rate of rise may indicate a leak. Absolute vacuums should be measured using accurate measuring equipment selected for the specific application.

Expansion valves and solenoids are stripped before welding refrigerant pipes so as to avoid overheating and associated damage to seals, or they are to be kept at constant temperature by means of damp rags.

Should the refrigerant piping run longer than normal, the amount of refrigerant oil is increased in the pipe system as per the manufacture’s specification.

###### Drain Piping

Each air conditioning unit is provided with suitable PVC or galvanised drain piping 32 mm or 25 mm diameter that rises to a maximum allowable height in accordance with manufacturer’s specification, so as to create the correct trap arrangement.

The drain piping on the outside of the building is extended to the water gutter that runs around the building. Each drain piping set has a suitable P-trap depth.

The Contractor allows for adequate PVC drain piping for each air conditioning unit. The first 2 m of the drain piping from the indoor unit are covered with non-drip tape to ensure no condensation around the drain pipes on the inside of the building. The drain piping is supported every two meters by mean of brackets.

###### Mechanical Ventilation Fans

Safety protection is provided for the motors as follows, unless otherwise specified:

- Single phase motors:		Thermal overload protection.

- Three phase motors:		Combined thermal overload and phase failure protection.

The maximum allowable downtime for installed fans is such that replacement does not take longer than 2 hours when executed by qualified building maintenance staff.

The Contractor submits service, maintenance, troubleshooting and testing instructions in order to obtain acceptance approval. Documentation is indexed in accordance with the equipment part of the Operating & Maintenance Manuals.

- Fans are provided complete with standard flanges.

- Bearings are the permanently lubricated type.

- Air flow arrow indicators are installed for each fan unit.

- Fans are direct driven, suitable for mounting at any angle and mounted on vibration isolation mountings.

- Motor rating is not less than the maximum power required by the fan at any operating point between zero and break off capacity.

- Fan casing is insulated with high density acoustic insulation to limit break out noise to the occupied space.

- The fan motor is provided with manually adjustable speed controller to deliver the specified air quantity where required.

The Contactor installs fan assemblies in accordance with manufacturer's recommendations. The Contractor supplies the necessary field testing instruments and detailed description of field testing arrangement to prove a capacity/performance measurement accuracy of ± 5% for the fan acceptance testing. Certified test results are plotted on the official published and certified equipment performance graph/table to confirm that claimed performance is achieved. The various tests as required by the QMS are demonstrated and accessible to the Project Manager at all times for monitoring.

Centrifugal Fans

Centrifugal fans are multi-bladed type with forward or backward curbed blades. The bearings may be of the sleeve, ball or roller type, they are selected and fitted for quiet operation, as recommended by the bearing manufacturer. The impellers and casings are rustproof to prevent corrosion.

The fans are direct drive type and the motor is the standard type that is easily replaceable and is either sleeve or ball bearing type. Maximum speed of the motor is 1450 RPM.

Propeller Fans

Propeller fans are the ring-mounted type when operating without ducting, and of the diaphragm-mounted type when mounted in ducting.

The bearings are the sleeve type, except where the shaft of the fan is mounted vertically, when ball or roller bearings are used. The motors are totally enclosed, single-phase up to 380 mm diameter. Where fans are handling moist air, all components of the fan and motor are suitable for operation in saturated atmospheres.

Axial Flow Fans

Impellers are genuine aerofoil design and incorporate an adjustable blade pitch feature facilitating factory or site resetting of fan duty. Hubs and blades are die cast in aluminium silicon alloy materials, assembled with high tensile zinc plated steel bolts and nuts. Complete units are statically and dynamically balanced.

The fan casings are hot dip galvanised after manufacture. Standard casing lengths cover the overall length of the impeller and motor assemblies. External terminal boxes are provided on the casings of fans fitted with standard totally enclosed motors. Where flameproof motors are fitted electrical connections are integral with the motors and external connections are not provided.

###### Testing and Commissioning

General

After the completion of the installations and when all pressure testing is complete, the Contractor sets the Plant and Materials to work and regulate control valves to demonstrate that the installations are functioning correctly and efficiently to the complete satisfaction of the Supervisor.

Items of specialist nature e.g. automatic controls are commissioned by the manufacturer or their representative, who instructs the Employers personnel on the function and proper operation of the Plant and Materials.

All test instruments required during commissioning are provided by the Contractor together with any other Equipment they may require.

Inspection prior to testing and commissioning

Prior to tests taking place on the completed or a section of the installation the Contractor checks the following points:

- That the components comprising of the installation or sections of an installation are installed as described in the specification and drawings.

- That the components have been installed correctly.

- That the manufacturer‘s test data for Plant and Materials, if necessary for testing and commissioning, is provided and is available for reference.

Cleaning and flushing of ductwork and pipe work systems

All pipe work and ductwork systems included in this contract are thoroughly cleaned internally to remove any foreign matter. The following operations are completed by the Contractor:

- The cleaning of completed pipe work and ductwork to remove dirt etc. accumulated in pipe work and ductwork during installation by flushing out the installation.

- The external cleaning of all pipe work and ductwork carried out to remove surplus jointing material, paper labels, dirt and grease.

Testing

The site testing of the various installations take place prior to the application of thermal insulation. High and low pressure ductwork is tested for air tightness, using the system fan or fans, by observation and air flow measurement. The sum total of measured air quantities at all outlets (supply system) and inlets (extract system) are compared with the air quantity measured in the adjacent main duct. Any discrepancy greater than plus or minus 5% for low velocity and 1% for high velocity indicate that unacceptable leakage exists and should be remedied.

All leakage tests are witnessed by the Supervisor and are independent of any performance tests on the whole system, which is as detailed elsewhere in this specification.

Installations or sections thereof, which is embedded in the structure or concealed in permanently sealed ducts or voids, etc., is, in addition to the above specified tests, individually tested as they are laid and before being concealed.

On completion of the installation the Contractor carries out sound tests to measure the sound pressure level in each octave band in each space, under the supervision of the Supervisor and with all plant running. The Contractor uses a sound analyser with one (1) octave band range 63 to 8000 Hz to establish the sound spectrum on each space. In carrying out these analyses the Contractor pays particular regard to the following points:

- All items of mechanical services plant or equipment is running normally.

- Areas adjacent to these areas being tested are unoccupied.

- There are no interference from the Contractor’s Equipment or from any other abnormal noise source.

- The microphone is between 1 and 2 meters from floor level.

- Microphone is not held in air velocities greater than 1.2 m/sec and in any case never nearer than 1,2 m from a noise source such as grilles, diffusers etc.

- An average of three (3) readings is to be taken for each area for each octave band

- Sample readings of background noise dBA are taken with Plant and Materials not in operation before and after noise reading in any one area.

##### Electrical Designs

The Employer will provide the following documentation/drawings:

- Proposed Substation Layouts

- Conceptual Single Line Drawings

#### Compressor house HVAC Drawings and Submissions

The drawings, Plant and Materials selection and Sample submissions are to be handled as follows:

##### Employer’s Drawings

The HVAC drawings prepared by the Employer show general layout of all Plant and Materials and distribution systems, complete with schematic arrangements. These, together with the specification, give sufficient information to enable the Contractor to estimate the cost and to determine how the system is installed, tested, balanced, inspected, operated, serviced and maintained. These drawings are not dimensioned shop drawings, and cannot be used as shop drawings. Location dimensions shown are only indicative of the routes and zones in which the service must be installed.

The following drawings are applicable and issued with this tender documentation for tendering purposes only and are updated by the Contractor with the information based on the Plant and Materials selected by the Contractor:

Table 8: HVAC Drawings

| Drawing No. | Sheet No. | Revision | Title |
| --- | --- | --- | --- |
| 0.61/97200 | 1 | 0 | FFP and DHP Compressor House HVAC P&ID |
| 0.61/97200 | 2 | 0 | FFP and DHP Compressor House HVAC P&ID |
| 0.61/97205 | 1-40 | 0 | FFP and DHP Compressor House |

##### Contractor’s Plant and Materials Selection, Drawings and Sample Submissions

The Contractor is responsible for Plant and Materials selection including installation/shop based on the Employer’s design and that such shop drawing/s are submitted to the Project Manager for acceptance prior to procurement and manufacture of any Plant and Materials.

The selection, construction details and shop drawings/installation arrangements for Plant and Materials are carried out in accordance with the manufacturer/supplier/authoritative sources (SANS, ASHRAE, SMACNA and other applicable international standards) official published literature, documentation, design and applicable manuals. Where these details are non-existent or not sufficient, reference are made to the sections and detail drawings of the Employer.

##### Plant and Materials Selection

The Contractor is to select Plant and Materials which comply with the specifications and submits these to the Project Manager for acceptance.

The Contractor does not install Plant and Materials if the selected Plant and Materials deviates from the Employers design or deviates from the accepted Plant and Materials offered, or if the Plant and Materials selection submission has not been accepted by the Project Manager.

##### Shop Drawings

Shop drawings are to indicate all Plant and Materials, distribution systems, testing/inspection/instrumentation positions, access requirements and builder's work requirements. Shop drawings are be based on the Employer's design shown on the detailed design drawings.

The Contractor is to review, stamp all shop drawings to confirm that co-ordination with building and services drawings have taken place before submitting to the Project Manager for acceptance.

The Contractor’s drawings are prepared in accordance with SANS 10111: Engineering drawing practice. General arrangement and detailed drawings be intelligently cross referenced.

##### “As built” drawings

The Contractor is to provide “As Built” drawings based on the shop drawings embodying all modifications made during construction. The “As Built” drawings are to include floor and ceiling layout drawings indicating all terminal and/or fan coil units and/or controller positions. Safety, instrumentation, control and operation drawings are also to be included “As Built” drawings indicating the intended functioning, capacity data and control functioning of all systems.

##### Samples

Samples are any Samples required by the Project Manager which may be over and above those listed in the Samples below.

The Project Manager reserves the right to call for Samples of the Plant and Materials offered and for the Supervisor to inspect the workmanship as the work proceeds and to either accept or reject the Plant and Materials or workmanship. The Supervisor acceptance of the workmanship, Plant and Materials in no way reduces the Contractor's liability to provide a complete and proper working Plant and Materials, which is abreast with modern technology.

The Contractor is to submit the following Samples to the Project Manager for acceptance:

- Constant volume terminals (CAV)

- Supply grilles

- Weather louvers

- Ductwork complete with insulation.

All such Samples are retained until Completion of the contract. All such Samples have securely attached thereto labels designating the contract by name and number (if any), the name of the Contractor and any further relevant information.

The Contractor is to ensure that the Plant and Materials complies with the specified requirement before arranging for the Supervisor’s factory acceptance inspections. The Contractor makes arrangements for the Supervisor to inspect the following items of Plant and Materials before they are dispatched to Site as part of quality management:

- Air conditioning units

- Ductwork

The purpose of these inspections is to reduce the risk of non-compliant Plant and Materials being transported to Site. The inspections do not reduce the Contractor’s responsibility to comply with the contract.

### Updating the Employer’s Design

The Project Manager informs the Contractor of any changes to the tender drawings and provides him with all the relevant update drawings in the agreed upon time.

## Parts of the works which the Contractor is to design

The Contractor has to modify the Compressor house design with its HVAC, electrical , controls, lifting equipment, transformers, MV switchgears and LV switchgears so that it houses the control air compressors with all its auxiliaries.  All reasonable precautions are taken in the design of the works to ensure the safety of personnel concerned with the operation and maintenance of the works. Safety, isolation, locking and interlocking facilities comply with the relevant standards and requirements within the Works Information.

The Contractor completes his design fit for purpose according to the specifications set forth in the Works Information.

The Contractor designs, supplies and installs the following:

### Mechanical

#### Hopper Aeration system

- Hopper aeration aeration pad support casings and membranes.

- Modifications to the hoppers to facilitate fitment of aeration pads in the valleys between the hopper walls. [LOSS-06-08-02]

- Hopper aeration blower trains and heaters.

- Relocation of the fuel oil pipeline in the area where the blower house is positioned.

  - Including the removal of the existing fuel oil pipe between the ESP casings and the flue gas outlet ducting to the smoke stacks.

  - The Contractor installs isolation valves where the Contractor’s rerouted piping is reconnected to the existing piping.

  - A suitable pressure relief valve is installed (if required) on both the supply and return pipeline as specified by BS EN ISO 23251:2007 + A1:2008.

- The aeration system must not reduce the temperature of the fly ash.

- Each hopper must be able to be isolated from the air supply.

- The aeration system must aerate the ash sufficiently to increase its flow ability.

- The air must be clean and dry, heated to minimise temperature drop on the fly ash inside the hopper.

- The air aeration system will consist of aeration pads fitted to the inside of each hopper to facilitate the aeration of the ash.

- The air supply to the aeration pads will be supplied by a dedicated air supply system per unit, consisting of 2 x 100% blowers in a blower house.

- The blower house will be equipped with as a minimum fire detection (which must interface with the existing station fire detection system), lighting, lifting equipment, air filtration equipment and will be pressurised.

- The aeration blowers must be air-cooled and the noise level should be below 65 decibels.

- The dry air piping must be able to resist corrosion at all operating conditions.

- The aeration blowers will be fitted with energy efficient heating system, to ensure that the aeration air temperature is at a minimum of 130 degree Celsius at the ash hoppers.

- The plant must be easily maintainable without the need for specialised equipment/tools.

- All air supply valves, piping, insulation, instrumentation and pipe supports including structural members, fasteners and clamps.

- The Contractor proposes as an alternative option for an optimised hopper aeration system such that the system is not aerating the ash at all times but only when the aeration is required if the DHP is in its backlog operating mode.

3.2.1.2   Ash bunker aeration air system

- There are three ash bunker complexes on the Power Station.  Each ash bunkers complex has two ash bunker compartments and each ash bunker compartment has one ash conditioner. With six boilers on load, then there are three ash conditioners in operation.

- Bunker aeration system with its rotary air distributor valves stays the same. The electric 380 V actuators and butterfly valves needs replacements on all the six ash bunker compartments and the manual isolated gate valves needs replacement on all six the ash bunker compartments.  The aeration air volume control valves need replacements on all the six ash bunker compartments. New conditioner feed airslide piping including all valves, instrumentation and pipe supports need to the design, supplied and installed by the Contractor.

- There are three aeration air blowers for the ash conditioners and the contractor is to design, select, supply, install, test and commission a fourth blower which will tie-into the existing blowers aeration air common discharge pipe line. This blower should be air cooled and be  equipped with air pressure reducing valve in case of pipe blockages.

- These blowers are on the first floor of the ash bunkers. New control air pipe lines and valves are needed for the additional conditioners and additional blower air intake filters.

- The control air for the blower intake filters cleaning needs to be dry and these filters are self-cleaning air filters. New crawl beams with crawlers are needed for the existing and new aeration air blowers.

- The fourth aeration blower must be air cooled.

- The dry air piping must be able to resist corrosion at all operating conditions.

- The fourth aeration air blower must be easily maintainable without the need for specialised equipment/tools.

- The fourth aeration air blower should have pressure relief system via silencers into the atmosphere, in case if there is a discharge pipe blockage.

#### 3.2.1.3    Dust Handling Plant

The current Dust Handling Plant (DHP) is designed to collect ash from the ESP’s which have an uneven ash collection distribution from field 1 to field 5 due to the nature of the ESP’s operation.

The quality of the coal that is being received by Tutuka has deteriorated since the commissioning of the station, which has resulted in an increase in the quantities of ash that the DHP needs to transport. The Power Station Load factor for the remaining life of the station is approximately 30% and the maximum ash load per boiler should be 61 tons per hour. The DHP will need to be upgraded to align the capacities of the DHP with the selected design base ash quantities that will be produced by the boilers.

Field:                            1                2                  3                  4                5                 Total

Ash distribution:         84%          12%              3 %             0.8%         0.20%

Recovery Time hrs:    12, 74         0, 25            0, 65           0, 16         0, 04            13, 84

The current ash hoppers are fitted with agitating chains and a stirrer, which facilitate the agitation of the ash to prevent problems with the ash discharge from the hoppers. This system will be retained and an air aeration system will be installed which will become the primary means of agitating the ash. The aeration system will aerate the ash by supplying air into the ash via aeration pads. The hopper discharge components sizes needs to be design check and selected to ensure that the chute, slide gate valves and single flap valves do no restrict the ash flow from the hoppers.

The DHP accepts ash from the precipitator hoppers and transport it via conveyors and bucket elevators to a dust distributor, which distributes the ash into the selected ash bunker. There are three routes which run independently of each other. Routes 1 and 3 both have two transfer conveyors which can run at low or high speed. Route 2 has one dust transfer conveyor which also runs at low or high speed. The bucket elevators in Routes 1 and 3 can run at low and high speed. Bucket elevator B (2) can only run at low speed. The normal operating condition for above drives is at low speed.

The eight precipitator hopper conveyors are common to all routes. Conveyors A, B, C and D deposit material into dust transfer conveyors A1 and C1. Conveyors E, F, G and H deposit material into dust transfer conveyors A2, B and C2.  The precipitator conveyors are selected for a route via the selection of slide gates underneath the conveyors. There are two slide gates each for conveyors A, B, C and D and three slide gates each for conveyors E,F,G and H. The slide gates are manually operated and selected. Only one slide gate per route may be open at one time.

In the normal running condition all eight precipitator conveyors must be running, but not into a single route. Not more than four hopper conveyors should be selected on one route. In emergency mode it may be possible for all eight hopper conveyors to charge onto a single route on high speed.

The fly ash sometimes does not flow freely from the ash hoppers into the hopper conveyors and this dust plant takes about 72 hours to clear a backlog. The transfer conveyor (A,B & C) and bucket elevator routes A and C are operating all the time on high speed. The existing conveyor drives are absolute and it take a long duration to repair. The existing dust plant vacuum system is not sufficient to have the dust plant under vacuum.

- The Mechanical Engineering scope required is to an assessment on the exiting conveyor system and upgrade the existing mechanical infrastructure that will ensure backlog recoveries of 80 tons per hour. The chains and liners wear must be minimum. The chains and wear rails should last for 7 years and the bucket elevator chains should last 33 000 hours. The chain conveyors liners should last for 14 years. This will include the assessment of the existing infrastructure, design, procure and upgrade the existing dust handling plant and the dust plant venting system.

- The hopper conveyors casing height should be the same from the first hoppers up to the second hopper and then a bit smaller from the second hopper up to the third hoppers, which would ensure the third hopper rows would not take too long to get empty.

- Care must be taken in order not to overload the hopper conveyors. The new drives should last for 100 000 hours and the spares availability for these drives should be locally available for 21 years. There must be low speed couplings between the gearboxes and the conveyor drive shaft plummer boxes. The new drives should use torque arms and the service factor of these new drives should be 1,6 based on motor size. The new drives should have a dust/water ingress prevention rating of IP65 and the noise levels should be below 65 decibels at full load.

- The Mechanical Engineering scope required is to upgrade the existing dust plant venting system, so that the dust plant can operate under vacuum conditions. The bunker vacuum must be measured before proceeding with the design.

- Basic maintenance on the DHP (lubrication, chain replacement, drive replacement, chain tension adjustments and chain joints) must be able to be done with the unit on load.

- The ash must be able to be deposited into either of the bunker compartments.

- The chain conveyors and bucket elevators must have operational modes with different speeds for normal operation and backlog operation.

- The operational mode must be able to be selected from the control room and locally.

- The bucket elevators must have a specific speed setting that will be used for inspections.

- The chain conveyor chains and wear rails should be able to last for a minimum of 7 years and the chain liners should be able to last 14 years. The bucket elevator chains should last 33 000 hours.

- The hoppers must be kept at a low level at all times in case of hopper conveyor repairs and the relevant hoppers can be used as a buffer.

- Upgrading the DHP utilising the existing chain conveyor and bucket elevator technology.

- A new transfer conveyor (B1) feeding onto the current B transfer chain conveyor will be installed to collect ash from hopper chain conveyors A – D. This will improve the system redundancy to provide for a 3 x 100% transfer conveyor/bucket elevator stream capability.

- The contractor need to take fly ash samples from the plant and do a chemical elemental analysis, particle diameter determination and particle volume distribution measurements across all the different particle sizes, and determine the fly ash density range.

- The ash hopper filling times must be obtained by the precipitator consultant to determine the hopper conveyor mass flow rate for maximum operation and back log recovery flow rate.

- The ash hoppers discharge chutes, slide gate valves and the single flap valves sizes need to be designed checked and selected, in order to prevent ash bridge at the hoppers discharges. Care must be taken, so that the hopper conveyors must not get flooded. Ash floor dumping equipment from each hopper and hopper water washing chutes should be part of this design. The water should drain directly onto the concrete floor during precipitator washing. Hopper fly ash floor dumping should be done by using valves controls.

- The ash hopper discharge chutes with its equipment should be upgraded, so that it can also discharges directing into the transfer conveyor casings in the case where the relevant hopper conveyor is not available. The first three hopper conveyor rows from the precipitator inlet should have this emerging ashing function. These hopper by pass systems should have manual operating valves for safe fly ash discharging into the relevant transfer conveyors.

- The chain conveyors and bucket elevators must be able to operate at different speeds to facilitate the change from normal operation to emergency operation, where only one route is available. The changeover process from one transfer conveyor/bucket elevator route to another route must be operator friendly. The Contractor has to design, supply and install these down pipes with aeration air pads to ensure free ash flow.

- The double flap valves and its chutes sizes need to be verified to make sure that all the fly ash per hopper conveyor can flow freely into the selected transfer conveyors under back log recovery operation mode.

- All the chain conveyor drives and double flap valves drives needs to be replaced with new model drives with low speed couplings between the gearboxes and the drive shafts plummer blocks. New drives service factor should be 1,6 based on motor size.

- The bucket elevator capacity flow rates must be design reviewed to determine that it would handle the ash flow rate under emergency mode where one transfer/bucket elevator stream is available. The new or existing bucket elevator drives should have low speed couplings between the gearboxes and bucket elevator drive shafts plummer blocks.

- There must be no dust leaks at the chain conveyor shafts during backlog recovery mode operation and the whole plant should be under vacuum.

- All components of the current system that will be re-used will be assessed and replaced or refurbished, if required.

- The current crawl beam and hoist system located at the 45m level of the ash bunker cannot resist the loads from the bucket elevator drives and needs to be replace. The new crawl beam and hoist should be capable to safely lift the bucket elevator drives and lower them down to the ground level. The existing crawl beam support structure should be reviewed to ensure it can resist the loads from the new crawl beam and if not capable, the structure should be modified or replaced. The crawl beam support structure should include a roof covering to allow for the safe storage of the hoist from the weather when the hoist is not in use.

- Change the orientation of the bucket elevator drives as these leak oil and it is difficult to do motor direction checks.

- The drive hold back should be easily removable without needing to remove the drive gearbox.

- A canopy should be installed on top of the ash bunker over the drive stations of the bucket elevators to protect the bucket elevator drives from weather exposure.

- Electrical requirements for the system will be reviewed.

- The C&I system will be reviewed and upgraded where required.

- Additional DHP equipment and the aeration system will be interfaced with the new DCS.

- Replacement of the existing hopper slide gates. [LOSS-06-08-01]

#### Compressed Air System

- Instrument air compressors in the DHP common compressor house for all six (6) units.

- All compressor auxiliaries e.g. water traps, driers, filters, air receivers, cooling systems, including associated electrical and C&I plant, etc.

- Supply a temporary mobile compressor to start up and commission the instrument compressed air systems. The temporary mobile compressor delivers compressed air at the same quality as the new instrument air system (-30 to -40 °C pressure dew point). After start up, testing and commissioning the temporary mobile compressor is removed from Site.

- Dedicated instrument air piping from the compressor house to each unit’s DHP Hoppers.

  - Pipe supports including structural members, fasteners and clamps, for the DHP compressed air pipe supports up to the terminal points shown on drawing 0.61/97205 Sheets 1 to 40.

  - Pipe supports including structural members, fasteners and clamps, for the DHP compressed air pipe supports up the terminal point of the existing ash conditioning system control air common pipe.

- All valves for the compressor system including automatic condensate drain valves on the compressed air supply piping.

- Cooling water supply:

  - Demineralised water piping and associated valves from the water treatment plant to the compressor house and to the DHP compressed air make-up water head tank. [LOSS-EE-08-02, LOSS-06-08-04]

  - Potable water piping and associated valves from the emergency potable water head tank outlet to the compressor house and to the DHP cooling tower water ponds. [LOSS-EE-08-03, LOSS-06-08-03]

  - Cooling water pipe supports including structural members, fasteners and clamps for the DHP Hoppers Instrument Compressors pipe supports and the compressors cooling water pipe supports up to the DHP Hoppers aeration equipment (compressors, air dryers, pumps and cooling towers).

  - Compressor cooling system blowdown and compressor house drainage piping and associated valves from the compressor house and compressor cooling system to the station drains. [LOSS-06-08-05]

#### Conditioning Plant

- New conditioners installed in the ash bunkers.

  - The Contractor removes all the ash from ash bunker to facilitate the installation of the new conditioners and the replacement of the existing 6 ash conditioners.

- Plant and Materials for the conditioner feed system which conveys the ash from the ash bunker compartment to the conditioner [LOSS-SS-AA-05].

- A wet ash vapour scrubber system with all water supply piping/valves on each conditioner.

- Online moisture analysers and mass meters installed on each of the conditioner conveyors.

- Conditioning water supply system water piping with all associated valves, instruments and pipe supports [LOSS-EE-08-05].

  - Pipe supports include structural members, fasteners and clamps.

- A self-cleaning strainer in the conditioning water supply system.

- Flow meters and flow control devices to facilitate accurate water supply and supply measurement to the conditioners.

- Conditioning water supply pumps.[LOSS-EE-08-05]

  - This includes any pipes, valves, actuators, pipe supports, fittings, concrete plinths, pump basis necessary to integrate the new pumps with the new suction and discharge manifolds (21.61/55241).

  - New common supply pipes, supports and valves from the effluent pump house to each ash conditioner.

  - New water flow control system to each ash conditioner.

- Interfacing of the new conditioners water supply piping to the existing emergency potable water supply pipework [LOSS-EE-08-04].

- New Crawl beams for the new ash conditioners and the replacement of the Crane Aid 10 ton electric hoist, with slings, load cells and hook. This hoist to have a chain operated trolley car. Lift height is 20 meters. Load test certificate to be issued, after load testing.

- The Contractor can propose a system such that the flow of ash supplied to the conditioner from the ash bunker can be measured as an alternative option for the ash feed to the conditioners.

- Modifications required to the ash bunker structure for the installation of the upgraded conditioning plant.

- The Contractor reviews the uses of an inverted cone to promote constant discharge from the ash bunker. This proposal is submitted and an alternative option and is subject to the approval by the Project Manager

- The proposal is to install the new ash conditioners first on the plant and commissioned it. If the new ash conditioners are proven, then the existing ash conditioners can be replaced with new ash conditioners. These installations and replacements can be done while the units are on load.

- The contractor is to determine if the existing dirty water supply system is sufficient for the 12 ash conditioners. If not, then the dirty water supply system needs upgrading.

- The contractor is also to determine if the conditioner conveyors can handle the amount of ash from two ash conditioners. If not, then these conveyors and moving heads needs to be upgraded.

- The new scrubbers must be able to minimise the ash particles from the conditioner surroundings and discharge this dust/slurry into the relevant ash conditioner. These scrubbers should use dirty water.

### HVAC

- Ventilation in the unitised blower house buildings.

- HVAC for ash bunker 1, 2 and ash bunker 3 substations.

  - Controls for the Plant and Materials for the HVAC system as well as any connection between units are to be supplied and installed by the Contractor to ensure operation of all units according to the Employers design requirements

  - HVAC electrical system power and associated interfaces

  - HVAC control system and interfacing with fire detection system and building management system

- HVAC in the DHP Hoppers control air compressor house needs to be designed by the Contractor. (0.61/97200 sheets 1 and 2) including but not limited to:

  - Supply, installation, testing and commissioning of two (2) (100% each) split units with auxiliaries to service the DHP Compressor House C&I Equipment room.

  - Supply, installation, testing and commissioning of three (3) (50% each) ducted direct expansion industrial air handling units together with condensing units and auxiliaries to service the switchgear room.

  - Supply, installation, testing and commissioning of a fresh air supply fan with filters to complement the ducted direct expansion industrial air handling units.

  - Supply, installation, testing and commissioning of 8 (six (6) in operation and two (2) on standby)  wall mounted axial flow fans together with roof mounted ridge louvres and auxiliaries to service the DHP Hoppers compressor house.

  - Supply, install, test and commission ducting and return air grilles from the direct expansion industrial air handling units to their respective areas

  - Design, supply, install and test local control stations for all HVAC equipment

  - Interface all HVAC local control stations with the existing BMS

### Electrical

The Contractor is responsible for the following as a minimum:

- Provide a preliminary electrical load list (Refer to Table P2 in Appendix P).

- Complete the compliance schedule (Refer to Table P2 in Appendix P).

- A design philosophy which will be used to design the electrical system.  This philosophy is a discussion on the methodology used, to design the required electrical systems.

Once the Contractor completes detail design and has selected specific Plant and Materials, he provides the Project Manager with the design and Plant and Materials specifications so that the Employer can update their design in accordance with the new information received.

The Contractor adheres to 36-681 Generation Plant Safety Regulations and 32-846 Operating Regulations for High Voltage Systems for all electrical work.

The Contractor’s scope of work includes the following electrical works namely:

#### LV Switchgear

- Complete the Technical Schedule A & B (Refer to Section 6.3).

- Use the existing 380V Ash Bunker Boards 1A-3A, and 1C-3C. these buckets with its switchgears would need cleaning and replacement of any relays, contactors and thermal overload switches. The fourth aeration air blower for the ash bunkers can be use the existing spare switch gear in bunker boards 1A/B. The internals need to be design, selects, procure, install and commissioned for the additional aeration air blower motor. A new power and earth cable needs to be design, select, installed, pressure testing and commissioned from this switch gear up to the fourth aeration air blower.

- The existing transfer conveyor B which would need a bigger two speed drive and the existing switchgear needs upgrading for units 2 and 6 dust handling plants.  This upgraded transfer conveyor B will becomes the B2 transfer conveyor and the new two-speed motor size is 7,5/15 kW. Additional new B1 transfer conveyor for units 2 and 6 will need a new bucket and switchgear in the existing bunker boards 1A/B. This motor size should be 5,5/7,5 kW two speed motors. New power and earth cables would be needed for the new additional B1 transfer conveyor and for the existing upgraded B2 transfer conveyors for units 2 and unit 6. The existing bucket elevator B on units 2 and 6 is a single speed 15 kW drive and this drive needs to be replaced with a new 16/32 kW two speed drive with the new gearbox. The existing 15 kW switch gear needs to be upgraded for a 16/32 kW motor. The existing 15 kW power cable can be used for the new 16 kW low speed motor and an additional cable needs to be designed, select, install, pressure test and commission for the 32 kW high speed motor.

- The existing hopper conveyor geared motors, transfer conveyor geared motors and double flap valve motors/gearboxes need replacements on unit 2 and unit 6. The bucket elevator drives at unit 6 needs replacements and the bucket elevator drives on unit 2 needs refurbishment.

- Design, procure, install, test and commission new LV switchgear to replace the existing 380V Ash Bunker Boards 1A-3A and 1C-3C (See Figure R1, R2 and R3, in Appendix R, for the respective substation layouts).  The Contractor installs new LV Switchgears in the existing Ash Bunker substations, it is preferred that there are no modifications required to the substation buildings.  The Contractor is responsible for the removal of the existing ash bunker boards to a designated area as indicated by the Project Manager.

- Design, procure, install, test and commission new LV switchgear for the common DHP equipment and auxiliaries. The Employer supplies a maximum of two 3 phase 50Hz supply points with a combined power rating of 5.15MVA at 3.3kV per board. The four supply points are allocated on 3.3kV FFP Cleaning Air Equipment Board A&B. The Contractor is responsible for installing these boards within the substation. The new LV switchgear including battery charges, UPSs and battery cabinets are housed in the common compressor substation. The Employer provides proposed layouts of the switchgear and associated electrical equipment (See drawing 0.61/97205).

- The IED’s for all LV Switchgears, for incomers and bus-sections, will be free issued by Others. The Contractor is responsible for the engineering and design of the LV Switchgear including protection and control schemes with these IED’s. The Contractor is responsible for installing these IED’s. The configuration of the said IED’s is implemented by Others.

- The Contractor develops single line diagrams for the electrical reticulation.  The Employer has provided conceptual single line diagrams with drawing numbers 0.61/93933, 0.61/1703, 0.61/96067 and 0.61/96069 (Refer to Section 7) for information only.

- The existing switchgear rooms should be upgraded with new HVAC systems should be installed to keep temperatures between 18 degree Celsius and 24 degree Celsius, at positive pressure to keep dust outside the buildings.

- While there is a high likelihood that existing 380V Ash Bunker Boards could be sufficient for the upgrade, the scope of the project includes an assessment of this switchgear to determine available capacity and suitability, with partial or full replacement being a possibility.

- The requirement of new smart relays for all chain conveyors and bucket elevators will influence this, as retrofitting of existing switchgear might not be possible or practical. Space constraints between panels has also been identified as a potential challenge.

- The scope also includes supplies and cables for additional aeration air blowers. For this, there is a high likelihood that additional switchgear and cabling for the conditioner conveyor drives will also be required.

- In all likelihood, all motors on the plant will be replaced, together with all power cabling. New cable racks will be installed where necessary.

New Electrical Loads

The scope includes a full load flow and fault study to determine the impact of increased loading on the existing switchgear and upstream reticulation system, as well as a review and possible revision of electrical protection settings.

There are a number of new unitised loads that will be added to the Dust Handling Plant, for which power and suitable protection will be required. Some of these loads will be situated in dedicated blower rooms that are still to be built.

- Additional transfer conveyor per unit.

- Additional aeration blower for the ash bunkers and ash conditioners.

- Six (6) additional Ash Conditioners

- Twelve (12) additional Scrubbers.

- Two new hopper aeration air blowers per unit.

- Two (2) air dryer systems per aeration blower.

- Two (2) isolation valves per aeration blower.

- Lighting, small power and ventilation in new Blower Rooms.

- Four (4) Instrument air compressors.

- Four (4) air compressors water cooling pumps.

- Four (4) air compressor demin water cooling pumps.

- Open circuit water treatment system with four (4) 100% chemical dosing pumps.

- Close circuit water treatment system with four (4) 100% chemical dosing pumps.

Once detailed design of mechanical plant has been finalised, and a complete electrical load list has been confirmed and submitted, electrical requirements will be reviewed and finalised accordingly.

Drive Requirements

- Service Factors of 1.6 is required for all new drives, based on motor size. Drive motors should have a locked rotor duration of 15 seconds when the motor is hot. New motor sizes should be 50% bigger than the conveyors and bucket elevators power absorption.

- The new motors must be IP65 rated, with standard B5 type mounting flanges. Motors should be locally available for 21 years, with bearings rated for 100,000 hours of useful life.

Hoist Winch Upgrade

- At present, the system has a built-in hoist winch that trips on load cell, due to maximum weight capacity. The scope includes modification of the mechanical structure to allow for increased weight capacity.

- In the event that an upgrade to the drive motor is required, this could in turn result in upgrades to the cable and switchgear bucket supplying the drive motor. However, there is a high likelihood that the correct gearbox ratios will be sufficient to accommodate the increased load capacity, without any changes required to the drive motor. Either way, this can only be determined during detailed design, once mechanical design has been finalised.

- The 10 ton electric host with it travel trolley needs to be replaced at the ash conditioner floor level.

Design Review of Electrical Requirements

- The scope includes a design survey to examine all existing services which may be affected by the Dust Handling Plant upgrade project, and to ensure that all requirements are covered by the upgrade. This includes a full assessment of the loading on 380V Ash Bunker Boards, either to confirm their suitability or to provide recommendations for partial/full upgrades.

- Once mechanical detailed design has been finalised and after complete load list has been confirmed and submitted, electrical requirements will be reviewed and finalised accordingly.

#### Transformers

- Complete the Technical Schedule A&B (Refer to Section 6.3)

- Design, procure, install, test and commission new dry type transformers to replace the existing 1250kVA 11/0.4kV Dyn11 dry type ash bunker transformers. The Contractor is responsible for the removal of the existing ash bunker transformers to a designated area as indicated by the Project Manager.

- Design, procure, install, test and commission new oil and dry type transformers to supply the common compressor house switchgears.

- The Employer provides proposed transformer layout drawings (Refer to Appendix R).

#### Essential and Standby Power

- Complete the schedule A&B (Refer to Section 6.3).

- Design, procure, install, test and commission new 220V DC self contained battery chargers (SCBC) to replace the existing 220V DC ash bunker BTUs (Refer to Figure R1, R2 and R3, in Appendix R, for the respective proposed substation layouts). The Contractor is responsible for the removal of the existing ash bunker BTU’s to a designated area as indicated by the Project Manager.

- Design, procure, install, test and commission new 220V DC SCBC in the common compressor house substation to supply the DC requirements for the new LV Switchgear.

- Design, procure, install, test and commission new 220V AC UPS in the common compressor house substation to supply the AC requirements for Control and Instrumentation. This also includes the batteries and battery cabinets.

#### Cabling and Racking

- Design, procure, install, test and commission new cabling and racking required for the common compressor house loads. The Contractor provides all protection and power cabling required for the works including the cable terminations and transformer cable termination compounds.

- Dismantle and remove the existing cabling from the 11/0.38kV ash bunker transformers to the existing 380V ash bunker boards 1A-3A, 1B-3B and 1C-3C. The Contractor is responsible for the removal of the existing cables to a designated area as indicated by the Project Manager.

- Design, procure, install, test and commission new cabling and racking from the new 380V ash bunker boards 1A-3A, 1B-3B and 1C-3C to the unitised blower house loads for units 1-6 including existing loads on the old 380V ash bunker boards that is required for the ESP. The cable termination to the 11kV unit boards will be done by Others.

- Design, procure, install, test and commission new cabling and racking for the supply cables to the SCBC and UPS’s as while as cabling to the loads.

- The Contractor is responsible for the marking of the switchgear room floor for additional cable entry holes. The drilling of holes in the floor and sealing of the holes that becomes redundant is the responsibility of the Contractor.

#### Small Power and Lighting

- Design, procure, install, test and commission the lighting and small power system for the unitised blower houses.

- Ensure that the all applicable standards are adhered to once all equipment in the ash bunker substations is installed.

- Design, procure, install, test and commission the lighting and small power system for the new DHP compressor house.

- Design, procure, install, test and commission the lighting and small power system for the ash bunker substations.

#### Lightning and Earthing Protection

- Conduct a lightning protection study for the DHP and associated system.

- Design, procure, install, test and commission new earthmat, earthing and lightning protection for the new unitised blower house where the new blowers are installed.

- Design, procure, install, test and commission new earthing of the DHP, conditioning plant and associated system to the existing earthmat.

- Connect the unitised blower house earthmat to the main station earthing mat.

- Procure, install, test and commission new earthing for the new DHP compressor house as per the design given in 3.1.9.2.2.  Any updates or changes, that will be required during execution of the given design, must be communicated to the Employer as per the Project Engineering Change Management Procedure. The Contractor is responsible to produce and supply any auxiliary documentation that will assist in the successful execution of this design.

### Control and Instrumentation

#### General

The Contractor refers to Appendix S for the portion of the scope to be considered as a takeout option during the tendering process,

- The Contractor is responsible for the design, procurement, installation and commissioning of new Plant and Materials and systems for the compressor plant system (instrument air), hopper aeration air plant system (unitised blowers), upgrade of existing DHP and upgraded conditioner/scrubber plant C&I systems. The design, procurement, installation and commissioning include the following as a minimum:

- C&I field cabling

- C&I field cable termination in the junction boxes/enclosures

- Power cabling, analogue junction boxes, digital junction boxes, conduits and trunking.

- Interface hopper aeration air plant system and DHP system with the ABB unit control systems in Units 4-6 (The Contractor designs for new HMI mimics with operator control options) and the new unit control system installed by Others for Units 1-3. The Contractor design up to the interface junction box/enclosures and liaises with Others in Unit 1-3.

- Interface conditioning/scrubber plant and compressed air system with outside plant Yokogawa system (including designs for new HMI mimics with operator control options).

- Interface of the new fire protection and detection to the existing station BMS.

- Extension or expansion of PA and communication system to the new compressor house and the blower  house

- The Contractor is responsible for optimization of the controls of the DHP, hopper aeration, conditioning/scrubber and compressor systems.

- New field instruments, drives, actuators, junction boxes, local control stations and cabling for the new DHP, aeration, conditioner/scrubber and compressor systems.

- Local Control Station’s / Panels are installed for the new DHP, blower house, pneumatic compressor system and conditioner/scrubber system.

- Power supply requirements for all C&I associated Plant and Materials within the Contractor’s scope of work.

- Field cabling conduits, trunking and routing to the localised junction boxes/enclosures for entire DHP system, aeration air plant, conditioning plant and sub systems.

- If applicable, programming devices, software, licensing and copyrights for DHP and associated systems (hopper aeration, conditioner/scrubber and compressor).

- Interface the conditioner effluent supply pump systems and associated systems such as the self-cleaning filter system to the water plant control room.

- The Contractor ensures monitoring of all water flow meters (within his scope) in the water treatment plant control room.

- The Contractor ensures monitoring of all instrumentation (within his scope) for the ash conditioning water supply system in the water treatment plant control room

- Provision of DHP, aeration air system, conditioning/scrubber and compressor plant systems functional design specification, control and protection philosophies.

- Earthing and lightning protection for all Plant and Materials for the C&I systems within the Contractor’s scope of work.

- The Contractor develops and supplies logic drawings for the Plant and Materials system designs within the Contractor’s scope of work and interface with Others to ensure the correct implementation in the DCS. The responsibility for the correct operation and implementation of these philosophies in the DCS remains the responsibility of the Contractor.

- The Contractor is responsible for safety clearances of power supply interfaces on field instrumentation, actuators, field panels, junction boxes, compressor/blower controllers power supply, DCS cubicles within his scope and all the other equipment that forms part of his scope of the design.

- Documentation which include updated operational procedures (affected by change/modification), product manuals, C&I system configuration documentation and maintenance procedures.

- The Contractor is required to provide information and documentation in accordance with the requirements set out in this Works Information

#### Unit 1 - 3

The boiler/turbine auxiliary control system replacement project for Unit 1 - 3 completed by Others coincides with the DHP project during a planned outage. The Contractor interfaces with Others for provision and coordination of information to realise the control/operating philosophy and commissioning of the DHP and aeration system. There will be a new DCS installation for Unit 1 - 3 at Tutuka P.S. and the solution is such that:

- The Contractor is responsible for the C&I design of the works, and works in conjunction with Others to realise the control/operating philosophy and commissioning of the DHP and aeration air plant system.

- The Contractor provides for the designs from the field design up to the localised junction boxes and enclosures in Unit 1-3 (The design includes supply of and terminations in the junction boxes/enclosures). Interfacing to Unit 1-3 DCS is by Others. Documentation/Drawings are provided for all Plant and Materials designs as well as affected plant areas in accordance with the requirements of the new DCS supplied by Others. Integrating the Contractor’s drawings in the system is by Others in Unit 1 – 3. The final loop connection drawings provided by the Contractor are to show the instrument in the field all the way up to the DCS.

- The Contractor develops functional logic drawings and control philosophies for the works as per requirements of the VGB standard (VGB R170 Ce) and interfaces with Others in Unit 1-3 for correct implementation in the new DCS.

- The upgraded existing DHP system and blowers for the hopper aeration system will be unitised. The Contractor provides for the design of these systems up to the localised junction boxes/enclosures. The interface to the new DCS for control, protection and monitoring is by Others in Unit 1-3.

- The Contractor provides for a upgraded existing DHP and hopper aeration HMI mimic design with operator control options and interface (liaise) with Others to integrate the HMI mimic design into the new DCS for control and monitoring in the unit control room.

- The Contractor provides all the necessary design documentation required for the simulator update/mod and interfaces (liaise) with Others to expand and modify the Unit 1-3 Simulator to include upgraded existing DHP and aeration air plant system.

#### Unit 4 – 6

Unit 4 - 6 is controlled from the existing ABB P14 DCS. The Contractor is responsible for the C&I subcontract the OEM of the DCS for the DCS designs and ensures that the new Plant and Materials designs are incorporated in the existing DCS for control, protection and monitoring, by expanding the system to accommodate the plant systems as required by the works. The Contractor is the main and only contractual interface for the Employer and the solution is such that:

- The Contractor is responsible for the design, procurement, supply and installation of all field instrumentation, equipment and cabling including junction boxes/enclosures, trunk cabling, cable trays, trunking and racks as required by the Works Information from the field up to the termination in the DCS control cubicles. The Contractor is responsible for all terminations in the junction boxes/enclosures and marshalling/control cubicles

- Documentation is provided for all new Plant and Materials as well as affected plant areas in accordance with the requirements of the existing control system.

- The Contractor designs and extends power supply to the new P14 control cubicles in Unit 4 – 6.  New P14 control cubicles are installed and added in the existing equipment room to expand the existing ABB P14 DCS in Unit 4 - 6 to cater for the control, protection and monitoring of the existing upgraded DHP and aeration plant system. The design proposal for these cubicles is submitted to the Project Manager for acceptance. The Contractor updates the existing equipment room layout drawings as required to reflect the changes/mods. The Contractor is responsible for all civil works that may be required as a result of these modification/additions.

- The Contractor is responsible for Unit 4 - 6 LV switchgear (within his scope) interfaces to the DCS.

- Integrating the Contractor’s drawings in the system to show the instrument in the field all the way up to the DCS is the responsibility of the Contractor.

- The Contractor ensures that new Plant and Materials information in Unit 4 - 6 is linked to the existing PIS for data storage and long term information.  The allocation of the tags is estimated at 3 x the I/O count of the works.

- The Contractor is responsible for the optimisation and capability tests.

- The Contractor ensures correct interface to the GPS since the existing ABB DCS will be expanded. In case of spare capacity limitations the Contractor provides the GPS.

- The Contractor is responsible for functional integration of DHP including aeration air plant system operation and logics with unit control system.

- The existing upgraded DHP and blowers for the aeration air plant system in the new blower house are interfaced to the unit DCS. The interface these plant systems allows for control, protection, condition monitoring and status monitoring in the DCS.

- A unitized existing upgraded DHP and hopper aeration HMI mimic design is integrated into the DCS and configured to be controlled and monitored from the unit control room. The Contractor implements the HMI designs with operator control options.

- The Contractor ensures time synchronization of a existing upgraded DHP and aeration air plant system.

- Interfacing to the existing GPS (where required), in case of spare capacity limitations the Contractor provides new GPS.

- Documentation is provided for all new Plant and Materials as well as affected plant areas in accordance with the requirements of the existing ABB P14 DCS.

- The Contractor provides all the required design documentation required for simulator updates/mods to the Project Manager and liaises with Others to ensure that the simulator is updated. Plant simulator updates/mods include an update of existing plant simulator with the upgraded existing DHP and aeration air plant system.

#### Outside Plant Control Room (OPCR) DCS

The Contractor subcontracts the OEM of the existing Yokogawa OPCR DCS and ensures the correct interface of the compressor plant and conditioning/scrubber plant in the existing Yokogawa OPCR DCS.

The Contractor design, supply and installs new DCS cubicles for the DHP instrument air compressor plant.

The Contractor is the only contractual interface and the solution is such that:

- The Contractor is responsible for the design, procurement, supply and installation of all field instrumentation, equipment and cabling including junction boxes/enclosures, trunk cabling, cable trays, trunking and racks as required by the Works Information from the field up to the termination in the DCS control cubicles. The Contractor is responsible for all terminations in the junction boxes/enclosures and marshalling/control cubicles.

- The Contractor supplies control/operating philosophies; interface details (such as loop connection diagrams, functional specifications including logic diagrams) for the compressor plant and conditioning/scrubber plant system and ensures the correct interface and implementation in the OPCR DCS. The Contractor takes responsibility for the correct interface and implementation in the OPCR DCS.

- Designing the functional logic diagrams is in compliance with the requirements of the standard, VGB R170 Ce

- The Contractor provides for the new HMI mimic designs with operator control options (compressor plant and conditioner/scrubber) in the existing HMI (Operator terminal) in existing OPCR.

- The Contractor designs new DCS control/marshalling cubicles to cater for the compressor plant. An I/O panel/cubicle for the compressor plant utilizes 230VAC UPS supply and converts it to 24VDC internally in each panel to cater for the 24VDC power supply requirements of this design. The 24VDC power supply is used for control and monitoring of the plant, including those signals required to control the LV switchgear. The Contractor ensures that the power supply requirements complies with the Employer’s standard 240-53114248.

- The Contractor takes responsibility of functional integration of compressor plant and conditioning/scrubber system operation and logic with OPCR DCS.

- Conditioner/scrubbers plant, compressors for the instrument air and their auxiliaries in the new pneumatic compressor house are interfaced to the OPCR DCS for control, protection, condition monitoring and status monitoring.

- Conditioner/scrubber plant, conditioner conveyors and pneumatic compressor plant HMI mimic design are integrated into the OPCR DCS and configured to be controlled and monitored from the OPCR. The Contractor implements the HMI design with operator control options.

- Control wiring from DCS to LV Switchgear for the compressor plant.

### Civil engineering and structural works

Contractor is responsible for design work as stated in the Works Information the extent of the Contractor’s design includes all work which, although not expressly noted, can reasonably be inferred from the Works Information.

For all Plant and Materials designed by the Contractor, the Contractor submits a full set of detailed structural drawings and calculations for acceptance by the Project Manager.

The Contractor can adopt international standards provided that acceptance by the Project Manager has been granted. The Contractor obtains acceptance before adopting the international standards.

#### Unitised Blower House Building

The scope includes:

- Cut-out and disposal of the reinforced concrete surface slab necessary for excavation activities for the unitised blower house buildings foundation system and making good the slab after construction of the buildings.

- Modification of cable tunnel access manholes at the unitised blower house buildings.

- The Employer’s unitised blower house buildings design includes plinths for the blowers only; the Contractor designs all other necessary bases and supports for Plant and Materials within the hopper aeration system.

#### Compressor House

- The scope includes for the design, supply, installation and testing of a 6.3 ton SWL overhead travelling crane for the common compressor house.

- The design and preparation of the terracing around the compressor house in order to avoid water ponding around the building, including any necessary piping and connection to existing storm water drains.

  - Where required as part of his design the Contractor carries out a surveys in order gather required topographical information to sufficiently design the terracing and drainage.

- The Contractor relocates the existing light mast in the area where the compressor house is due to be constructed.

#### Piping and equipment supports and support structures

The Contractor designs all piping support system to suit his mechanical design, this includes all pipe racks complete with pipe plinths, pipe connections to existing structures and any other accessories necessary for successful installation and securing of piping. The Contractor submits all proposed pipe routes (not specified by the Employer) and his pipe support mechanisms to the Project Manager for acceptance prior commencement of detailed design. Where the Contractor has opted to support such piping on existing structures and infrastructure the Contractor is responsible to assess structural integrity of existing structure to support the pipe and submit supporting calculations to the Project Manager for acceptance prior commencement of detailed design.

Removal of the existing fuel oil line steel support structure and foundations, as well as the design and construction of a new fuel oil line steel support structure complete with foundations.

Where piping or other items are to be supported on to the hoppers, the Contractor submits to the Project Manager for acceptance and assessment of the hoppers the weights and connection details of such. The Contractor awaits acceptance of the Project Manager before commencing with design of affected items.

#### Existing DHP Upgrade support structure

The Civil scope required is to review design, procure and construct the chain conveyor support steel work, the bucket elevator drive-end support steel work and for the bucket elevator drives electric hoist system and crawl beam steel works as per design requirements and  specifications. The bucket elevator tail-end casings at zero meter level should be such as to prevent rainwater from flowing into the bucket elevator sumps below ground level. New concrete plinths and transfer conveyor casing support steel work need to be designed and constructed for the six new B1 transfer conveyors. The Contractor is to design and construct/modify the existing transfer conveyor B2’s so that these conveyors can be lowered, so that the new B1’s transfer conveyors can feed the new B2’s transfer conveyors.

The DHP and Ash Conditioning system existing switch gear rooms needs to be modified to include air conditioners to keep the inside temperature range from 18 to 24 degree Celsius and these rooms should have air ventilation systems to keep the whole room under positive pressure to prevent dust ingress. The new fire detection system inside each room needs to be connect with the Power station’s fire detection system. Each room has to have sufficient lights and 220 V wall plugs.

Complete structural assessment will have to be done on the ash bunkers and crawl beams to ensure that the structure can resist the loading from the new additional ash conditioners, 12 x scrubbers, additional blowers and bigger conditioner conveyors.

The Dust Handling Plant blower houses will be equipped with as a minimum fire detection (which must interface with the existing station fire detection system), lighting, 220 V wall plugs, lifting equipment, air filtration equipment and will be pressurised. Big access doors for blowers, motors and other equipment handling onto and from trucks. Each blower room should have amble space for the blower, motor, air cleaning equipment, air drier systems, transformers, switch gears and air heaters for easy plant inspections and maintenance. These buildings should have sufficient air ventilations to keep the blowers, transformers and switch gears at normal operation temperatures.

#### Ash bunker

The Contractor conducts a complete structural assessment and any required design modification of the existing ash bunkers to suit the new ash conditioning plant as described in 3.2.1.4.

New roofs are installed over the new equipment on top of the ash bunkers. The storm water should flow into the existing ash bunker drainage system.

### Equipment

- All nonstandard/off the shelf Equipment that the Contractor requires.

### Compressor House building fire protection and detection

- Fire protection and detection system for the common DHP compressor house including but not limited to the following:

#### Structural Stability of Building Elements

The compressor house is a D4 occupancy, this requires a 120 minute stability of structural components, this includes stability, integrity and insulation for floors, roofs, walls, doors, window, etc. as per SANS 10400-T

- This does not apply to the compressor room section of the building, due to sufficient safety separation distance from the nearby structures.

- This applies to the switchgear rooms (LV and MV), the cable chambers (LV and MV) and the HVAC room due to its criticality as well as its exposure to the transformers.

- Brick walls to be constructed between adjacent transformers.  The dimensions of the walls (especially height) is to follow the recommendations of NFPA 850 to ensure that a fire on one of the transformers does not affect the adjacent transformers.

- Drainage of water/oil mixture at the transformers’ bunds needs to be included in the design. Sizing of the drainage to comply with the recommendation of NFPA 850

#### Escape routes

Escape routes is to comply with SANS 10400-T, taking travel distances into account with regards to feeder routes, escape routes and emergency routes, including but not limited to exit doors and access doors, including all signage.

#### Electrical Equipment & Cables

In terms of SANS 10142-(Part 1 & 2) the following is to be done as a minimum but is not limited to:

- The electrical reticulation to, and within, the DHP compressor house is to be designed and signed-off by a competent engineer.

- An electrical clearance certificate needs to be issued by the electrical installation contractor.

- All cabling is to be run on, or in, appropriate cable ways. Cables are not to lie on hot or dirty surfaces.

- All cable terminations are to be checked for hotspots, with the use of thermal imaging equipment, during the commissioning phase.

- All cable entries to the new DHP compressor house are to be sealed with a 2 hour rated, SABS approved, penetration sealant.

- Grouped electrical cables is to be coated with a 2 hour fire rated coating every 10 meters to limit the fire spread.

#### Automatic Fire Protection

- Automatic deluge protection with high velocity nozzles, to be designed in accordance with NFPA 15 and to be installed on all transformers with an oil capacity of equal or more than 1890 litres.

- Automatic inert gas suppression system is to be installed in the Switchgear rooms (LV and MV).

- SAQCC requirements are adhered as per the department of labour to design a gas suppression System.

#### Hose Reels

Hose reels to be installed at a rate of 1 for every 500m2 is to comply with the requirements of SANS 10400-T, SANS 543, SANS 10105-1 and SANS 10400-W. The end of each of the hose reels installed to reach any point in the area to be protected. These hose reels that are installed in any building to bear, in a prominent position on the reel disc facing the user, a certification mark from an accredited certification body.

#### Hydrants

Hydrants required to be provided at a rate of not less than one per 1 000 m2 or part thereof of total floor area. This equates to a minimum of 3 hydrants for this buildings. Pipes feeding hydrants is not be less than 100 NB. The flow rate for the fire hydrants is 20 l/s (1 200 l/min) and the standard requirement is the simultaneous flow of two hydrants as per the Eskom standard. Where feed pressures only is required at the hydrant (the fire brigade is to provide boosting of systems), the system should be designed with the most remote hydrant having a pressure of 350kPa, as per Eskom minimum requirements. These hydrants are to be easily accessible from the roads.

- The site has existing hydrants and thus any addition to be made with the same type of hydrant.

- The hydrant valves installed to comprise of 80mm Rising Spindle R.S.V. gate valve and an angle patterned 80-65mm reducing adapter with a 63.5 Morris instantaneous coupling.

- Fire hydrants to be supplied through 80 mm risers. Double outlet hydrants supplied through 100 mm risers are also acceptable where required.

- The location of the new compressor house does not have existing hydrants located within 60m of the building. Thus as part of the scope for this project, all 3 hydrants to be provided in compliance with the requirements stated. These hydrants are to be strategically placed to ensure that they are not exposed to any mechanical damage and not located within the risk areas.

#### FIRE EXTINGUISHERS

Fire extinguishers to be hung on purpose made boards and located in secure positions. D4 occupancies require 1 portable fire extinguisher for every 400m2 floor area, this is according to table 11 in SANS 10400 – T. Fire extinguishers are to be placed so that there is access to the fire extinguishers in the event of a fire, this is be done in positions approved by the local authority.

- The portable fire extinguishers are provided in pairs. Each pair will consist of

  - 1 x 5kg Carbon Dioxide;

  - 1 x 9kg Dry Chemical Powder.

- Portable fire extinguishers to comply with the requirements of SANS 1910. It is to be installed, by competent persons in accordance with SANS 1475-1 and SANS 10105-1.

#### Signage

Signage to be done as required per SANS 10400-T.

- Relocation and re-routing of a section an existing fire main and provision of standby emergency fire fighting services during the re-routing of identified section of the existing fire ring main.

- Cable racking for the DHP equipment

- Communication system for the compressor house (PA system and telephone lines)

### Overhead travelling crane for Compressor House

The Contractor designs, supplies, installs and tests a 6.3 ton, class 2 double girder overhead travelling crane for the compressor house building complete with controller, load limiter, electric hoist, and other accessories as indicated on the Employer’s drawings and compliant with the of OHS Act 85 of 1993.

- Structural and Mechanical Requirements

The Contractor submits to the Project Manager detailed drawings of the crane including all the static and dynamic loading imposed on the runway and end stops to allow the verification of the runway beams, end stops and structure.

- Electrical Requirements

Others supply an AC 400V (3 phase) to the crane DB, the Contractor is responsible for provision of the crane DB, all cabling and wiring for the crane, which are compliant with the cabling and racking specification. The Contractor provides an isolator lockable and inter-lockable in off position, as per OHS act. All cabling between the Contactor and rails as well as to all equipment mounted on the crane are supplied and installed by the Contractor. The Contractor provides limit switch design for overrun protection including preventing the crane to run into the end stops.

  - Electrical cable with extruded solid dielectric insulation for fixed installations:

- Rated current

- Rated voltage

- Cable size verified

- Cable test certificate

- Cable Schedule

  - Isolator of correct rating and able to withstand fault level:

- IP 65 rating for isolator enclosure

- Isolator enclosure allowing for lockout during maintenance in an off positions

- Isolator enclosure to be interlocked when in locked out position

  - Circuitry verified and accepted on SPF:

      - Earth Leakage protection unit (Core balance).

      - Circuit diagram available in DB for temporary use during construction. Normally the crane will be connected from a bucket on 400V Board.

  - Earthing between supply, isolator and DB:

      - Crane rails must be interconnected and earthed

      - Festoon or similar cable support earthed and allowing free movement

- Inspection and Commissioning Requirements

The Project Manager reviews and accepts the crane documents required for all inspections and tests. The Supervisor is notified by the Contractor of agreed crane installation holding points during the installation and construction of the work as per the relevant installation ITPs, i.e. mechanical and electrical.

The Contractor is only permitted to submit an application for plant safety clearance if the final inspection (which does not form part of the safety clearance or commissioning process) is successful. The application is sequenced and first submitted for all mechanical works, followed by an application for electrical works, where electrical works include the power source and supply to the crane isolator switch(s).

AKZ numbers (mechanical) and cable and motor numbers (electrical) are inspected during the respective safety clearances procedures. All documents required by the commissioning team are submitted along with the application for safety clearance. If the safety clearance procedure is completed successfully, the crane is ‘locked out’ using a commissioning ‘lock in’ preparation for commissioning. If required, the outstanding limit switches, are located and measured during the functional checks (commissioning of the crane). After the commissioning procedure has been successfully completed, the limit switches are installed using the ‘permit to work procedure’.

On successful completion of all commissioning procedure activities, including all the limit checks, the crane is locked using a commissioning ‘lock in’ preparation for the load test.

The Contractor is responsible for executing and providing any and all Equipment required for the load test. In accordance with the OSH Act and SANS 4310 static, dynamic and deflection tests are conducted on site to certify the crane and supporting structure. The structural design engineer(s) for the crane supporting structure must be present during the load test(s).

All Plant and Materials for the overhead crane and accessories are guaranteed as per conditions of contract.

### Temporary works

All temporary works required for the construction of the works are designed, supplied and erected by the Contractor.

## Procedure for submission and acceptance of Contractor’s design

The Project Manager reviews and accepts the Contractors submitted documents. The Contractor ensures adherence to the Works Information and that a technically sound design approach is incorporated. Specific information required from the Contractors during tender phase is set-out in the Vendor Document Submittal Schedule (VDSS), Appendix B.

After the Contract Date, the Contractor proceeds in the design phase for the portion of the works which he designs. Each document submitted to the Project Manager requires a transmittal note (refer to Employer’s template 240-71448626 for minimum metadata requirements) from the Contractor. The Contractor includes interpretation of results in every report compiled. Appendix B lays out the specific documents requiring the Project Manager’s acceptance before the Contractor can proceed with design, fabrication and construction activities.

### 2D Drawings and 3D Models

The preferred system for 2D drawings and 3D models is SmartPlant. The Contractor adheres to the SmartPlant Data Take-On Standard (240-107305502).

The final design is submitted in SmartPlant in the Employer’s SmartPlant Environment. The 3D model is fully integrated with S3D, SPO, P&ID, SPRD+, SPEL and SPI. It incorporates all associated intelligence.

The Project Manager is responsible for providing all the necessary licences.

The creation, issuing and control of Engineering Drawings are in accordance with the Employer’s Engineering Drawing Standard (240-86973501).

The Contractor’s structural steel and concrete drawings further complies with SANS 10143 Building Drawing Practice, and the structural steel engineering design drawings further complies to the Southern African Structural Steelwork Detailing Manual by the Southern African Institute of Steel Construction.

Drawings that the Contractor submits to the Project Manager for review and acceptance purposes have the compiler(s) and approver(s) signatures.

Electronic drawings have a water mark indicating the approval phase of a drawing and hardcopies are stamped to indicate the phase.

### Design Review Documentation

The Contractor conducts design reviews as per the Contractors official design review procedure. Contractor further takes note of the Employers Design Review Procedure (240-53113685 Rev 1) and participates in all design reviews as specified by the Employer. The Employer may “Authorise”; “Authorise with Comments” or “Not Authorise with Comments”. If required, the Contractor makes the necessary revisions on the documentation and ensures acceptance is obtained from Project Manager. The Contractor includes these design reviews as part of the schedule and suggests appropriate timing for such reviews.

The following design reviews below are conducted, by the Project Manager, as per the design review procedure.

- Contract Award Review (prior to contract sign-off)

- Design Freeze Review(s) (Detail Design)

- System Integrated Design Review (Detail Design)

- Pre-Commissioning Review (per unit)

- Hand-over Review

Design Freeze reviews can be conducted as End-of-Phase Design Reviews or as a series of Interim Design Reviews with the aim to design freeze a system or subsystem/asset in order to enable subsequent designs to progress. The number of design freeze reviews is accepted between the Contractor and the Project Manager.

Documentation for design review is presented to the Project Manager at least twenty (20) working days prior to the start of the formal technical clarification discussion.

The Project Manager reviews any design documentation submitted a maximum of 3 times, if after the 3rd time the Project Manager is still not satisfied with the design documentation the cost to review the documentation to where it is accepted by the Project Manager is covered by the Contractor.

The completed Integrated Design Report (IDR) (in the template included in Appendix O) is reviewed in the System Integrated Design Review (Detailed Design), It is not acceptable to submit the design for this review as a collection of documents developed in the Contractors own template. The report is structured such that all the design information is included in the body of the report and appendices include information supporting the content in the body of the report only.

#### Contractors Responsibilities in Employers Design Review Process

The Project Manager conducts Design Reviews as per the Employers design review procedure; Participation of the Contractor in the Employers Design Reviews consists of:

- The Project Manager conducts Design Reviews as per the Employers design review procedure and the Contractor presents (the design developed by him) and participates in the design review.

- If any fundamental errors were found in the designs or further actions are required, the Contractor addresses all concerns raised and revises the designs.

- The Contractor submits the documents for another Design Review session once all designs are revised according to the concerns raised by the Project Manager.

- If no fundamental errors are found in the designs during the Design Review session, the Project Manager compiles the Design Review minutes and report.

- The Contractor reviews the report and minutes. If the report/minutes are not acceptable, the Contractor submits comments to the Project Manager.

- The Project Manager accepts the Contractor’s design once the report is accepted and signed by the Employer’s project team and the Contractor.

### Engineering Change Procedure

The Contractor takes note of the Employer’s Engineering Change Procedure (240-53114026, Rev 1). An engineering change includes any proposed engineering change originating from the Contractor or Project Manager from an established design baseline by the design review procedure.

### Process for Submission of Documents

The Contractor submits all documents according to the accepted VDSS in Appendix B. The process for submission of documents is described below:

- The Contractor submits the documents/drawings to the Project Manager through a Transmittal. The Contractor submits both the native (SmartPlant or as specified by the Data Take-On Standard - 240-107305502) and PDF.

- The Contractor sends the documentation to the Project Manager through the medium agreed between the Contractor and the Project Manager.

- The Project Manager’s document controller downloads the documents from the said medium.

- The Project Manager’s document controller performs the quality check on the document submitted by the Contractor. If there is missing information, the Project Manager notifies the Contractor.

- The Project Manager’s document controller registers the documents.

- The Project Manager’s document controller distributes the documents/drawings to all relevant parties within the Project Manager’s project team.

- The Project Manager’s project team reviews the documents/drawings and submits all comments or inputs to the Project Manager and the Project Manager submits to the Contractor for consideration.

- If the Project Manager finds major deficiencies in the submitted documents/drawings, the Contractor revises the documents/drawings and resubmits to the Project Manager.

### Time Required for Acceptance of Designs

Not later than one (1) month after receipt, the Project Manager returns one (1) copy of the drawing/ document marked as “Authorised”; “Authorised with Comments” or “Not Authorised with Comments”, as may be appropriate. The notations “Authorised” and “Authorised with Comments” authorise the Contractor to proceed with the manufacture of the Plant and Materials covered by such drawings/ documents subject to the corrections, if any, indicated thereon, unless otherwise stated. If drawings/ documents are “Authorised with Comments” the Contractor submits an updated version of the document/ drawing to the Project Manager with the comments incorporated. Where prints or drawings/ documents are “Not Authorised with Comments” the Contractor makes the necessary revisions on the drawings/ documents and submit further copies for acceptance in the same procedure as for the original submission of drawings/ documents. The revised drawings/documents are submitted by the Contractor to the Project Manager no later than 2 weeks after the Project Manager returns the drawing/ document marked as “Not Authorised with Comments” to the Contractor, however if the Contractor requires a longer period to revise the documents he applies (with reasoning) to the Project Manager for an extension on this timeframe.

Every revision shows by number, date and subject in the revision block on the drawing and documents.

## Other requirements of the Contractor’s design

The Contractors design adheres to the specifications as set out in Section 6 of the Works Information. In addition the following are adhered to in the Contractors design;

### Process Design Information

#### Site Conditions

The Contractor ensures that works is designed to accommodate the ambient conditions specified in the Part 4: Site Information of the Works Information (unless otherwise stated) such that the operation of works is not impaired, damaged or does not perform according to requirements.

### Ash Specification

The typical composition of the ash is represented in Table 9 below.

Table 9 Typical Ash Analysis, expressed in percentage

| Ash Elemental analysis (air dried basis) |  |  |
| --- | --- | --- |
| Silicon as SiO2 | % | 57.60 |
| Aluminium as Al2O3 | % | 26.20 |
| Iron as Fe2O3 | % | 3.80 |
| Titanium as TiO2 | % | 1.40 |
| Phosphorus as P2O5 | % | 0.25 |
| Calcium as CaO | % | 5.00 |
| Magnesium as MgO | % | 1.80 |
| Sodium as Na2O | % | 0.01 |
| Potassium as K2O | % | 0.80 |
| Sulphur as SO3 | % | 3.10 |
| Manganese as MnO | % | 0.02 |
| Total | % | 100.0 |

Depending on conditions the bulk density of the fly ash can vary, the extent to which is listed below.

- Max. – 1 200 kg/m3

- Min. – 700 kg/m3

The maximum continuous operating temperature of the ash to be handled by the works is 160°C.

Table 10 below depicts typical ash particle size distribution for the ESP for Field 1 and Field 5 at Tutuka.

Table 10 Typical Ash Particle Size Distribution

|  | Field 1 | Field 5 |
| --- | --- | --- |
| d10 [m] | 9.9 | 1 |
| d50 [m] | 49 | 3.6 |
| d90 [m] | 147.5 | 13.3 |

Previous investigations undertaken by the Employer have shown that the shape of the ash particles have the dominant influence on the extent of the abrasiveness of ash. The shape of the ash particles are determined by the combustion process, milling process and coal quality. The Contractor designs the works for actual Tutuka P.S. ash properties. The Contractor guarantees that the works operates as per the requirements in the Works Information with the actual ash properties. The Contractor conducts any tests required to determine the exact ash properties of the ash generated by the boilers. Ash samples from Tutuka P.S. are supplied by the Project Manager to the Contractor if required, for analysis purposes.

#### Fuel Oil

Tutuka P.S. utilised fuel oil as a supplement to the PF supplied to the boiler during start up and during transient conditions. The specification of the fuel oil is stated in Table 11 below.

Table 11 Bunker 150 Fuel Oil Specifications (Boiler start-up fuel)

| Properties | Units | Grade 3 (Fuel oil 150) |
| --- | --- | --- |
| Flash point (PMCC) min. | °C | 60 |
| Water (v/v) max. | % | 0.5 |
| Sediment (v/v) max. | % | 0.1 |
| Total Sediment in residual fuels by std aging (v/v) | % | 0.1 |
| Viscosity at 50 °C, min. | cSt | 90 |
| Viscosity at 50 °C, max. | cSt | 150 |
| Viscosity at 100 °C, max. | cSt | 20 |
| Conradson carbon residue mass, max. | % | 15 |
| Ash mass, max. | % | 0.1 |
| Sulphur mass, max. | % | 3.5 |
| Copper strip corrosion rating (3 hours at 100 °C) max |  |  |
| Density at 20 °C, max. | kg/m3 | 991 |
| Pouring point (winter), max. | °C | 9 |
| Aluminium, max. | mg/kg | 30 |
| Silicon, max. | mg/kg |  |
| Aluminium and silicon, max. | mg/kg | 80 |
| Vanadium, max | mg/kg | 400 |
| Iron | mg/kg | 50 |
| Acid number |  | Nil |
| Stability: Accelerated dry sludge, (m/m), max. | % | 0.1 |
| Stability: Existent dry sludge, (m/m), max. | % | 0.1 |
| Energy content, min. | MJ/kg | 41 |

- The fuel oil piping is designed according to the following parameters

  - Maximum temperature 	:160 °C

  - Maximum pressure 	: 6.4 MPa

### Effluent Water

The conditioning water is supplied from the Tutuka P.S. effluent sump. This sump consists of four (4) compartments.

- Compartments 1 and 2 receive effluent from the Cooling Water (CW) and the mine water clarifiers.

- Compartments 3 and 4 receive regeneration effluent from the water treatment plant.

- It is possible that any of the compartments can overflow into the other compartments.

The ash conditioning water supply is taken from compartments 1 and 2.

A typical water quality can be seen in Table 12 below.

| Table 12 Typical Effluent Sump Water Quality Parameter; Unit; Minimum; Maximum; Average; 95th Percentile. Calcium Hardness as CaCO3; mg/kg; 1.6; 3 233; 205.603; 367. Chloride; mg/kg; 130; 5 045; 617.096; 989.4. Conductivity; µS/cm; 5.55; 12 121; 6 212.15; 9233. m-Alkalinity; mg/kg; 0.2; 12 402; 160.172; 239.965. p-Alkalinity; mg/kg; 0; 8 305; 13.7812; 25.065. pH; ~; 5.59; 11.27; 8.6801; 9.1. Turbidity; NTU; 1.9; 229; 32.6208; 60.9. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |

The above water quality is a summary of analysis of CW from May 2012 to May 2015 and can be used for preliminary design. The Contractor remains responsible for taking samples from the sump twice a week from the start of the contract till the design freeze date for the conditioning plant as a minimum to confirm the quality of the water that is to be used for the ash conditioning plant final design. The Contractor submits a water sampling plan to the Project Manager for acceptance.

### Precipitator Plant

The Contractor takes into account the upgrading of the existing ESPs at Tutuka P.S. that is done by Others.

The Contractor takes the following into account as a minimum;

- The ESP for each unit consists of two (2) casings with one (1) draft group per casing, each casing has twenty (20) hoppers.

  - Each ESP casing consists of  four hopper conveyors and each hopper conveyor can collects ash from 5 hoppers.  Figure 4 below shows the DHP layout for each ESP.

Figure 4. ESP Compartments Layout

  - The ESP upgrade does not result in a change to the hopper outlet height.

- Modifications are made to the stiffeners on the hoppers, the layout of the proposed stiffeners is shown in drawing 0.61/97161

Two (2) Precipitator casings per boiler. Each casing has 5 fields. Each field is subdivided into two electrically independent half fields.

Dust removal from the precipitator hoppers is continuous using a dry process. (En-Masse)

Each boiler flue is fitted with an optical dust monitor.

The quantity of air introduced into the ESP through the hopper aeration system and the ash bunker vent pipe has an impact on the design and operation of the ESP done by Others. The maximum allowable air quantities discharged into the ESP are:

  - 12,1 m3/min for the ash bunker vent pipe (excluding the DHP venting requirements and including bunker compartment aeration air usage)

  - 50 Sm3/min introduced into the hoppers from the hopper aeration system.

The distribution of ash captured by the ESP is  as follows:

- Field:                            1                2                  3                  4                5                 Total

- Ash distribution:         84%          12%              3 %             0.8%         0.20%

- Recovery Time hrs:    12, 74         0, 25            0, 65           0, 16         0, 04            13, 84

Table 13: ESP dust loading

| Precipitator Efficiency and Dust loading |  |  |  |
| --- | --- | --- | --- |
| All fields in operation |  | First field out of operation |  |
| Efficiency % Field 1: 83,5 Field 2: 73,3 Field 3: 67,3 Field 4: 58,7 Field 5: 50,0 Total: 99,70 | Dust Amount kg/h 60 890 8820 2162 617 217 72 706 | Efficiently % - 83,5 73,3 67,3 58,7 99,40 | Dust Amount in kg/h - 60 890 8820 2162 617 72 489 |

The dust handling plant has be sized for both conditioners.

The backlog recovery is 1,25 x the maximum capacity of the DHP.

- Table 14: Stored dust to be cleared

| Precipitator stored dust to be cleared |  |  |  |
| --- | --- | --- | --- |
| All fields in operation |  | First field out of operation |  |
| Field: 1 2 3 4 5 Total: | Dust Amount kg 548 010 79380 19458 5553 1953 654 354 |  | Dust Amount in kg - 548010 79380 19458 5553 653 401 |

In the case of emergency, the ash hoppers can store fly ash for 9 hours and the backlog recovery duration is about 32 hours.

The DHP Instrument compressor cooling system requires both potable and demin water. The expected flow rates of demin and potable water required by the DHP compressor cooling system are shown below. These are indicative quantities and the final flow rates will be specified by Others when the ESP equipment selection has been done.

  - Potable water	: 4.67 m3/hr

  - Demin water	: 4 m3/hr

### Hopper Aeration System

The Contractor supplies aeration air to the aeration pads that is:

  - Clean.

  - Moisture and oil free.

### DHP

The Contractor ensures that the following requirements for the DHP system, are met as a minimum;

DHP mass flow rate is 61 tph and the backlog recovery ie 80 tph.

Three long transfer conveyor routes.

Two routes in operation and one route on standby.

One route need to handle 80 tph on high speed mode operation..

Maintenance costs, maintenance time (MTTR) of the abovementioned chain conveyors and bucket elevators is supplied by the Contactor.

The DHP is able to start up with bucket elevators and chain conveyors under full load conditions.

There would be eight hopper conveyors, six transfer conveyors and three bucket elevators.

The following parameters are taken into account when designing the ash bunker vent pipe:

  - Air vented can have a high dust concentration.

  - Conditions where conveying air fully expands while the both units are operating at backlog capacity.

  - Minimise the chance of the vent pipe blocking. The vent pipe is fitted with a system which indicates if the vent pipe is blocked.

### Compressed Air System

The compressed air system is designed, by the Contractor, for the ambient conditions and operating range in Table 16 below.

Table 16 Ambient reference conditions and operating range for the design of the compressed air systems

| Inlet Parameter | Minimum | Normal Operating | Maximum |
| --- | --- | --- | --- |
| Pressure | pnormal-5kPa | pnormal=p0*e(-g*M*h)/(R*T0) | pnormal+5kPa |
| Temperature | -10°C | 25°C | 40°C |
| Relative humidity | 20% | 60% | 80% |

| p0 | sea level standard atmospheric pressure | 101325 Pa |
| --- | --- | --- |
| T0 | sea level standard temperature | 288.15 K |
| g | Earth-surface gravitational acceleration | 9.80665 m/s2 |
| M | molar mass of dry air | 0.0289644 kg/mol |
| R | universal gas constant | 8.31447 J/(mol•K) |
| h | Height above sea level | Site specific in m |

### Conditioning Plant

The Contractor ensures that the following requirements for the conditioning plant, are met as a minimum;

The conditioners condition the ash to the following moisture contents by weight:

  - Normal operation  	: 13 – 16%

  - Maximum 		: 20%

The conditioning water supply piping is able to withstand the maximum pressure possible exerted on it (conditioner emergency potable water supply from the air heater washing system).

  - The pressure of the air heater washing system is 10 bar at the conditioners.

### HVAC

The Contractor ensures that the following requirements for the HVAC system, are met as a minimum;

Outdoor design conditions

  - Summer: 		32°C DB, 20°C WB

  - Winter:                  2°C DB

The velocity across the filters is less than 2.5 m/s.

The design life of the HVAC system is 15 years

The total unit cooling and heating capacity includes for the equipment load, building load, fresh air load at design parameters and the unit inefficiencies.

The blower house pressurisation fans supply air capacity also includes make – up air required for the blowers.

### Additional requirements

The Contractor ensures that the following general requirements are met as a minimum;

The works is designed to operate till end of station life.

The works is designed to minimise energy consumption.

The works limits transmission of vibrational forces to structures (steel and concrete) and other equipment.

The Contractor takes note of the cable tunnels in close proximity to the unitised blower houses and compressor house as per drawings 0.61/96022.

The works is able to be cleaned with washing water at 10 bar without impairing the performance of any of the components.

All components are designed to operate in harsh, dusty environments unless positioned within a structure that has a means for creating a dust free environment.

All actuated valves are pneumatically actuated utilising control air from the control air compressors supplies as part of the compressed air supply system.

  - The limits of the actuators are designed such that they are positively locked and don’t loosen during normal operation of the Plant and Materials.

The works minimises fugitive dust emissions.

The works provides safe operating and maintenance conditions.

The Contractor complies with all standards and procedures referred to in the Works Information and, in addition, all relevant industrial, national and international standards and procedures, as listed in Appendix E.

The works is designed for steady-state and normal transient conditions.

Manual isolation valves are lockable with chains and locks.

The control air supply to each actuator can be isolated by a lockable isolation valve and required lockable valves to vent the control air remaining inside the actuators to atmosphere for when maintenance is required.

All seals and rubber components are to be able to operate at a temperature of up to 220°C

The maintenance strategy for the all newly installed or upgraded plant (in the Tutuka Power Station approved RBO format) must be handed over before commissioning of the plant. After the compilation of the RBO process, new PM’s must be compiled.

The DHP upgrade and installation of hopper aeration system must be completed within a 120 day outage (Breaker open to breaker closed). Work that will not affect the operation of the unit can be conducted before the commencement of the outage.

The complete DHP upgrade and hopper aeration system will be handed over to the Tutuka Power Station by the project team according to an approved plan.

All designs to be taken through the Modification process by Tutuka Engineering.

Site engineers to be fully involved during the commissioning phase of the project. Site engineers will be utilised on an ad-hoc basis during the design and construction phase.

All redundant equipment and systems will be completely decommissioned and removed from the operating environment.

Contractor to submit a critical and normal spares list for all the new plants and the contractor and Eskom would determine which spares must be stock items. The contractor must fill in all the required stock item request forms.

The precipitator hoppers must be fitted with emergency offloading mechanism to empty blocked ash hoppers.

The dust plant venting system should be able to vent to the existing ash bunkers so that the dust plant can operate under vacuum conditions. The vacuum at the ash bunkers top must be measured before the design phase.

The new drives spares must be locally available for 21 years.

Any make standard flanged motor must fit on the gearboxes.

The new drives must have oil level inspection glasses. These inspection glasses must indicate low oil levels and normal working oil levels.

There must be shaft coupling between the motor and gearbox.

The housing between the motor and gearbox must have an inspection hole to inspect the coupling and for oil leaks.

The housing between the motor and gearbox must have an opening at the bottom, in case if the gearbox input shaft seal is leaking oil.

The electric motor bearings to have grease nipples.

The motors and gearboxes bearings to have a life span of 100 000 hours.

Low speed couplings between the gearboxes and conveyor drive shaft bearings.

These new drive units must operate in a horizontal position with torque arms.

These drives need to operate in dusty conditions and the gearboxes to have air breathers. IP65

The contractor is to design and select the correct size drives and the drive shaft selection for the chain conveyors and for the bucket elevators.

The proposal is to install the new ash conditioners first on the plant and commissioned it. If the new ash conditioners are proven, then the existing ash conditioners can be replaced with new ash conditioners. These installations and replacements can be done while the units are on load.

The recommendation is also to install the new additional aeration air blower first and tie it into the existing common air pipe header, and then the existing three air blowers can be replaced.

The contractor is to determine if the existing dirty water supply system is sufficient for the 12 ash conditioners. If not, then the dirty water supply system needs upgrading.

The contractor is also to determine if the conditioner conveyors can handle the amount of ash from two ash conditioners. If not, then these conveyors and moving heads needs to be upgraded.

The complete ash conditioning upgrade, aeration air system and additional conditioners will be handed over to the Tutuka Power Station by the project team according to an approved plan.

All designs to be taken through the Modification process by Tutuka Engineering.

Site engineers to be fully involved during the commissioning phase of the project. Site engineers will be utilised on an ad-hoc basis during the design and construction phase.

All redundant equipment and systems will be completely decommissioned and removed from the operating environment.

Contractor to submit a critical and normal spares list for all the new plants and the contractor and Eskom would determine which spares must be stock items. The contractor must fill in all the required stock item request forms.

The new scrubbers must be able to minimise the ash particles from the conditioner surroundings and discharge this dust/slurry into the relevant ash conditioner. These scrubbers should use dirty water.

- New crawl beams would be required for the new ash conditioners.

## Use of Contractor’s design

The Contractors design is used to complete the works, certain portions of the works are designed by the Employer (as specified in section 3.1) and the designs supplied to the Contractor for construction. All documentation as specified in the Works Information is supplied to the Project Manager by the Contractor.

Any detail design drawings required for maintenance purposes is supplied to the Project Manager, by the Contractor. The detail design drawings or fabrication drawings supplied to the Project Manager by the Contractor can be supplied to any maintenance partner that the Employer wishes to enter into a partnership with during the life of Tutuka P.S.

The Contractor notes that all GA, assembly and dismantling drawings become the property of the Employer upon Completion of the works. The Employer is permitted to purchase replacement parts off these drawings from the lowest cost suppliers.

## Design of Equipment

N/A

## Equipment required to be included in the works

### Special Tools and Equipment

It is preferred that no Special Tools are required for operating and maintaining the works.

If Special Tools are required to operate or maintain the works these are proposed to the Project Manager for acceptance.

  - If accepted a minimum of two (2) of each accepted Special Tool is supplied to the Project Manager by the Contractor as part of the works.

## As-built drawings, operating manuals and maintenance schedules

The Contractor is responsible for the compilation and the supply of all the documentation required during the various project stages and to provide the documentation programme to link with the agreed upon submission dates. Documentation and drawings are programmed for delivery to meet the submission dates and in accordance with the agreed VDSS in Appendix B.

As a minimum the Contractor supplies the following:

- 2x electronic copies for each manual in PDF format.

- 1x maintenance software for each manual (if applicable).

- 5x hard covered copies for each of the manuals.

- 2x full sets of hard copy as-built drawings.

- 1x electronic copies of as-built drawings in a format as specified in SmartPlant Data Take-On Standard (240-107305502).

- A fully integrated SmartPlant model in the Employers environment with all intelligence incorporated.

- All other documents:

  - 1x hard copy.

  - 1 x electronic copy.

All documentation, including reports, manuals, etc. are in the English language and comply with the specification VGB R171, 2nd edition, 2010.

All documentation is customised for Tutuka P.S.

### Manuals

The Contractor supplies the following manuals:

Operating manuals

Maintenance manuals

Training manuals

The manuals conform to the specifications set out in this Works Information and are submitted to the Project Manager for acceptance.

Each of the manuals has a high level AKZ coding. For example, if conditioning plant high level code is WU, then it is clearly indicated in the manual. If there is a reference of a system or component in a manual it is referenced according to its AKZ codes. For example, a pump is not just a pump, it must be referenced according to its AKZ coding.

The manuals include the power station name and order number as a minimum.

Any special instructions pertaining to the storage of spare parts or to their shelf life is included in the manuals and is specifically pointed out in writing with the delivery of the equipment. All drawings required for component locations, dismantling and re-assembly for maintenance are included in the manuals.

### Operating, Maintenance and Engineering Documentation

The Contractor supplies the Project Manager with the following documentation according to the agreed upon VDSS in Appendix B

- Operational Documentation includes but is not limited to:

  - Operating procedures.

  - Emergency operating procedures.

  - Plant isolation procedures

  - Routine inspection and test procedures.

  - Re-commissioning procedures.

- Maintenance and Engineering Documentation includes but is not limited to:

  - Detailed design report.

  - Technical specification sheets for different equipment to be compiled, inclusive of the AKZ codes relevant to the different equipment.

  - Routine inspection specification.

  - Service interval specification

  - Bill of material, material number and supplier.

  - Maintenance plan per system.

  - Compilation of new PM documentation for the works in the Employers PM template.

  - Installation drawings and instructions.

  - Overhaul procedures and specifications.

  - Test procedures and specifications.

  - Serial numbers of items installed plus the AKZ position installed in.

  - Drawings applicable to works.

  - Recommended spares list.

  - Details of all the components.

  - Detailed drawings of all components of the works sufficiently detailed for the procurement of spares (e.g. conditioner shafts, conditioner paddles) and conducting of maintenance.

The Contractor prepares maintenance plans that specify when, at what frequency and how maintenance tasks are performed on the works. The maintenance plan is submitted in the Employers RBO template in Appendix D. Each maintenance plan includes tasks for condition monitoring, failure finding surveillance tasks, inspection schedules and descriptions for each task.

The Contractor completes all documentation required to develop planned maintenance (PM) activities documentation in the Employers template in Appendix G.

#### Recommended Spares List

The Contractor supplies a list of recommended critical and normal spares as per the VDSS in Appendix B. The recommended spares lists is for normal operation for mechanical, process control, C&I and electrical components required to maintain the works between GOs (six (6) years).

The spares list includes the following:

- Price, valid for six (6) months

- Component reference number

- Component description

- Guaranteed supply period before component becomes obsolete

- Mean time between failure (MTBF) of components/parts

- Mean time to repair (MTTR)

- Order lead time

- Criticality (low, medium or high)

- Indication of the availability of local support for components

The Contractor assists the Employer to determine which spares (for the entire works) are to be kept as stock items in the Employers stores. The Contractor completes all the documentation and the process to create the new spares as stock items, the examples of the required forms to be completed are found in Appendix F.

All similar items for the works and all similar consumables are interchangeable with each other, this results in the spares stock holding being minimised. Where it is possible, components such as motors are designed to reduce the number of equipment variation.

Spares are to be available in South Africa.

The Contractor specifies all new motors, gearboxes, blowers, compressors, pumps, pressure vessels and valves which have spares back up from the market for a minimum period of 20 years. It would be preferred that the new motors, blowers, compressors, pumps, pressure vessels, valves and gearboxes have a spares back up of 40 years.

### As-Built Drawings

The Contractor hands over as-built design documentation to the Employer as per procedure Documentation Management Review and Handover Procedure (240-66920003).

All as-built drawings are signed off by the Contractor confirming that the drawings submitted are actual representations of the works constructed.

The Contractor supplies all as-built drawings to accurately and clearly depict the works, examples of as-built drawings which can be supplied but not limited to are:

- General arrangement

- P&IDs

- Dimensioned site layout

- Process flow diagrams

- Structural drawings

- Single line diagrams

- Cable routing

- Logic diagrams

- Junction box diagrams

- Pipe routing

- Lighting and small power layout

- Earthing diagram

- Concrete and reinforcement

- Connection details

- Etc.

For work where the Employer is responsible for the detailed design, the Contractor is responsible for the provision of all as-built information necessary for the Employer to complete his as-built drawings, unless it is specified in the Works Information that the Contractor supplies completed as-built drawings to the Project Manager for the specific areas of the works design by the Employer. The as-built information is marked up in red; neatly on a paper print of the drawing and is submitted as per section 5.2.1 of the Works Information.

For work where the Contractor is responsible for the detailed design or completing the as-built drawings for the Employers design, the Contractor submits as part of his data books as-built drawings for the Project Manager acceptance. The drawings are duly stamped/watermarked "As-built ".

### LV Switchgear

The following Employer drawing numbering system is proposed for the new LV Switchgear drawings.  The Contractor may assign his own drawing number as required to meet his document control system requirements:

Table 17 Proposed drawing numbering system

| Sheet number |  |  |
| --- | --- | --- |
| A-F | Contractor | Cover Sheet |
| G-Z | Contractor | Cover Sheet |
| 1-30 | Contractor | Switchgear Schedule |
| 31-40 | Contractor | Summary Sheet |
| 41-49 | Contractor | Bus Wiring Arrangement |
| 50-55 | Contractor | General Arrangement Drawing |
| 56-100 | Contractor | Schematic Drawings |
| 101-199 | Contractor | Cable Block Diagram |
| 200-299 | Contractor | Cable Schedule |
| 300-399 | Contractor | Cable termination Drawings |

### Motors

The Contractor provides general arrangement drawings completely dimensioned, showing:

- Preliminary outline drawing indicating certified motor mounting dimensions, shaft height, shaft diameter and coupling detail, maximum overall dimensions, weight for total motor and removable heat exchanger (if applicable), interface location for terminal boxes (main power supply, auxiliary, and accessories), and cooling water (if applicable).  The rated kW output, speed, supply voltage, line current, frequency and phases are clearly shown.

- The hot and cold motor thermal limit curves at 100%, 85%, and 75% of motor rated voltage.  A series of graphs are plotted for each voltage level.

- Bearing details including vendor, type, arrangement, locations of temperature pockets and details of inserts, showing all oil pipes and their flanges, fits/clearances on the shaft and housing, loads on bearings, shaft run-out or endplay, maintenance requirements, expected operating temperatures, and selection criteria used for the bearing to suit application.

- Stator and rotor winding details.

- Details of foundation requirements, showing embedded parts and static and dynamic loading on the foundations for starting run up, normal and fault conditions.

- Cross-sectional drawing of the motor showing the rotor and stator construction, end-winding bracing arrangements and clearances from the end-shields, airflow, shaft and bearing locations, rotor and stator core with slot dimensions, rotor and stator winding dimensions including slot fits and clearances, etc.

- Detailed drawing of main and auxiliary terminal boxes, with identification and physical arrangement details of terminals for external cabling connections. This drawing includes cross-sectional dimensions of the power supply terminal boxes.

- Final details of accessories such as temperature detectors, detector location, and, oil level indicators.

- Motor performance data and curves, which include: 1) starting current versus time for 100%, 90% and 80% of rated voltage; 2) current and torque versus speed for 100%, 90% and 80% of rated voltage; 3) efficiency, power factor and current versus load power from 25% to 125% at 25% increments and rated voltage.

- Motor protection data/requirements such as; heating time constant, cooling time constant, cooling time, winding temperature alarm and tripping levels, winding temperature restart inhibit level, stall withstand/capability time, fault current level, locked rotor current, safe starting time, number of starts per hour (hot and cold), minimum period between starts, thermal limit curves etc.

The drawing requirements for all other electrical systems forming part of the works, is as per the specifications within the Works Information.

# Procurement

## People

### Minimum requirements of people employed on the Site

The Contractor does not alter previous decisions communicated to the Employer or Others without the Employer’s acceptance or agreement.

All semi-skilled and non-skilled employees required for this project shall be sourced from the Local to site communities in Lekwa Local Municipality. The Employer will make the local to site employment database available to the Contractor for recruitment of non-skilled and semi-skilled employees. The Contractor is not allowed to recruit non-skilled and semi-skilled employees from the gates of Tutuka Power Station or any other process other than the utilisation of the employment database which will be provided by the Employer.

Any new foremen/Supervisors appointed by the Contractor after Contract Date or during provision of the works are fully conversant with respect to details of the methodology and communication process existing, prior to accessing the Site.  The Contractor provides the CVs and all other relevant information of the replacement employees to the Project Manager.

Permits for foreigners – The Contractor informs the Project Manager of any need to employ foreigners and on acceptance by the Project Manager, the Contractor arranges permits for such employees. The Contractor informs the Project Manager when the services of specialists are required.  The Contractor ensures interface with Others is managed before commitment is made to bring specialist to Site.

The Contractor ensures that the Contractor’s workforce is trained and competent to perform their respective duties.  The Contractor provides CVs and proof of qualifications of his key persons (listed in Section 2.7 of this Works Information) as a returnable schedule.

The Contractor provides for professionally registered (Pr.Eng) and experienced design engineers.

### BBBEE and preferencing scheme

The Employer requires the Contractor to either maintain or improve the Broad Based Black Economic Empowerment Recognition Level (B-BBEE Recognition Level) as at the Contract Date.

Penalty on B-BBEE Recognition Level:

The Contractor shall be penalised 0.5% of the committed contract value if the Contractor or its

Sub-Contractor(s) fails to maintain the B-BBEE Recognition level as provided at contract award.

### Skills Development, Local Content and Local Production

The Employer, as a State Owned Enterprise, is mandated to comply with Preferential Procurement Policy Framework Act (“PPPFA”).  The Employer’s contribution to this initiative is to agree on Local Content and Local Production as well as Skills Development targets as committed by the Contractor to achieve.  This commitment is achieved through leveraging the Employer’s procurement spend in a manner that allows flexibility within the business in order to accommodate government local development initiatives and policies.

#### Localisation Compliance

For the duration of the contract, the Employer will retain 2.5% of any invoice (excluding VAT) payable at the end of each periodic interval as security for the fulfilment by the Contractor of its SD&L obligation.

The penalty for non-compliance will be 2.5% of the value of the contract for each percentage not met, and it shall be deducted from the final payment.

#### Skills Development

Skills Development will not be a criterion that is weighted, however, the Contractor is encouraged as part of the tender submission to propose skills development initiatives in terms of the skills required for a project.  Skills Development Targets will be agreed with the prospective Contractor during negotiation stage.  This will form part of the contractual obligation with the successful Contractor.  If applicable, the Contractor will be required to keep accurate records and provide the Project Manager with monthly reports on the Contractor’s actual delivery against the agreed skills development targets.

The Contractor shall submit to the Project Manager a detailed Labour Resource Plan that reflects both retained and new jobs to be created by the project.

All trainees required for this project shall be sourced from the Local to site communities in Lekwa Local Municipality. The Contractor shall follow the recruitment processes, i.e. advertising on local media.

The Employer shall verify all the candidates before the placement.

The penalty for non-compliance on Skills Development will be 2.5% of the value of the contract for each percentage not met.

#### Job Creation

Job creation proposals by tenderers will not form part of the tender evaluation criteria. It is however, part of Eskom’s contribution towards the Government’s job-creation initiative as contained in the New Growth Path (NGP) and the New Development Plan (NDP).

The Employer has made a number of empowerment commitments to the local communities surrounding the areas where it conducts its construction activities. Amongst these, are commitments to be considered for local empowerment possibilities in its procurement strategy. In doing this, the Employer is seeking to ensure that the local communities benefit from its procurement spends through wealth generation and capacity development; and that this benefit is spread as widely as possible throughout the community.

The Contractor to propose to the Employer the number of semi-skilled and unskilled labourers that will be sourced from local to site in support of this empowerment commitment to the local communities.

Furthermore, all semi-skilled and non-skilled employees required for this project shall be sourced from the Local to site communities on Lekwa Local Municipality.

Note: The Employer will make the local to site employment database available to the Contractor for recruitment of non-skilled and semi-skilled employees. The Contractor is not allowed to recruit non-skilled and semi-skilled employees from the gates and any other process other than the utilisation of the employment database which is with the Employer.

## Subcontracting

### Preferred subcontractors

The Contractor shall sub-contract a minimum of 30% of the value of the contract. The Contractor shall sub-contract to an exempted micro-enterprise (EME) Level 1 or 51% or more, Black Ownership / Qualifying Small Enterprise (QSE) Level 1 with 51% or more, Black Ownership that has the capability and ability to execute the sub-contracting scope.

In the event that the Contractor intends to sub-contract after the contract award, the

2nd and 3rd Tier Companies should be submitted to the Employer for evaluations and classification.

The Contractor shall not subcontract with their subsidiary companies as this may be interpreted as subcontracting with themselves and / or using their subsidiaries for fronting. Where the Contractor subcontracts with a subsidiary this must be declared in tender documents.

#### Reporting

The Monthly report for SD&L shall be submitted on matrix to the Project Manager on or before the 7th day of every month.

- Sub-contracting Reporting

Sub-Contractors (2nd and 3rd Tier) spending shall be done monthly.

This requirement is only for reporting purposes.

The report should state the following:

- Reporting Month

- Contract title and Contract number

- Sub-Contractor Vendor Name

- Activity / Bill item related to contribution

- Payment Value for month – in ZAR

- Sub-Contractor’s Invoice number

- Main Contractor’s Payment Reference Number

- B-BBEE Credentials (including percentage of black ownership).

Each page of the report shall bear a signature of the Contractor declaring accurate reporting.

The Sub-contractors’ invoices should reflect the Project, Site and Activity to the related service/s performed.

First preference shall be given to Local to site Black Owned entities. Local to site “means all areas that fall within Lekwa Municipality.

- Skills Development Reporting:

- The Contractor shall submit a detailed Skills Development Plan within 28 days after contract award.

- Skills development progress reporting shall be done on a Quarterly basis

With regard to skills development, the same student cannot be linked to more than one project at the same time. The Contractor will be required to provide Names, Identification and Contact numbers, as well as certified copies of Identification documentation of students on skills development, which will be monitored by the Employer.

All skills developed shall be retainable for a minimum period of 3 years.

The correctness of the figures shall be audited / verified at any time by the Employer.

SUMMARY OF SD&L TARGETS:

| Criteria | Minimum Target |
| --- | --- |
| Local Content to SA | 80% |
| Local Content to Site | 10% |
| Procurement from BO | 12% |
| Procurement from BWO | 8% |
| Procurement from SBE | 8% |
| Procurement from BYO | 2% |
| Procurement from BPLwD | 1% |
| Core Skills | 2 Safety Officer |
| Critical Skills | 6 Artisans, 2 Quantity Surveyor and 2 Civil Technician |
| Scarce skills | 2 Mechanical Technician |
| Jobs Created (New Jobs to be created For the Local to site) | Contractor to Propose |
| Jobs Retained (Company’s core crew) | Contractor to specify |

*Local Content to Site refers to but not limited to Accommodation, Transport, Fuel, etc. The Employer will make accommodation and transport database available to the Contractor

**Local to Site “means all areas that fall within Lekwa Municipality

Corporate Social Investment (Not a weighted criterion)

The tenderer is required to submit a CSI Proposal to a value of at least 2% of the Contract value as a direct benefit to the Local to site communities

| Criteria | Expected CSI (%) | Target (%) | Proposal |
| --- | --- | --- | --- |
| CSI | 2% | 2% |  |

#### Enterprise Development (ED)

The Contractor shall submit an Enterprise Development plan that seeks to provide assistance or acceleration of black enterprises leading to growth and sustainability of their business.  A detailed ED plan that shows impact to the beneficiary should be submitted to the Employer for approval prior to contract award. ED implementation plan should include:

- Clear objective;

- Priority interventions;

- Key performance indicators; and

- A concise implementation plan with clearly articulated milestones.

First preference shall be given to Local to site EME level 1. Local to site “means all areas that fall within Lekwa Municipality.

### Subcontract documentation, and assessment of subcontract tenders

- The Contractor uses the NEC3 form of subcontract for all subcontracts

- The Contractor provides the the B-BBEE status level verification certificates for all Subcontractors.

- The Contractor informs the Employer when it subcontracts parts of the works

- The Contractor only employs qualified sub-contractors and suppliers as specified in section 4.2.1.

### Limitations on subcontracting

- The Contractor does not sub-contract more that 25% of the contract value to another enterprise that does not have equal or higher B-BBEE status level, unless the intended sub-contractor is an Exempted Micro Enterprise   that has the capability and ability to execute the sub-contract.

- In relation to a designated sector, the Contractor will not be allowed to sub-contract in such a manner that the local production and content of the overall value is reduced below the stipulated minimum threshold (Percentage of the specific contract).

- The Contractor does not subcontracting with his subsidiary companies as this may be interpreted as subcontracting with himself and / or using their subsidiaries for fronting. Where the Contractor subcontracts with a subsidiary this must be declared in tender documents.

### Attendance on subcontractors

The sub-contractor attends all meetings which the Contractor attends and all meetings as required by the Employer which requirement is not a compensation event.

## Plant and Materials

### Quality

Refer to QM58 attached.

### Plant & Materials provided “free issue” by the Employer

Plant and Materials issued by the Employer becomes the responsibility of the Contractor post issue there of pertaining to its identification, traceability and preservation. The following Plant and Materials are “free issued” to the Contractor:

- LV Switchgear IEDs

### Contractor’s procurement of Plant and Materials

The Contractor provides suitable storage at site to store parts and equipment during the installation process. The store needs to be water tight and the parts and equipment should be sealed to prevent moisture and dust. In general the warrantee is one year after commissioning of the unit.

### Spares and consumables

The Contractor supplies the Employer with a detailed complete list of all spares required in order to maintain the Plant as specified in section 3.8.2.1.

## Tests and inspections before delivery

All spares is delivered in approved packaging suitable for storing such parts over a period of ten (10) years without damage or deterioration. The Contractor will be expected to provide a warranty for all spares.

The Contractor provides all test Equipment required for Plant and Materials testing.

The Contractor does not use any of the Employer’s tools and testing equipment for Plant and Materials testing.

Inspection and testing prior to delivery is conducted in accordance with requirements of Eskom Procurement Quality Standard QM58 par 3.5.5 and 3.5.6 with the control of the associated generated documents aligned to that standard and approved project quality plan.

The Supervisor carries out quality inspections at his discretion.

All inspections and testing are performed in accordance with the quality control plan (QCP) developed by the Contractor.

The Project Manager, Supervisor and Others are provided access to the Contractor’s premises for the purpose including but not limited to:

- Establishing compliance with the contractual requirements by means of inspections, surveillance and audits.

- Witnessing the performance of any tests.

The Contractor obtains clearance from the Project Manager before despatching of certain Plant and Materials, these Plant and Materials are agreed upon by the Project Manager and Contractor. This factory release inspection does not release the Contractor of any of his obligations under the contract.

No Plant and Materials is released for dispatch without the AS MANUFACTURED documentation and drawings accompanying them.

### Inspection and Testing

All Plant and Materials are comprehensively tested in accordance with the QCPs prior to delivery which is agreed to between the Contractor and the Project Manager. The Contractor tests and verifies the performance of the Plant and Materials against the requirements and the detailed engineering design freeze documentation.

A documented testing and inspection procedure is submitted to the Project Manager, by the Contractor, for acceptance and is recorded on the ITP/QCP and documented in the data book before any testing is done.

The Project Manager reserves the right to appoint a representative or representatives to inspect all parts during refurbishment and erection, and to be present at any of the tests specified. Such witnessing of tests by the Supervisor, or if the Project Manager chooses to waive the witnessing of any tests, does not relieve the Contractor of his responsibilities.

Tests that are required by the Project Manager are carried out by the Contractor during erection to prove compliance with the specification independently of any test that may have been carried out at the Contractor’s works.

The Supervisor inspects parts of the Plant and Materials at his discretion during manufacturing stages and before shipment as per the agreed QCP.

## Marking Plant and Materials outside the Working Areas

In addition to the information required when shipping (detailed in shipping procedure developed by the Contractor) the Plant and Material, the Contractor marks all Plant and Material with the following information while outside the working areas and ensures that the information is accurate and clear/readable;

- Project Manager name

- Contract name

- Contract number

- AKZ code and description

- Plant and Material description if AKZ number is not applicable

## Contractor’s Equipment (including temporary works).

The Contractor supplies all Equipment that he requires to provide the works.

## Civil and structural contractor/subcontractor CIDB designation

The civil and structural contractor/subcontractors possess Construction Industry Development Board (CIDB) grade 9CE/GB designation. As part of his tender returnable, the Contractor submits the original CIDB Certificate of Registration, or proof of application for the Certificate of Registration for the contractor/subcontractor carrying out the civil and structural works.

# Construction

## Temporary works, Site services & construction constraints

### Employer’s Site entry and security control, permits, and Site regulations

Refer to the Employer’s standard Tutuka Refurbishment SHE Specification GCD/TUT/SHE06.

### Restrictions to access on Site, roads, walkways and barricades

During refurbishment project there are a large volume of people entering the power station premises. Access to the main gate could be a problem. The Contractors are also required to observe the speed limit within Eskom Premises. Refer Tutuka refurbishment Specification GCD/TUT/SHE06.

### People restrictions on Site; hours of work, conduct and records

All Contractor personnel are not allowed on running units.

### Health and safety facilities on Site

Refer to Procedure GCD/TUT/SHE/06

### Environmental controls, fauna & flora, dealing with objects of historical interest

All Environmental issues are governed by Waste management Procedure 32-245 and Management of waste at Tutuka PS/244/001.

The Contractor is responsible for disposal of all the waste generated from Providing the Works in an environmentally friendly manner, ensuring that hazardous (contaminated rubble) and general waste are disposed of at a nearest registered landfill site. The Project Manager needs to be notified of the disposal site before any disposal can be done. For all scrap metal, cables and material the Contractor must submit with the tender the price per tonne for disposal of such material. In case of salvaged equipment, identified by the Project Manager, the Contractor will be expected to safely remove such equipment and store it at the designated site as identified by the Supervisor. The list of all salvaged equipment will be issued to the Contractor before the start of the works / (outage).

### Title to materials from demolition and excavation

None

### Cooperating with and obtaining acceptance of Others

- The unitised blower house buildings has interface to the following:

  - The existing ID fan infrastructure

  - The existing surface slab

  - The existing cable tunnels

The unitised blower house site is in close proximity to the existing IDs.

- The lifting activities required for the removal of the existing ash bunker vent pipe and installation of the new ash bunker vent pipe is conducted by the Contractor with his/her mobile crane.

  - These lifting activities are limited to the movement from the ash bunker vent pipes operating position to grade for removal and the movement from grade to the ash bunker vent pipes operating position for reinstallation, all other lifting activities are conducted by the Contractor [LOSS-06-08-07]

- The upgrade of the existing bucket elevators and associated structural steel and crawl beams on the roof of the ash bunkers is conducted by the Contractor. This includes the upgrading of any equipment that needs to be upgraded/decommissioned (e.g. cabling and cable racking) that is connected/supported to the existing steel structure or crawl beams on the roof of the ash bunker.

- The Contractor is required to work below the ESP casings which are upgraded by Others during the same time the Contractor is installing Plant and Materials. The Contractor needs to take into account that Others are conducting lifting activities with a boom crane and where construction activities create an unsafe working environment below the ESP casings, thus there are times when the Contractors work schedule in the DHP area is interrupted due to the risk of an unsafe environment created below the ESP casings.

The Contractor is required to plan his activities to evade the following interface risks and any other risks which may arise:

- Interface issues arising from working in close proximity to Others, risk of disrupting each Other’s critical path, for instance, through working in the same space at the same time, shutting down utility supplied by one contractor (1) which is required by the another contractor.

- Access

- Material storage

- Delivery, receiving deliveries at Site on the same day

As part of the tender returnables, the Contractor provides a mark-up of the area required for his construction activities showing amongst others excavation perimeter, material storage and equipment layout to enable the Employer to assess interface with Others. The Contractor further submits a construction method statement and risk assessment advising on his proposed approach and methodology to mitigate risks described above and any other risks which may impede successful execution of the works.

The Contractor is encouraged to corporate with Other’s, to plan his activities to accommodate Other’s and where required his plan is sufficiently flexible to accommodate changes which may arise during execution.

### Publicity and progress photographs

The Contractor is not allowed to take any photographs on Site, unless written permission was received from the Project Manager.

### Contractor’s Equipment

The Contractor is required to furnish and maintain the necessary Equipment for the completion of the works which includes, but is not limited to:

Manual and power tools.

Rigging.

Vehicles.

Site workshops.

Mobile Cranes.

Elevators.

Lifts.

Etc.

The Contractor marks all tools, scaffolds, and other Equipment for easy identification. Others are allowed to inspect the shipment of tools and Equipment leaving the Site if so requested. A detailed list of tools and Equipment being shipped off Site is required to be submitted to the Project Manager from the Contractor prior to removal from Site.

The Contractor provides all scaffolding required for the completion of the works.

The Contractor is not allowed to utilise a tower crane, only mobile cranes are allowed to be utilised. If the Contractor is not able to complete a task without a tower crane, this task is brought to the attention of the Project Manager as soon as the Contractor becomes aware of this.

The Contractor includes a construction execution plan outlining the means and methods they intend to use in executing the works. The plan includes the proposed position of Equipment required (e.g. mobile crane arrangement) in sufficient detail to determine the viability of the Contractor’s execution plan.

The Contractor provides all test Equipment for testing the individual modules, the sub-assemblies and the functional groups for site testing and commissioning.

### Equipment provided by the Employer

None

### Site services and facilities

Refer to Employer’s specification Safety, Health & Environmental specification, GCD/TUT/SHEQ06 rev 1. All services and facilities that are not specifically stated to be provided by the Employer and which are necessary for providing the works are provided by the Contractor.

#### Water Supply for Construction Purposes

The Contractor connects to the nearest available water supply point as indicated by the Supervisor.

#### Power Supply for Construction Purposes

The Contractor connects to the nearest available power supply point as indicated by the Supervisor.

#### Site Office, Store and Housing

An area will be made available by the Employer for the Contractor’s site offices, workshops and stores. The Contractor needs to communicate with the Supervisor for site related issues.

#### Telephone Facilities

The Contractor is responsible for arranging his own telephone facilities.

#### Ablution Facilities

Ablution facilities are available on some areas on Site. In areas where the facilities are far from the Contractor working area the Contractor may make the necessary arrangement to provide these facilities.  Chemical serviced toilets are the minimum acceptable standard and maintained in a clean and sanitary condition.

#### Storage Facilities

The Employer has no roofed storage facilities available for use by the Contractor who must make his own arrangements in this regard. There is however a lay down area available on site for the Contractor to temporarily store construction materials. All storage facilities (Plant and Materials and Equipment) are within the boundaries of the Site not to affect the operations of others. ,The contractor shall  delivery  Plant and Material in good order to site, off-loading, safe and preserved storage, removal of old components, installation/erection, site testing, commissioning, performance test (witness and acceptance) and monitoring and remedy of any defects at site in accordance with and subject to the terms and conditions of the contract for the following:

### Facilities provided by the Contractor

#### Contractor’s Yard, Offices, Workshops and Stores

It is required, for the proper co-ordination and execution of the works that the Contractor has an office on Site for the duration of the contract.

The Contractor includes in his establishment rates for all further treatment of the yard areas that he considers necessary for his entire operation throughout his period of occupation and under all weather conditions. The Contractor also includes for all security fencing, security and access arrangements. The yard will be kept clean and tidy at all times, this will include all workshops and storage areas under the control of the Contractor. Maintenance of the yard is the Contractors responsibility and is for the Project Managers acceptance.

Outfall drainage of all surface run-off drains is constructed by the Contractor to the acceptance of the Project Manager to minimise erosion and to effect control of contaminated water. The Contractor’s plan for the layout of his yard area are accepted by the Project Manager prior to occupying the yard and the Contractor does not occupy any site area other than that allocated to him. The Contractor’s plan states fully what measures are taken regarding removal and storage of topsoil, stabilisation of eroded areas and further loss of topsoil.

The Contractor complies with the environmental policy given in the Site Regulations. The Contractor provides, erects and maintains for his own use adequate size office accommodation and stores together with such drainage, lighting, heating, and hot and cold water services as may be required. Provision is also made for adequate parking and a turning area adjacent to all the aforesaid structures. The Supervisor prior to commencement of any work on Site accepts all designs and layouts for these provisions.

The Contractor dismantles and clears the yard of all such temporary structures and associated foundations and infrastructure at the direction of the Supervisor on Completion of the whole of the works. No such dismantling and clearance work is carried out without prior acceptance from the Supervisor.

It is required, for the proper co-ordination and execution of the works that the Contractor has an office on Site for the duration of the contract.

The Contractor includes in his establishment rates for all further treatment of the yard areas that he considers necessary for his entire operation throughout his period of occupation and under all weather conditions. The Contractor also includes for all security fencing, security and access arrangements. The yard will be kept clean and tidy at all times, this will include all workshops and storage areas under the control of the Contractor. Maintenance of the yard is the Contractors responsibility and is for the Project Managers acceptance.

Outfall drainage of all surface run-off drains is constructed by the Contractor to the acceptance of the Project Manager to minimise erosion and to effect control of contaminated water. The Contractor’s plan for the layout of his yard area are accepted by the Project Manager prior to occupying the yard and the Contractor does not occupy any site area other than that allocated to him. The Contractor’s plan states fully what measures are taken regarding removal and storage of topsoil, stabilisation of eroded areas and further loss of topsoil.

The Contractor complies with the environmental policy given in the Site Regulations. The Contractor provides, erects and maintains for his own use adequate size office accommodation and stores together with such drainage, lighting, heating, and hot and cold water services as may be required. Provision is also made for adequate parking and a turning area adjacent to all the aforesaid structures. The Supervisor prior to commencement of any work on Site accepts all designs and layouts for these provisions.

The Contractor dismantles and clears the yard of all such temporary structures and associated foundations and infrastructure at the direction of the Supervisor on Completion of the whole of the works. No such dismantling and clearance work is carried out without prior acceptance from the Supervisor.

### Existing premises, inspection of adjoining properties and checking work of Others

For each designated area of the Site and its surrounds the Contractor, together with the Project Manager, within 14 days prior site establishment of any facility or the starting of any work therein, make detailed records, of the existing state of all areas, structures and other features which will be affected by his facilities.

Such records, photographs, drawings or statements as appropriate, are dated and two (2) copies of each  submitted to the Project Manager prior site establishment of any facility or the starting of any work in that area. The Contractor maintains a duplicate record on Site. The Contractor ensures he has a permit to take photographs on Site.

### Excavations and associated water control

Where required, the Contractor is fully responsible for keeping the excavations free from water whilst the construction work is being carried out. The Contractor provides the necessary pumping equipment, pipes and other necessary equipment and temporary works to deal with water. The Contractor refers to the safety documentation for requirements on how to deal with storm water and ground water and any contaminated water. Furthermore, the Contractor submits a method statement as per VDSS for the acceptance by the Project Manager specifying how he is going to deal with water.

### Underground services, other existing services, cable and pipe trenches and covers

Tutuka P.S. has a network of subsurface cable tunnels, a layout of the cable tunnel network can be seen in the drawing 0.61/1119 sheet 2.

There are existing pipe trenches and cable racks installed at Tutuka P.S., where possible the existing infrastructure should be reused.

Drawings 0.61/96245 Sheets 1 and 2 shows the results of a ground penetrating radar (GPR) scan that was conducted by the Employer. These scan results are utilised for information purposes only, the Contractor is responsible to conduct all scans require to detect any underground services in the areas of construction and excavations.

The Contractor is held responsible for any damage to known services (i.e. services that are within the Site and are shown on the drawings) and he takes all necessary measures to protect them. All work or protective measures are subject to acceptance by the Supervisor. In the event of a service being damaged, the Contractor immediately notifies the Supervisor; the Contractor does not repair any such service unless instructed to do so.

As soon as any underground service not shown on the drawings is discovered, it is deemed to be a known service and the Contractor is held responsible for any subsequent damage to it.

Where the Project Manager elects to carry out, on its own account, any alterations or protective measures, the Contractor co-operates with and allow such party reasonable access and sufficient space and time to carry out the required work. Permanent alterations to or permanent diversion of services necessitated by the execution of the works and authorised is paid for in terms of the conditions of contract.

### Control of noise, dust, water and waste

Refer to GCD/TUT/SHEQ06 rev 1.

### Sequences of construction or installation

The DHP common compressor house is to be constructed by the Contractor, the DHP compressor plant required for the first unit is fully functional before the first unit outage commences. The compressors required for the subsequent units are commissioned before each of the unit outages commences. The compressor house is completed by the Contractor in a sufficient time before the commencement of the outage such that the Contractor and Others can install and commission all Plant and Materials and components required for the  DHP compressor plants for the first unit.

The construction and installation is executed during the power stations outage period (unless specified in the Works Information or is accepted by the Project Manager), the outage duration is constrained. As part of his tender submission the Contractor proposes construction activities which can be executed prior the outage and those which can be executed post outage, whilst noting existing infrastructure. The proposal for any work (unless stated in the Works Information) outside of the outage period (either prior or post) is subject to acceptance by the Project Manager.

The Contractor takes into account additional construction sequencing as attached in Appendix Z.

### Giving notice of work to be covered up

The Contractor gives 24 hours advance written notification to the Supervisor of work to be covered up.

### Hook up to existing works

All terminal points are defined in section 1.4 and the LOSS diagrams in appendix C.

## Completion, testing, commissioning and correction of Defects

### Work to be done by the Completion Date

On or before the Completion Date the Contractor has done everything required to provide the works except for the work listed in Table 18 below which may be done after the Completion. The Project Manager cannot certify Completion until all the work except that listed below has been done and is also free of Defects which would have, in his opinion, prevented the Employer from using the works and Others from doing their work.

Table 18 Items that may be completed after the Completion Date of the works

| Item To be Completed | To be Completed by |
| --- | --- |
| As built drawings of works | Within 14 days after completion. |
| Performance testing of the works after Commissioning | See Performance Testing (as per section 5.2.8) |

### Use of the works before Completion has been certified

The Project Manager utilises any of the Plant and Materials before Completion if there is an emergency which can result in production losses of any of the power station units or if required for commissioning. The Project Manager notifies the Contractor of the requirement for Plant and Materials to be utilised to prevent production losses. The time frame for the use of the required Plant and Materials is agreed upon between the Project Manager and the Contractor.

### Materials, facilities and samples for tests and inspections

The Contractor supplies all of the materials and facilities for all of the tests conducted for the works, the use of Employers testing equipment is not permitted.

If samples of ash are required by the Contractor for testing purposes, the Contractor requests the quantity of ash required from the Project Manager. The Employer supplies the quantity of ash requested by the Contractor as long as the quantity is within reasonable limits. The facilities for any test that the Contractor does on the ash samples is provided by the Contractor

### Commissioning

Commissioning is defined as bringing into service all items of the works as specified, meeting the requirements of the functional Works Information, as well as the control system and all Plant and Materials performance including all necessary testing and verification of the stated performance.

The works covered by the Works Information is installed and complete in all respects by the dates stated in the Accepted Programme. The Contractor provides sufficient personnel for the satisfactory and timely commissioning of the equipment.

Before the works is placed in service, the Contractor certifies that it is in a suitable and safe condition.

Prior to the time when Cold Commissioning commences, the Project Manager notifies the powers station representative responsible for co-ordination of the commissioning of the generating unit such that the commissioning of the works can be incorporated into the commissioning plan of the generating unit.  All GCD commissining will be done as per Procedure :Commissining and completion of refurbishment project at Tutuka Power Station procedure 240-114516712.

The Contractor co-operates with the power station representative/s in the process of commissioning the portions of the generating unit for which the Employer is responsible .

The Contractor develops a commissioning procedure that is submitted to the Project Manager for acceptance.

The Contractor provides all Equipment required for the commissioning of the works.

#### Pressure Testing

A pressure testing procedure is finalised and submitted to the Project Manager for acceptance prior to the finalisation of the design.

Prior to any commissioning activities commencing, the works requried to be pressure tested are tested according to the requirements specified in the design code utilised.

The Contractor provides all test Equipment required for pressure testing.

#### Cold Commissioning

The purpose of Cold Commissioning is that, following completion of no load checks; the plant is run without load to certify that it is complete in all respects.  The checks include but not limited to:

•           Final inspection of plant by commissioning engineers.

•           Charge system with media.

•           Ensure electrical power to motors is connected up.

•           Direction checks of motors.

•           Coupling alignment check.

•           Eliminate any unacceptable vibrations.

•           Thorough test of interlocks and protective systems. Replace all guards and covers removed to carry out this work.

•           Check calibration of all instrumentation such as level switches.

#### Hot Commissioning

The Contractor notifies the Project Manager that Cold Commissioning is complete and requests the commencement of hot commissioning.

The purpose of hot commissioning is to prove the performance of the works to the Project Manager. The Contractor's commissioning manager and his engineers, assisted by Employer’s engineers are responsible for hot commissioning. The checks include but not limited to:

•           Coupling up to driven units.

•           Setting driven units in motion.

•           Check system integrity.

•           Direction check of motors.

•           Check the calibration and rectify where necessary all system instrumentation.

•           Verification of sequence controls and interlocks.

•           Check all process flows.

•           Complete all remedial work for acceptance by Project Manager.

•           Train operating staff (at least 2 training sessions)

Contractor carries out a 72 hour proving period as required by Employer

The Employer is responsible for plant preparation for hot commissioning. However, for that portion of the works, which cannot be commissioned separately from other plant areas, the commissioning is at the discretion of the Project Manager for the particular stage of commissioning.

In those cases where various components (existing or new) are connected to form an integrated system, the Contractor, at the time of commissioning, carries the responsibility for the correct functioning of the whole of the system.

If a defect is identified in the equipment interfacing or external to the Contractor’s scope the Contractor directs the Project Manager’s to rectify the defects.

##### Functional Tests

The functional tests form part of the Cold Commissioning of the control system and are to include the checking of all measurement loops, interlocks, sequence controls and analogue controls.

##### Valve and Damper Tests

All dampers, analogue and binary valves are local and/or remote manual operated and checked for correct operation by the Contractor.

These tests are conducted in conjunction with the Supervisor and Others. Special care is given to safety aspects, rotation direction, special function limits, torque settings, position indication and mechanical stops.

The Contractor is responsible for the setting of limits (stroke checking), torque settings and position indication.

##### Electrical Drive Tests

All electrical drives are local and/or remotely operated and checked for correct operation by the Contractor.

These tests are conducted in conjunction with the Supervisor and Others. Special care is given to safety aspects, motor rotation direction and protection.

### Start-up procedures required to put the works into operation

All start up will be done as per GCD commissioning and completion of refurbishment project at Tutuka Power Station procedure. CMD/TUT/CP/001

### Take over procedures

Takeover will be done as per GCD commissioning and completion of refurbishment project at Tutuka Power Station procedure. CMD/TUT/CP/001Access given by the Employer for correction of Defects

### Performance tests after Completion

After Completion of the works the Contractor applies formally to the Project Manager to conduct any tests on the works. No optimisation and commissioning of any Plant and Materials is permitted during any testing periods.

The Contractor develops and submits for acceptance to the Project Manager a complete testing and inspection procedure for all tests/test phases to be conducted after Completion of the works. The testing and inspection procedure includes all tests and inspections deemed necessary by the Contractor to prove to the Project Manager’s satisfaction that the works performs according to the Employers specification. The testing and inspection procedure includes as a minimum:

- Reliability Tests.

- Capacity Testing.

- Operational acceptance tests

- Capability acceptance tests

The following are confirmed during the testing of the works:

- The control system performs according to the design with reference to control, sequence starting and stopping and all devices, limits and communication links are operating correctly.

- No spillages.

- No water or air leaks.

- Acceptable levels of dust in the environment.

- The DHP system is capable of starting, with full conveyors and bucket elevators, after a loaded system trip.

- The ash conditioners and conveyors are capable of starting, with full ash conditioners and conditioner conveyor belts, after a loaded system trip.

- The conditioners are capable of restarting with a full load of ash, after a trip at full capacity.

- All required functional operations of the works under load.

- Air and power consumptions.

- Conditioned ash moisture content.

In the case of a failure of any of the tests/test phases, the functional tests for the relevant areas of the works and all affected areas of the works are repeated. The capacity and reliability tests are redone in total on the relevant portions of the works.

During the test period, the Employer’s personnel operate the works, under the supervision of the Contractor. The Contractor is not permitted to directly operate or make changes to the works.

The Project Manager reserves the right to carry out further testing on the works.

On completion of all the tests the Contractor supplies in triplicate, completed test certificates. The Contractor supplies all prescribed statutory documents as are required, certifying that the works are in complete working order and that all working parts are evenly lubricated.

The Contractor provides all test Equipment required for the performance tests.

#### Reliability Test

Reliability test constitutes at least thirty (30) days of continuous operation of the works in automatic mode, of which the last seven (7) days are completely trouble free.

The works are considered to have passed the reliability test when the stoppages as a result of the works is limited to a maximum of 0.5 incidents per day and the downtime as a result of the combined stoppages is less that fifteen (15) min per day on average, measured over the thirty (30) days continuous operation in the fully automatic mode with no control simulations in place.

#### Capacity Test

The capacity test consists of as a minimum two (2) separate tests. These tests are as follows.

- The works operates at normal capacity for a continuous period of more than twenty four (24) hours while the unit operates at full load.

  - The works operates satisfactorily with no indication of constraints while operating under these conditions.

- The works operates at the backlog capacity for a continuous period of at least twenty four (24) hours.

  - The works operates satisfactorily with no indication of constraint on the functional performance for the extended operation at this maximum capacity.

#### Operational acceptance tests

On completion of the hot commissioning, the Contractor requests the commencement of operational acceptance tests from the Project Manager.

The Contractor produces a detailed operational acceptance test procedure twenty (20) working days in advance for acceptance by the Project Manager.

The control system is pre-tuned in order to prevent deviation limits of process parameters from exceeding the maximum permissible values defined during the technical clarification stages.

After satisfactory completion of installation and commissioning of the control system in conjunction with the works, the Contractor demonstrates that the control system successfully performs the following:

- The works operated local and/or remotely and in all other modes of operation.

- The works operated on manual with all remote supervisory/monitoring functions in the main control room.

- The works operated automatically (start-up, sequential control and shutdown) with all remote supervisory/monitoring functions.

- The works operating on modulating control, responding to a safe and stable state for dynamic changes in the plant.

- All individual operating and control functions such as alarms, displays, report generation, historian views, perform successfully.

Process server and station plant information system functions are demonstrated, including process LAN and client access operations according to the Works Information and all archiving and back-up functions.

The Contractor notifies the Project Manager on completion of operational acceptance tests.

#### Capability acceptance tests

The Contractor performs capability acceptance tests. These capability acceptance tests prove that the control system is fully optimised to meet the Works Information requirements as well as the safety of the works and performance tests are accepted by the Project Manager for operation.

### Training and technology transfer

Training courses for the Employer’s Engineering, Maintenance and Operating personnel are provided by the Contractor to ensure that the Employer’s personnel are fully conversant in operating, testing, fault finding and maintaining the new systems. The training program is developed by the Contractor and accepted by the Project Manager. The training includes but it not limited to the following:

- The Contractor provides training on the Plant and Materials included as part of the works to the various categories of the Employer’s technical staff.

- All training is at the power station, provided by the Contractor, and customised for Tutuka P.S. and is directly applicable to the actual Plant and Materials supplied for the works.

- Training is focused on the specific systems’ architecture, configuration, layout, Plant and Materials and design that the Contractor provides.

- Training facilities are provided by the Contractor.

- Training material and tools are not shared by trainees during the training.

- The training facilities provided are:

  - Air-conditioned and suitably sized.

  - Accommodates all trainees comfortably.

  - Includes all engineering tools and workstations.

The training is provided as per the detailed training programme and prospectus accepted by the Project Manager

Classroom and practical hands-on training where required is provided to the Employer’s personnel.

#### Control and Instrumentation Training Requirements

The first training required is on compressor PLC/controller system configuration, network configuration and logic functions for the engineering staff that will be involved with the operating and maintaining the works.

The next part of training is for maintenance and engineering personnel to prepare them for commissioning and maintenance of the works. The scope of training, as a minimum, includes O&M Manual, field instrumentation set-up, use of commissioning tools, signal loop drawings for trouble shooting, network configuration and system alarm response procedure. This training is offered before Cold Commissioning begins.

The last part of training is for operating personnel to prepare them for commissioning and monitoring of the plant after takeover. The scope of training, as a minimum, includes PFD’s, O&M manual, process design and operation, the layout and information in the new mimics, the role of the control system in plant control (interlocks), the limitations of the control system in plant control, alarms to be monitored and responded to. This training is provided before Cold Commissioning begins.

#### Training Documentation

The Contractor develops all course materials for the training provided. The course material consists of but is not limited to:

- Training Manual.

- Training presentation to be presented during training.

- Facilitator Manual.

The Contractor develops the training manuals in the template provided for in Appendix M

The course material is in English and includes all third party documentation.

Printed and soft copies of training documentation are supplied for each trainee. An additional three (3) hard copy master sets and one (1) soft copy is also supplied.

All training documentation provided by the Contractor is customised for Tutuka P.S.

Training manuals are continuously updated by the Contractor up to Completion for the entire works.

#### Trainee participants

The total number of participants trained is 177, the categories are as follows:

- Basic and Advanced maintenance		: 26, three sessions required.

- Operator					: 130, 10 sessions required.

- Engineering Training			: 14, 2 sessions required

- Training Facilitators				: 7, 1 session required

The Employer bears the cost of salaries, accommodation, travelling expenses and other allowances of his personnel during the training, but all other training costs are borne by the Contractor.

The Contractor submits a training plan to the Project manager for acceptance.

### Operational maintenance after Completion

N/A

# Plant and Materials standards and workmanship

The Contractor supplies all Plant and Materials and conducts all work in accordance with the following specifications.

## Civil Specification

### Investigation

#### Scope

The Contractor assesses the requirement to carry out any geotechnical investigation for use in his design; where the Contractor deems it necessary to carry out geotechnical investigations; the Contractor makes provision for Equipment, personnel, testing facilities and any other requirements necessary to successfully carry out such geotechnical investigation.

#### Scheduling

The Contractor informs the Project Manager in writing, at least 14 days before commencing such work, of his intention to perform any geotechnical work. The Contractor schedules the geotechnical studies such that it does not result in any delays in his programme and Others.

#### Excavation permits

Requirements for excavation permit are set out in the procedure GCD/TUT/SHE06.

### Survey control and setting out of the works

The Employer provides the primary survey control beacons as shown on drawing 0.61/1101, the Contractor establishes through an approved land surveyor/engineering surveyor his own secondary control beacons closer to the specific site. The Contractor is responsible for accurate setting out within the required tolerances as shown on the drawings and specifications. The current system on site is Lo29° and the Contractor uses the same system.

Upon access to the Site and prior to commencement of any excavation works, the Contractor  carries out a comprehensive site survey and verify coordinates, elevations and dimensions with those shown on the drawings, for submission to the Project Manager along with a report highlighting any discrepancies, error or omission for acceptance.

The Contractor is required to conduct pre and post concrete pour survey and submit the results in reports to the Project Manager for review and acceptance.

Below is the minimum detail required on a survey report:

- Area surveyed

- Type of survey (Pre/Post/Excavation etc.)

- Control beacons used

- Relevant drawing number and revision (not the general layout, the actual drawing indicating position & dimensions for surveyed item)

- Date of survey

- Difference to design position (Y, X & Z)

- If it is items with a very tight tolerance (bolts) supply the difference perpendicular to the structures gridlines, and not the difference between the Y & X coordinates (see Figure 5 below).

Figure 5: Bolt Setting Out

### SANS 2001 BS1: Site clearance

SANS 2001-BS1:2008	South African National Standard Construction Works Part BS1: Site Clearance

Specification data pertaining to SANS 2001-S1: 2008 is as listed in the table below. The clause listed in the table below refers to the clause number in SANS 2001-BS1 and the table below must be read in conjunction with the code.

| Clause | Specification data |
| --- | --- |
| 3 | Definitions |
| 3.2 | The designated area on which work is carried out is shown on the drawings, this includes areas identified by the Contractor to suit works designed by him and the Contractor's working and accommodation areas, the areas required for the construction of temporary roads, and the area required for the laying down of any services. Construction of the unitised blower house buildings does not require any Clearing, Grubbing and Topsoil removal as the area is currently covered with a reinforced concrete slab. |
| 3.4 | The levels of the finished earthworks are as shown on the drawings. |
| 4.1 | Areas to be cleared and grubbed |
| 4.1.3 | Not applicable. |
| 4.2 | Clearing |
| 4.2.1 | Activity numbers 1, 2, 5, 10 and 11 apply. |
| 4.2.1 | The depth for scarifying and breaking up hardened material is as shown on the drawings. |
| 4.2.3 | Use of masonry units is not permitted. |
| 4.4 | Disposal of material |
| 4.4.1 | Materials from Clearing and Grubbing operations are disposed of at an approved disposal site. Disposal certificates are kept on record by the Contractor. |
| 4.4.1 | Combustible material is disposed of as follows: - Cleared combustible material is taken to an approved waste disposal site. - Disposal certificates are kept on record by the Contractor. |
| 4.4.2 | Tree trunks and cleared tree debris are taken to a suitable waste disposal site |
| 4.4.3 | Fencing material is stacked at a site proposed by the Contractor and accepted by the Project Manager. |
| 4.4.4 | The material which is to be reused is stacked at a site proposed by the Contractor and accepted by the Project Manager. |
| 4.10 | Such flora is replanted in the following areas: - All flora not used as per variation clause 1 below is replanted as instructed by the Project Manager |
| Variations |  |
| Cl 4.9 | Add the following Topsoil stripping is scheduled for the dry season, as far as possible. |
| Cl 4.9 | Add the following Topsoil is handled twice only - once to strip and stockpile, and secondly to replace, level, shape and scarify. |
| CL 4.9 | Add the following Topsoil stripped from different sites is stockpiled separately and clearly identified as such. |
| Additional Clauses |  |
| 1 | The size of areas subjected to land clearance is kept to a minimum |
| 2 | All vegetation not required to be removed is protected against damage |
| 3 | No trees are removed without prior permission in writing from the Project Manager. |

### SANS 2001-BE1: Earthworks

SANS 2001-BE1:2008 South African National Standard Construction Works Part EB1: Earthworks

Specification data pertaining to SANS 2001-EB1: 2008 is as listed in the table below. The clause listed in the table below refers to the clause number in SANS 2001-EB1 and the table below must be read in conjunction with the code.

| Clause | Specification data |
| --- | --- |
| 4.1 | Materials |
| 4.1.1 | The following materials are required in embankments and terraces: a) material with a CBR of at least 3 % at the minimum specified density (compacted at OMC) and ab) hard material or rock material with a maximum dimension of 300 mm; or c) both clay or clayey material of a liquid limit that exceeds 40, or PI that exceeds 18 (or both), and rocks or boulders that have a maximum dimension greater than 300 mm, provided that they 1) are not placed against structures, and 2) are placed in predetermined quantities and in specified parts of the fill, in accordance with the requirements of 4.2.5.1; or d) materials that can be compacted so as to avoid settlement that exceeds 2 mm/m of depth of excavation, and that contain no more than 10 % rock or hard fragments retained on a sieve of nominal aperture size 50 mm and that contain no large clay lumps that break up under the action of the compaction equipment used. PI not exceeding 18 |
| 4.1.2 | Materials suitable for replacing the backfill in overbreak for foundations are capable of sufficient compaction to avoid settlement and are capable of placement without significant voids. 4.1.2.2 The backfill is not to contain appreciable quantities of organic matter or stones of average dimension exceeding the lesser of 150 mm or two-thirds of the thickness of the layer being compacted. In addition, the backfill is graded material that has a PI not exceeding 10 and a CBR of at least 10 % at the minimum specified density compacted at OMC. |
| 4.1.5.2 | Materials from excavation is disposed of as follows: Surplus and unsuitable material is disposed of in areas designated in the drawings. Spoil heaps are flattened to present a neat level or graded surface. |
| 4.2 | Methods and procedures |
| 4.2.1.1 | All areas in which excavation is to take place where applicable, are cleared in terms of SANS 1001-BS1. |
| 4.2.1.3 | The overburden is stripped and removed to depth of 300mm. |
| 4.2.2.1.1 | Materials from excavation is not preferred to materials from borrow pits or other sources. |
| Additional Clauses |  |
| 1 | The area where the unitised blower house buildings are to be constructed is currently surfaced with a reinforced concrete slab with estimated thickness ranging from 200 mm to 350 mm, where the finished floor level i.e. top of concrete of the surface slab is taken as the 0.0m level (ground level). Each building spans over a cable tunnel running west to east of the power station, the top of concrete of the cable tunnel roof is estimated to be 0.95m below ground level and the underside of tunnel is estimated to be 4m below ground level. The underside of the blower house buildings foundation is at 4.1 m below ground level. The compressor house building spans over a cable tunnel running west to east of the power station, the top of concrete of the cable tunnel roof is estimated to be 0.24m below ground level and the underside of tunnel is estimated to be 3.255m below ground level. The Contractor takes means to verify position and depth of cable tunnels to ensure method of excavation does not damage cable tunnels, where there are deviations in location and depth of the cable tunnel to those shown on the Employer’s drawings the Contractor notifies the Project Manager. |
| 2 | Design of Excavations The Contractor is solely responsible for the design and installation of all temporary works to ensure the stability of the excavations. The Contractor provides his proposals to the Project Manager for acceptance before excavation work commences on site. |
| 3 | Excavation Classification The Contractor uses any method he chooses to excavate any class of material but his chosen method of excavation does not determine the classification of the excavation. The Contractor uses guidelines for excavation classification and methods set out by SANS 1200. The Contractor removes and reinstates the reinforced concrete surface area to the extent specified by the Contractor on his working area layout; to allow excavation of the unitised blower house buildings the method used for removal of the surface slab is such that no damage and vibration should propagate to the remaining slab. The Contractor submits his proposed method of removal of concrete during tender. The following ground conditions were encountered during geotechnical assessment at the location of the compressor house building. • A 0.2 m top layer consisting out of a mixture of ash, coal dust and soil particles. • From a depth of 0.2 m to 1.8 m fill material consisting out of light brown sandy silty soil. • Numerous pebble to cobble sized residual shale was found in the fill material. • Around a depth of 1.8 m medium dense residual shale was encountered. • The residual shale marks the start of the natural ground. Due to the close proximity of the compressor house and blower house building’s foundations to existing cable tunnels, care is taken not to undermine the cable tunnel. |
| 4. | The Contractor notifies the Supervisor of his intention to excavate 7 days prior excavation, no excavation work to commence without the presence of the Supervisor. |

### Building works

#### Scope

This section deals with the requirements for building works constructed.

#### Materials and Workmanship

Only skilled labour is employed in this trade and only new and undamaged materials are used in the works.  Materials permanently installed in to the works are not used for any temporary purposes on Site. Materials used in accordance with the relevant manufacturer's written recommendations and instructions.

#### Brickwork

##### Materials

###### Cement

Cement complies with section 6.1.6.

###### Lime

Lime is hydrated bedding mortar lime complying with SANS 523.

###### Sand

Sand complies with SANS 1090, washed where necessary and screened through a 2.4 mm mesh sieve.

###### Burnt clay bricks

Burnt clay bricks comply with SANS 227.

Common bricks exhibit a liability to efflorescence not in excess of "Slight" and water absorption when tested in conformity with the requirements of SANS 227 does not exceed 14 per cent.

###### Concrete bricks

Concrete bricks comply with SANS 1215 and have a minimum compressive strength of 7 MPa.

###### Wire ties

Wire ties are the "Butterfly" or modified PWD type for hollow walls, of galvanised steel and comply with SANS 28. Ties are of sufficient length to allow not less than 75 mm of each end to be built into brickwork or embedded in concrete.

###### Brickwork reinforcement

Brickwork reinforcement is manufactured from hard drawn steel wire conforming to BS 785 and consists of two 2.8 mm diameter main wires with 2.5 mm diameter cross wires at 270 mm centres welded at intersections.

Brickwork reinforcement is lapped not less than 270 mm at end joints and for a length equal to the width of the widest reinforcement at intersections.

###### Mortar

Brickwork, is built in mortar Class II and complies with Table 1Table 19 below.

Table 19 Mortar classes

| Mortar Class | Portland Cement Kg | Lime Litres | Sand (measured loose and damp) Litres max. |
| --- | --- | --- | --- |
| I II III | 50 50 50 | 0 - 10 0 - 40 0 - 80 | 127 200 270 |

Mortar mixing is done with mortar mixing machines or on clean non-absorbent closed jointed platforms.  The platforms are well cleaned before mixing each batch.

###### Faced Brickwork

General

Facing bricks are sorted to ensure that proper mixing of the bricks within the colour range is obtained; sudden changes in the color of face work is not acceptable. Facing bricks are even in size and shape and equal to Samples submitted to and accepted by the Project Manager before use.

Bedding and Pointing, etc.

Faced work, is built as described on the architectural drawings. All perpends are to be accurately kept.  Scaffold boards against faced work are turned away from walls during rain.

Samples

Samples of the bricks to be used on Site including face bricks and stock bricks are submitted to the Supervisor for his acceptance and after acceptance these Samples are retained by the Project Manager for the duration of the contract.

Notwithstanding the acceptance of any Samples the Contractor ensures that all bricks used on Site are well burnt and cured and not subject to excessive shrinkage. Underburnt or immature bricks are rejected.

##### Workmanship

Care is taken to keep cavities free from mortar droppings or other mortar and temporary openings are left at the bottom of walls through which any droppings, etc., can be removed on completion and on completion these are to be bricked up.

Weep holes are formed, at approximately 900 mm centres, in the outside skin of cavity walls by leaving open perpends in the lowest course of brickwork immediately above the damp-proof course.

Brickwork is built within normally accepted tolerances being vertical as reflected on a builder's level and without bowing or bulging. Bowing or bulging in excess of 10 mm over any 3 m length will be rejected as unacceptable.

Where brickwork, built to unacceptable tolerances, is not condemned by the Supervisor, any resultant additional costs involved in modifications to finishes or other components is for the account of the Contractor.

The brickwork is carried up in a uniform manner, no part being raised more than 1.2 m above adjoining work. Where necessary, bricks are soaked with water before being laid and the course of bricks last laid is well wetted before laying a fresh course upon it.

Walls in thicknesses of more than one skin have the skins tied together with wire ties, at least five ties per square metre. Linings to concrete, unless otherwise specified, are tied to the concrete with wire ties, at least, five (5) ties per square metre.

Hollow walls, unless otherwise specified, are built of two half brick skins with cavity between, tied together with wire ties, at least five (5) ties per square metre.

Descriptions of beam filling are deemed to include for cutting and fitting between roof members, carrying hard up to the underside of roof coverings and flushing up in mortar.

Mortar joints to brickwork are not less than 5 mm or more than 10 mm thick and descriptions of brickwork, unless otherwise specified, is deemed to include for raking out joints whilst the mortar is soft to form an adequate key for plaster or mortar backing.

###### Setting up and Building in of Frames, etc.

Wherever frames, etc., are fixed in brickwork, or against steel they are left perfectly watertight and the descriptions are deemed to include for the following:

- Building of brickwork hard up against frames, etc., cutting of mortises and pinning or building in of lugs in mortar or screwing to plugs in concrete, including holes, screws and plugs, bedding solid in mortar around windows, frames, etc., as necessary and pointing all round on both sides.

- Screwing or spot welding of steel at not exceeding 500 mm centres including all necessary countersunk self-tapping screws, holes and welding.

- Necessary bracing and strutting of frames, etc., to prevent distortion.

#### Waterproofing

##### Materials

Damp proofing and waterproofing comply with the requirements given in Table 20below.

Table 20 Waterproofing materials

| Material | SANS | Type and/or Additional Requirements |
| --- | --- | --- |
| Bituminous damp-proof course to wall, sills, etc. Polyethylene sheet in damp-proof course to walls, sills etc. Ditto to floors and basements Mastic asphalt for roofing Mastic asphalt for damp-proof coursed and tanking Bituminous roofing felt Polyethylene sheet for the waterproofing of flat roofs Chloroprene rubber sheet (for waterproofing) Sealing compounds with two-component polysulphide base | 248 952 952 297 298 92 952 580 110 | Type FV Type B Type C - - Type 60 Type A At least 2.5 mm thick and 1200 mm wide Type 2 Gun Grade |

###### Application

Waterproofing materials are applied in accordance with SANS 10021.

###### Damp Proof Course on Walls

All joints in damp-proof course on walls are lapped a minimum of 150 mm except at junctions and corners where the lap is equal the full thickness of the wall.

###### Insulation

Insulation is “Sisalation 420" heavy industrial grade aluminium foil based or other accepted insulating sheets.

#### Carpentry and Joinery

##### Materials

Materials comply with the requirements given in Table 21 below.

Table 21 Materials for carpentry and joinery:

| Material | SANS |
| --- | --- |
| Materials for thermal insulation for buildings Flush doors Mild steel nails Metal screws for woods Fasteners for sheet roof and wall coverings Creosote | 1381 545 820 1171 1273 538 |

#### Steel Roofing

Roof sheeting is as specified on the architectural drawings; sheeting is free of white rust. Sheets are laid with a side lap of one corrugation (narrow flutes uppermost) and fastened with stainless steel hex-head fasteners to steel unless otherwise described, placed through narrow crowns of sheets at alternate ribs, that is one at each side lap and one in middle flute. Side laps are sealed with continuous Seelastick sealing strips and are stitched with sheetbolts or self-tapping screws at maximum 600 mm centres. All fasteners including sheetbolts, inside laps are fitted with round bitumen and flat galvanised steel washers.

#### Doors

##### Fire Resisting Doors

Fire resisting doors are purpose-made to class shown on the architectural drawings and comply with SANS requirements and tested and certified.

The doors are hung in a purpose made frame according to the manufacturer’s instructions and fitted with a locking mechanism.

#### Floor Coverings

##### Materials

Floor coverings and wall linings are as shown on the Employers drawings.

###### Acceptance of Screeds

Before laying the floor coverings, the Contractor satisfies himself that the surface to receive the floor covering is laid level and true and finished to a suitable surface to take the floor covering and that all screeds, etc., are thoroughly dry before the floor covering is laid.

#### Ironmongery

##### Locks, etc.

Locks are specified in the architectural drawings and comply with SANS 4.

##### Keys

Locks do not have interchangeable keys. Each lock has two keys and clearly marked with consecutive numbers and each key is punched with the corresponding number of the relative lock.

##### Fixing

Unless otherwise described, ironmongery is fixed to wood.

Items described as "plugged" are deemed to include for screwing to fibre, plastic or metal plugs.

Screws, bolts, etc., for fixing of ironmongery are of matching metal and finish, except for aluminium ironmongery or ironmongery fixed to aluminium in which case stainless steel screws may be used.

All necessary preparation of pressed steel door frames for the fixing of ironmongery to the frames is included with the pressed steel door frames.

#### Metalwork

##### Bolts and Nuts

Bolts and nuts, other than fitted bolts and nuts for friction grip joints, comply with the requirements of SANS 1700 or SANS 1143 as applicable. Nuts are of at least the strength grade appropriate to the grade of bolts or other threaded element with which they are used.

##### Screwing of Metalwork to Steel, Wood, Concrete, etc.

Where metalwork is described as "screwed" to steel, wood, etc., or "plugged" to brickwork or concrete, descriptions are deemed to include for fixing at not exceeding 500 mm centres, with necessary holes, countersinking, threading, screws, set screws, self-tapping screws and fibre, plastic or metal plugs.

#### Pressed Steel Doors, Frames, etc.

##### Door Frames

Door frames comply with SANS 1129.  Frames do not project less than 20 mm into floor finish. Frames are fixed to jambs and heads of openings. Frames for single and double doors are provided as shown in Employer’s design drawings.

Pressed steel door frames are manufactured from mild steel sheet, 1.6 mm thick for double rebated as shown on the architectural drawings. Head and jamb members are accurately bent to form the profile.  Corners are mitred and welded and also reinforced with 1.6 mm steel angles. Each frame is provided with a pair of sturdy channel section tie bars, welded below the frame. Where required for additional strength, cross struts of the same section are welded between and at right angles to the main ties. Adjustable 227 mm corrugated lugs are supplied with every frame. All frames are thoroughly cleaned, free from rust, scale, grease, etc., and painted with one coat oxide primer before despatch and are carefully protected in transit and during erection from twisting, dents and distortion.

##### Purpose made Doors, etc.

Purpose made doors, are constructed with doors of universal steel sections not less than 29 mm wide and not less than 4 mm thick.  Fittings are brass with three lever mortise locks and heavy lever handles and bolts.

Bottom openings in doors are fitted with kicking plates of 1.6 mm mild steel sheet fixed with metal beads.  Frames of outward opening doors are fitted at bottom with sills of door framing section (stepped sills) and of inward opening doors with metal ties, welded to frames, for embedding in thresholds.

#### Plastering

##### Preparatory Work

Surfaces are clean and free of oil and thoroughly wetted directly before any plastering or other in-situ finishes are commenced.  Concrete surfaces are slushed with a mixture of one part cement and one part coarse sand or otherwise treated to form a proper key.

##### Finish

All final coats of paving and plastering are executed in one operation without any blemishes. No touching up of finished work is permitted.

##### Screeds

Screeds are composed of one part cement and four parts sand; steel floated to true, even, level and fine textured finish suitable to receive finish specified.

All screeds to receive vinyl or other similar floors have a smooth polished finish, (cement sprinkle and steel floating) in accordance with the recommendations of and to the entire satisfaction of the flooring specialist.

##### Plaster

###### Thickness

Plaster thickness is as shown on the architectural drawings.

###### Patching

All cracks, blisters and other defects are carefully cut out and made good and the whole of the plaster work is to be left in perfect and clean condition on completion.

###### Cement Plaster

Cement plaster is composed of one part cement and five parts sand.

###### Tolerances

The tolerances for finished surfaces are as specified on the architectural drawings.

#### Painting

##### Materials

Paints, primers, undercoats, etc., comply with the requirements given in Table 22 below.

Table 22 Paint specifications

| Material | SANS | Grade or Type |
| --- | --- | --- |
| Priming coats on structural steel Priming coats on steel Priming coats on galvanised iron Red oxide zinc chromate primer Undercoats for paint (except emulsion paint) Distemper Emulsion paint for internal work Emulsion paint for external work Matt, eggshell or semi-gloss paint for internal work Oil gloss paint for internal and external work High gloss enamel paint for internal and external work Roof paint Structural steel paint Aluminium paint Varnish for interior use | 312 679 723 909 681 322 633 634 515 631 627 633 684 682 887 | Type II Grade I Type I - Type III Type I - Grade I Synthetic Polymer base - - Grade I Type B Type B Grade II Type I |

Materials for paintwork are delivered to the site in unopened containers and applied in accordance with the manufacturer's instructions. If necessary, materials are strained before use. Materials are suitable for application to the surfaces concerned. Undercoats are recommended by the manufacturer of the finishing coats. Thinners and other agents are not used without acceptance from the Supervisor.

##### Preparatory Work

###### General

All walls are thoroughly cleaned prior to commencement of painting and the premises kept clean and free from dust during painting operations. All surfaces not being painted are protected against spotting and spilling and cleaned down and made good as necessary. Locks, door handles and similar fittings or fixtures are removed (or masked) and refitted on completion of painting.

###### Plastered Surfaces, etc.

Plastered surfaces are thoroughly washed down and brushed in order to remove any traces of efflorescence and allowed to dry completely before any paint finish is applied.  Before any paint is applied, holes, cracks and irregularities in plaster and other surfaces are filled with suitable filler and finished smooth.

###### Metal Surfaces

Metal surfaces are sanded, where necessary, washed with a suitable cleaning agent and left smooth.

Protective coatings applied by manufacturers to galvanised metal surfaces are removed with a suitable agent and the surfaces washed down.

Rust, grease, and defective factory primers on metal surfaces to be painted, as well as pitch on cast iron pipes, are removed.

###### Wood Surfaces

Wood surfaces are prepared and painted as per paint manufactures instructions.

###### Application of Paint

Primers to other surfaces may be applied by roller with the acceptance of the Supervisor. Undercoats and finishing coats may be applied by brush or roller.

Paint is not sprayed on except in the case of cellulose and other special paints where spray painting is the accepted method of application.

Before subsequent coats of paint are applied the previous coat is properly dry and is sanded down where necessary.

Should a perfectly uniform finish and texture, free from any blemishes and with sufficient coverage, not be obtained as a result of defective preparation of surfaces and/or application, the Contractor applies an extra coat or coats of paint of the prescribed finish at his own expense.

###### Protection and Cleaning

The Contractor provides necessary tarpaulins, covers, etc., for the protection of the works. Before the paintwork is commenced all floors are swept and walls dusted and no further sweeping or dusting is allowed before all painted surfaces are perfectly dry.

###### Priming

Backs of wooden doors built in as the work proceeds, are primed before building in, whether the article is to be painted or not, to prevent moisture seeping into the wood from the masonry backing.

Priming to all surfaces such as backs of fascias and barge boards is applied before the timbers are fixed in position.

###### Doors and Windows

All doors and opening sections of louvers left ajar after painting or varnishing until the paint is perfectly dry.

###### Structural Steelwork

Paintwork for structural steel is performed as specified in Painting and Corrosion Protection - Section 6.1.7.

Design and construction of the structural systems complies with the codes and standards listed in Appendix E of the Works Information.

### SANS 2001 CC1: concrete works (structural)

This section deals with the manufacture, transportation, placing and testing of concrete and mortar used in the works where unreinforced and reinforced concrete is specified.

The Contractor establishes the concrete mix properties, submits documentation specified in this section of the Works Information and VDSS, prepares and implements a quality control plan and documents performance requirements have been met. The works is to be certified by the Contractor confirming compliance with requirements, whilst meeting production and delivery requirements.

The following codes are applicable:

| Code |  | Description |
| --- | --- | --- |
|  | Occupational Health and Safety Act (85/1993): Construction Regulations, 2014. |  |

SANS 2001-CC1:2012	South African National Standard Construction Works Part CC1: Concrete Works (Structural)

Specification data pertaining to SANS 2001-CC1: 2012 is as listed in the table below. The clause listed in the table below refers to the clause number in SANS 2001-CC1 and the table below must be read in conjunction with the code.

| Clause | Specification data |
| --- | --- |
| 4.2 | Materials |
| 4.2.1 | Cementitious binders |
| 4.2.1.1 | Cement required is CEM I-42.5R, Ordinary Portland Cement and complies with the relevant requirements of SANS 50197-1. |
| 4.2.3 | Aggregates |
| 4.2.3.1 (b) | The course aggregate nominal size is specified as follows: Cover to rebar < 25 mm – 13.2 mm diameter Cover to rebar >= 25 mm – 19 mm diameter |
| 4.2.3.4 | Plums are not permitted. |
| 4.2.3.5 | The following tests are required: a) Drying shrinkage on fine and coarse aggregates b) Drying shrinkage of concrete c) Flakiness index of the stone d) Alkali-silica reaction |
| 4.2.4 | Admixtures, air-entrainment agents and curing agents |
| 4.2.4.1 | The use of admixtures is permitted, provided that the results of trial tests which demonstrate their suitability and the following are submitted to the Project Manager for his acceptance: - The trade name of the admixture, its source and the manufacturers’ recommended method of use - Typical dosages and possible detrimental effects of under and over doses. - Whether compounds are likely to cause corrosion of the reinforcement or deterioration of the concrete. - The average expected air content of freshly mixed concrete containing an admixture that causes air to be entrained when the admixture is used at the manufacturer’s recommended dose. |
| 4.2.6 | The grade of concrete is as follows, unless otherwise stated on the drawings. - Blinding – 15 MPa - General concrete work, plinths etc. – 35 MPa |
| 4.3 | Formwork |
| 4.3.1 | General |
| 4.3.1.5 | Earth cuts may be used as forms for vertical surfaces. |
| 4.3.1.6 | Approval of the authority controlling the service is required before the commencing the design of the formwork over the road/street/railway. |
| 4.3.1.8 | The formed surfaces are as follows: - Foundations (below 150 mm from finished floor level) – Rough finish is acceptable. - All concrete from 150 mm below finished floor level which receives and additional finish – Smooth finish is required - Off-shutter concrete (not receiving any further finishes) – Smooth special finish is required. |
| 4.3.1.8 | The degree of accuracy required is II. |
| 4.3.2 | Design and construction of formwork and false work |
| 4.3.2.1 | General |
| 4.3.2.1.4 | The design and drawings for the formwork and false work is submitted to the Project Manager for acceptance. |
| 4.3.8 | Removal of formwork |
| 4.3.8.3 | - Where the structure is constructed in stages, the false work and supporting formwork is removed as specified on the drawings and specifications |
| 4.4 | Reinforcement |
| 4.4.1 | Bending |
| 4.4.1.3 | Bars may not be hot bent |
| 4.4.2 | Fixing |
| 4.4.2.2 | Welding of bars is not permitted |
| 4.4.3 | Cover |
| 4.4.3.1 | The cover is shown on the drawings. |
| 4.5 | Holes, chases and fixing bolts |
| 4.5.1 | Fixtures to be embedded in the concrete are attached as shown on the drawings. |
| 4.6 | Embedded items |
| 4.6.2 | Waterstops |
| 4.6.2.1 | The type and location of waterstops are as specified on the drawings. |
| 4.7 | Quality of concrete |
| 4.7.3 | Workability |
| 4.7.3.2 | Pumping of concrete is permitted. |
| 4.7.4 | Chloride and sulphate content |
| 4.7.4.1 | Efflorescence on exposed concrete surfaces is not permitted |
| 4.7.5 | Durability |
| 4.7.5.1 | Concrete that has an air-dry density in the range 2000 kg/m3 to 2600 kg/m3 contains entrained air that conforms to the limits given in table 6. |
| 4.7.5.2 | Concrete made to have an air-dry density that does not exceed 2000 kg/m3 contains 6% ±2% or 7% ±2% total air. |
| 4.7.10 | Placing |
| 4.7.10.11 | Plums are not permitted. |
| 4.7.10.15 | Pumping of concrete is permitted. |
| 4.7.12 | Joints |
| 4.7.12.1 | Construction joints |
| 4.7.12.1.1 | Construction joints are required. |
| 4.7.12.1.4 | Proprietary bonding compounds between old and new concrete is permitted. |
| 4.7.12.4 | Sealing of joints |
| 4.7.12.4 | Joints are sealed as shown on the drawings. |
| 5 | Compliance with the requirements |
| 5.1 | Testing |
| 5.1.1 | General |
| 5.1.1.8 | The test for the percentage of alkali-aggregate are as per ASTM C289 – Potential reactivity of aggregate (chemical method) or alternative method accepted by the Supervisor. |
| 5.1.2 | Acceptance of strength concrete |
| 5.1.2.3 | The test results may be assessed statistically. |
| 5.2 | Tolerances |
| 5.2.1 | General |
| 5.2.1.1 | The degree of accuracy is III for surfaces cast against earth cuts and II for other concrete surfaces unless otherwise specified on the Drawings. |
| Variations |  |
| 4.2.2 | Replace 4.2.2 with the following: Water for mixing or curing concrete or mortar is sourced from potable water supply. |
| 4.7.6.1 | Replace clause 4.7.6.1 with the following: The Contractor designs the mixes which he proposes to use in the works to requirements including the requirements for strength, durability, hot and cold weather, and temperature control and curing of concrete. The Contractor conducts tests on trial mixes and based on the results of the tests on the trial mixes, the Contractor submits full details of his proposals for mix design to the Project Manager, including the type and source of each ingredient, the proposed proportions of each mix and the results of the tests on the trial mixes. If the Project Manager does not approve a proposed concrete mix for any reason, the Contractor amends his proposals and caries out further trial mixes. No mix is used in the works without the written acceptance of the Project Manager. Once acceptance by the Project Manager has been given for the use of a particular mix, the proportions of cement, aggregate, water and admixtures is not to be changed without prior acceptance of the Project Manager. |
| 4.7.8.2 | Add the following: Should “ready-mixed” concrete be used, the uninterrupted supply of the correct volume to Site should be guaranteed. |
| 4.6.3 | Add the following: The space between pipes and ducts that are to be cast into reinforced concrete and any adjacent reinforcement shall not be smaller than the larger of the following: 40mm, or, 5mm plus the maximum size of the coarse aggregate. |
| 4.7.8.2 | Add the following: The Project Manager may permit production of concrete at a central production facility other than on the Site of construction and reserves the right to inspect for acceptance of these central production facilities. The Contractor is responsible for conducting all control testing. |
| 4.7.10 | Add the following: Concrete may not be placed before the Supervisor’s acceptance has been given in writing a minimum notice period of 24 hours prior to pouring is required for each part of the structure. |
| 4.7.12.1.1 | Add the following: Joint positions are in accordance with the drawings or as accepted in writing by the Supervisor. |
| Additional Clauses |  |
| 1 | Where strength of concrete is specified it is designated by its specified strength followed by the size of stone used in its manufacture, e.g. 35 MPa/19mm |
| 2 | Cement and cement extenders are free flowing and free of lumps, and is supplied in the manufacturer's sealed unbroken bags or in bulk. Material that has become hardened or lumpy or fails to comply with the Works Information in any way is removed from the Site, without delay. |
| 3 | The materials used in the construction of falsework and formwork are suitable for the purpose for which they are required and is of such a quality that will produce the standard of work specified. The Contractor submits his proposal of the materials that is used for the construction of the falsework and formwork to the Project Manager 2 weeks prior to use for his acceptance. |

### SANS 2001 CS1: Structural steelwork

SANS 2001-CS1:2012	South African National Standard Construction Works Part CS1: Structural Steelwork

Specification data pertaining to SANS 2001-CC1: 2012 is as listed in the table below. The clause listed in the table below refers to the clause number in SANS 2001-CS1 and the table below must be read in conjunction with the code.

| Clause | Specification Data |
| --- | --- |
| 4.1 | Materials |
| 4.1.1 | The following clause is added: “All materials are new and as specified in this document and on the relevant drawings. All steelwork is manufactured using grade S355JR steel unless otherwise specified on the drawings. Where commercial steel is used for cold formed steel, the steel is to have a yield stress of 200 MPa and tensile strength of 365 MPa. Prior to fabrication of cold formed steel, test certificates, or cast analysis certificates or both, pertaining to the steel to be used is supplied to the Supervisor by the Contractor. In the event of any specified steel not being available, the Contractor notifies the Project Manager in writing. |
| 4.1.5 | All structural bolts and holding down bolts are of class 8.8 unless otherwise specified on the drawings. |
| 4.2 | Drawings |
| 4.2.1 | General |
| 4.2.1.3 | Format of drawings The clause is deleted and replaced with the following: “All drawings prepared by the Contractor are issued to the Project Manager for acceptance, in accordance with Section 3.3.1. |
| 4.2.4 | Fabrication drawings (shop detailing) |
| 4.2.4 | The following clause is added: “Fabrication drawings are prepared by the Contractor. The drawings are issued to the Project Manager for his acceptance in accordance Section 3.3.1, dwg). The Contractor may not commence with fabrication until written acceptance from the Project Manager is received.” |
| 4.2.4.2 | Attachments to facilitate erections may not remain as part of the permanent structure. |
| 4.2.4.4 | Hole sizes for holding-down bolts in excess of 36mm diameter are as follows: Are not greater than 40m |
| 4.2.4.7 | Connections to allow movements are as shown on the drawings. |
| 4.3 | Workmanship (General) |
| 4.3.6 | Holing |
| 4.3.6 | The following clause is added: “Flame cutting of holes is not permitted.” |
| 4.4 | Workmanship (Welding) |
| 4.4.4 | Assembly techniques |
| 4.4.4.3 | Tack welds are not to be incorporated into the final welds |
| 4.4.4.5 | Attachments to facilitate erection may not remain as part of the permanent structure. |
| 4.5 | Workmanship (Bolting) |
| 4.5.1.3 | The maximum protrusion beyond the nut will not be more than 10 mm |

| 4.5.1.4 | Washers under nuts and bolt heads on flat surfaces are required |
| --- | --- |
| 4.6 | Workmanship (Erection) |
| 4.6.2.1 | The pressure or loading permitted on the hard standing is determined by the Contractor and does not exceed the strength of the hardstanding. |
| 5.3 | Non-Destructive testing of welds (Welding) |
| 5.3.4 | Ultrasonic or radiographic examination is required for butt welds only. |
| 5.3.5 | Fillet welds are tested either with dye-penetration (DPI) or magnetic particle inspection (MPI). 50% of the welds are tested. The testing position is indicated by the Supervisor. Butt welds are tested either with DPI or MPI and by ultrasonic. |
| Variations |  |
| Cl 4.1.2 | The chemical composition and mechanical properties of all steel incorporated into structures is stated in the mill test certificates and submitted to the Project Manager for his acceptance. |
| Cl 5.2 | Add the following: Properly documented evidence of previous qualification of welders is acceptable. |
| Additional Clauses |  |
| 1 | All materials are new and as specified in this document and on the relevant drawings. |
| 2 | Material not listed in this specification or on the relevant drawings is not permitted. |
| 3 | In the event of any specified steel not being available, the Contractor will advise the Project Manager in writing. |
| 4.3.7 | Structures, composite units and bolted assemblies that comprise component parts are not subjected to excessive stresses during the assembly, fabrication, or erection process. |
| 4.3.8 | Any necessary straightening or forming is carried out by methods that neither weaken nor deface the material. |
| 4.4.3 | The Contractor submits for acceptance full details of his proposed welding procedures and the provisions of AWS apply to the acceptance thereof. Acceptance of the welding procedures does not relieve the Contractor of his responsibility for correct welding and for the minimising of distortion in the finished structure. |
| 4.4.1 | All main butt welds have complete penetration and wherever practicable are welded from both sides. The backs of the first run are suitably gouged out. |
| 4.4.6 | Welds showing any planar defects such as cracks, lack of fusion or penetration and excessive slag inclusions or porosity are cut out and rewelded. Under-cutting is not permitted. |
| 5.2 | Properly documented evidence of previous qualification of welders is acceptable. |
| 4.4.6 | The Supervisor is informed of the necessity for repair or rectification work before any attempt is made to carry out such repair. Acceptance is obtained prior to commencement of the work. |
| 4.4.6 | Weld repairs are made to the same procedure as for the original weld. All tests are repeated after the repair has been completed and reports on ultrasonic tests are marked to indicate that the report refers to a repaired weld. |
| 4.3 | All metalwork for metal stairways, ladders, walkways and platforms are galvanised. |
| 5.3.2 | Visual examination of all welds check that: - There are no uneven leg lengths and there is no cracking or unacceptable undercutting or porosity, and full fusion is being achieved while welding is in progress. |
| 5.3.1 | Where required and prior to fabrication, test certificates, or cast analysis certificates or both, pertaining to the steel to be used are supplied to the Supervisor by the Contractor. |

#### Specification SANS 1200 HA: steelwork (structural) sundry items

Specification data pertaining to SANS 1200-HA: 1990 is as listed in the table below. The clause listed in the table below refers to the clause number in SANS 1200-HA and the table below must be read in conjunction with the code.

| Clause | Specification data |
| --- | --- |
| Variations |  |
| Cl 5.1.2 | Add the following: The said shop details and other drawings are submitted in duplicate to the Project Manager for approval prior to fabrication. |
| Cl 5.1.2 | Add the following: One paper copy is returned to the Contractor with the Project Manager’s acceptance. |
| Cl 5.2.10 | Add the following: Where no corrosion protection system is specified, open grid flooring is hot dipped galvanised. |
| Cl 7.1 | Add the following: Test certificates and cast analysis certificates are supplied to the Project Manager by the Contractor. |

#### SANS 1200 HB: cladding and sheeting

Specification data pertaining to SANS 1200-HB: 1985 is as listed in the table below. The clause listed in the table below refers to the clause number in SANS 1200-HB and the table below must be read in conjunction with the code.

| Clause | Specification data |
| --- | --- |
| Variations |  |
| Cl 3.2.1 | Add the following: Galvanized steel sheeting is coated with a minimum of 275g zinc per m2 and is free from white rust. |
| Cl 5.1.4 | Add the following: The Contractor is solely responsible for ensuring that the materials and method of installation comply with the details set out on the Employer’s drawings. Any further modifications and additional details are to be accepted by Project Manager. |
| Additional Clauses |  |
| 1 | Where the use of nails and screws is required: - Galvanised iron nails and screws are used for galvanized sheet iron and sheet zinc. - Copper and copper alloy nails and screws are be used for sheet copper and sheet lead. - Aluminium alloy or stainless steel nails and screws are used for sheet aluminium. |
|  | Each qualified welder and weld operator are assigned a unique identifying number. This number is marked on the work in indelible crayon to establish the extent of welds performed by the welder to whom it is assigned. Any welder or weld operator whose work is subject to multiple rejections will be required to undergo a re-qualification test on the appropriate weld procedure. At the discretion of the Supervisor any welder or weld operator failing a re-qualification test may be disqualified from any further welding on the works. |

#### SANS 1200 HC: CORROSION PROTECTION OF STRUCTURAL STEEL

Specification data pertaining to SANS 1200-HC: 1988 is as listed in the table below. The clause listed in the table below refers to the clause number in SANS 1200-HC and the table below must be read in conjunction with the code.

| Clause | Specification data |
| --- | --- |
| Variations |  |
| Cl 5.3 | Add the following: All burrs and sharp areas are removed by: - Chamfering or - Ground to a smooth radius of at least 1mm. |
| Cl 5.4.1 | Add the following: The method of cleaning and preparing the substrate of steelwork prior to the application of the coating system is in accordance with the applicable provisions of SABS 064 and takes place at a location proposed by the Contractor and accepted by the Project Manager. |
| Cl 5.4.3.1. b) | Add the following: Dry abrasive blast cleaning: - Blast cleaning media will not be recycled. Wet abrasive blast cleaning - Wet abrasive blast cleaning is carried out as indicated on the drawings. |
| Cl 5.7 | Add the following: The coating system is hot-dip galvanising which is carried out in accordance with SANS 121:2011. |

## Mechanical engineering works

### Air and Water Piping

- All piping is categorised in accordance with SANS 347 “Categorisation and conformity assessment criteria for all pressure equipment”.

- Steel piping is hot dip galvanised in accordance with SANS 121 “Hot dip galvanised coatings on fabricated and steel articles – Specifications and test methods” unless otherwise specified in the Works Information.

- All air piping is sized such that the velocity of air does not exceed 9 m/s and it does not exceed the pressure drop of 2.5 to 50 kPa per 100 m of delivery pipe.

- All water delivery piping is sized such that the velocity of water does not exceed 2.5 m/s and it does not exceed the pressure drop of 5 to 50 kPa per 100 m. If a flow velocity is required to be above 2.5 m/s to prevent settling due to the deposition velocity of particles within the piping, a proposal is submitted to the Project Manager for acceptance.

- All water suction piping is sized such that the velocity of water does not exceed 1.5 to 2 m/s and it does not exceed the pressure drop of 5 to 25 kPa per 100 m.

#### Pipe Supports

All pipe supports are in accordance with ANSI/MSS SP-58-2009.

- All hanger and pipe support attachments are galvanised in accordance with SANS 121 “Hot dip galvanised coatings on fabricated and steel articles – Specifications and test methods”.

- Pipe clamps are preferred so that no welding is done due to pipes being hot dipped galvanised.

#### Air Flow meters

- All air flow meters are of the annubar type with isolation valves for maintenance purposes.

### Hopper Aeration System

#### Aeration air supply to ash hoppers and additional bunker aeration air blowers (Drawings 0.61/96061)

- Blowers are electrically driven and are air cooled.

- The blowers are fitted with the following

  - An acoustic hood.

  - Ducting from the exhaust heat outlet of the acoustic hood to the outside of the building including fans if necessary.

  - A silencer.

  - Pressure reducing valves

  - Inlet filter.

  - Soft starters.

  - Isolation vales.

  - Non-return valve.

- The Contractor’s design takes into account operational cycling between one (1) blower in operation and one (1) blower on standby.

- The blowers are supplied via a VSD to allow for different operation capacities.

##### Intake Piping

The intake piping for the blowers are taken from a clean location inside the hopper aeration blower house.

- The intake piping is sized to give a minimal pressure drop.

- The intake piping includes a silencer and the Contractor conducts a pipe stress analysis for hot and cold operation, deadweight and vibrational loads to optimise the spacing and the selection of pipe supports.

##### Intake Filter System

- A cartridge type air intake filter which can be easily and safely removed for replacement, are installed for the blowers.

- Differential pressure monitoring equipment across filter elements is provided by the Contractor with the alarm and maximum differential pressure indicated.

##### Discharge Piping (Drawings 0.61/96061)

- The discharge piping delivers aeration air to the respective unit.

- Discharge piping includes a safety relief valve, non-return valve and silencer immediately after the blowers.

- Isolation valves are provided upstream of measuring and monitoring devices to enable isolation such that maintenance can be performed on them while the discharge piping is pressurised.

- The Contractor conducts a pipe stress analysis for hot and cold operation, deadweight and vibrational loads to optimise the spacing and the selection of pipe supports.

- The Contractor ensures the discharge piping is lagged and insulated in accordance with 240-56247004 for safety and to prevent condensation of air inside the discharge piping.

- The discharge piping is fitted with:

  - A pressure transmitter.

  - A temperature transmitter.

  - A flow meter.

- Areas of the aeration piping are to be able to be isolated such that maintenance can be conducted while the aeration system is operational.

  - The air supply to each hopper is able to be isolated while the rest of the air piping remains in operation.

- Flow meters are installed to monitor the flow of air to areas of aeration air piping to allow for leaks and aeration pad failures to be detected.

- The air supply piping to each of the aeration pads is fitted with a non-return valve to ensure that there is no back flow into the air supply piping if there is a failure on an aeration pads.

- Each unitised hopper aeration system supplies air to the unitized precipitator (40) hoppers.

The piping for each unit is from the unitized blowers to each unit’s precipitator hoppers. Each hopper    aeration air supply to each aeration pad have pneumatic actuators which open and close the air supply to each hopper.

- The common aeration air blowers will supply aeration air to all the ash bunkers and 12 ash conditioners. There are three existing blowers, but the Contractor need to design, supply, install, tie-in the new fourth aeration air blower into the existing common discharge pipeline of the existing 3 aeration air blowers.

#### Aeration Air Heaters

- The Contractor supplies heaters to heat the aeration air supplied to the aeration pads.

  - The air heaters consist of multiple banks of heating elements which have the ability to operate independently such that the desired heating capacity is obtained.

  - The heaters are preferred to be located outside of the unitised blower houses.

- The design of the heater system ensures that the heater is distanced from the heater control panel and the control panel is located in a clean environment, e.g. control panel incorporated into the blowers’ control panel.

  - A junction box is located between the heaters and the control panel.

    - Silicon covered wires are used for the cables for the heaters to the junction boxes, normal cabling is used between the junction boxes and the control panel.

    - The silicon covered wiring is protected by a sheath (steel pipe or similar) which is sealed on both ends once installed.

- The design of the heaters and the insulation takes cognisance of all maintenance activities which are carried out on the works. In addition:

  - The heaters boxes are IP65 compliant.

  - The heaters are mounted above the floor level, on plinths.

#### Hopper and Bunker Aeration Pads

- Hopper and ash bunker aeration pad membranes are installed within a supportive casing that is designed to self-protect against foreign objects which may pass through the hoppers or bunkers and damage the membranes.

  - The aeration membranes are supported and protected from the top and bottom by means of a grating to minimise movement, wear, and extend the life of the membrane.

- Due consideration is taken for the aeration pad assembly such that when operating at design temperature no air leaks occur.

- A high temperature membrane fabric (up to 160°C for extended periods and up to 200°C for short periods) is used.

  - Fabric containing asbestos is not permitted.

### DHP (Drawings 0.61/96025, 0.61/96026)

#### General

The DHP is to be upgraded by using the existing En-Massa system technology. The following systems are not included and are not acceptable to the Employer:

- Low pressure, “dilute-type” systems which operate at high pipeline velocities with high air volume requirements.

- Single stage multi pressure vessel based pneumatic conveying system of the positive pressure type conveying simultaneously into a common conveying pipe.

- Vacuum type systems.

- Screw feeders and pneumatic pump type systems.

- Systems with sensitive air flow distribution and/or pressure regulation requirements.

- Air Activated Gravity Conveyors (AAGC) - (airslides), horizontal airslides (aeroslides) or Air Activated Gravity Conveyors.

- A conveying pipe system with a membrane type aeration chamber.

- Any below ground installations.

The upgraded DHP has the following capabilities:

- Each ash hopper has an emergency discharge equipment, so that ash can discharge on the floor..

- The first three row hoppers can discharge into any of the three transfer conveyor routes. In case if that related hopper conveyor is out of operation.

- The hopper conveyor top casing should be the same height from the first row hoppers up to the third row hoppers

- All Plant and Materials for the DHP are watertight such that no water can be introduced via the DHP into the ash bunkers.

- Minimises fugitive dust emissions.

- The dust handling plant must operate under vacuum conditions under normal and backlog mode of operations.

#### Ash conditioners

- The current ash conditioners required inside cleaning once a week to remove the hard ash build-ups from the conditioners inside casings. The new design should reduce the amount of conditioner cleaning and the new conditioners must have sufficient access doors for this ash conditioner cleaning and maintenance purposes. The access doors should be lockable and be part of the ash conditioner lock-out process, to prevent unauthorised conditioner internal access.

- These ash conditioners and scrubbers will use dirty water and this water corrodes the mild steel. Care should be taken when selecting the correct steel materials for these ash conditioners and scrubbers.  The conditioner access doors should be made from stainless steel, to prevent failure, if personal is standing on top of this ash conditioner.

- The ash conditioners and ash bunkers should use minimum aeration air and the bunker venting and dust handling plant venting design should take the bunker aeration air inflow and hoppers aeration air in consideration.

- The new ash conditioner water flow control system, should be such that the magnetic flow meter is always full of water, to minimise overheating and to insure accurate water flow measurements. The new water pipe systems and water nozzles should handle dirty water.

- The fly ash product flow control valve should have a close limit stop, to prevent this valve from over closing. (The valves passes it close position) The ash bunkers fly ash discharge equipment should make provision for future fly ash sales, by providing fly ash off-tapping points with manual isolating valves and flanges.

- The fly ash temperature from the ash bunker towards the ash conditioner is about 120 degree Celsius and vapour/steam is forming inside the ash conditioner, when this hot fly ash is mixed with cold water. The new scrubbers should be able to handle this vapour/steam.

- Minimal dust particles in the surroundings of the ash conditioners and minimal ash settlements at the boiler house as per EVP 083 Rev 0.

- All isolating and control valves on the ash conditioners and scrubber systems should use spring to close pneumatic actuators, except for the fly ash product flow control valve, where it uses pneumatic cylinder.

- Easy access towards the ash conditioners and scrubbers.

- The water nozzles inside the ash conditioners should handle effluent water and these nozzles should be easy accessible for cleaning.

#### Ash bunker blowers

- There are three aeration air blowers for the ash conditioners and the contractor is to design, select, supply, install, test and commission a fourth blower which will tie-into the existing blowers aeration air common discharge pipe line. All blowers should be air-cooled and be equipped with air pressure reducing valve in case of pipe blockages.

- The new aeration air blowers for the ash conditioners and ash bunkers should have self-cleaning air filters by using moisture free control air.

- The aeration air blowers should have pressure relief system via silencers into the atmosphere, in case if there is a discharge pipe blockage.

#### Ash conditioning water supply

- The effluent pumps must handle dirty water and this dirty water has slurry inside the water.

- The effluent pumps should be direct drive.

- All piping should be HDPE piping and the pressure rating should be 16 bar.

- All water valves should have flanges on both ends and must be lockable and must be able to handle effluent water.

### Instrument Air System (Drawings 0.61/96027 Sheets 1 – 6, 0.61/96028 Sheets 1 – 3, 0.61/97205)

#### Compressors

- All compressors are electrically driven.

- Compressors types are either screw or centrifugal and are selected according to their best efficiency.

- Compressors are of an oil free type.

- Each compressor is fitted with a soft starter to minimise starting current.

- The inlet filter together with the intake piping for each compressor is situated inside the common DHP compressor house.

- All compressors are supplied with a dedicated vibration damping mounting devices to prevent the transfer of vibrations from the compressor to the foundation.

- Each conveying air compressor has a dedicated:

  - Inlet filter.

  - Silencer.

  - Non-return valve.

  - Discharge isolating valve.

  - Blow off valve.

  - Flow monitoring device.

  - Lubrication system.

  - Inter-stage - and after coolers.

  - Air dryers.

  - Pre and post air dryer filters.

##### Instrument Air Compressors

- The Contractor provides a separate instrument air system and ensures that it is adequately sized to provide the works with the required quantity of instrument air at the desired pressure.

- The Contractors design takes into account operational cycling of the instrument air compressors.

#### Intake Piping

- The intake piping for each instrument air compressors are taken from a clean point inside the common  DHP compressor house and are sized to minimise pressure drop.

- Intake piping is hot dip galvanised.

- The Contractor conducts a pipe stress analysis for hot and cold operation, deadweight and vibrational loads to optimise the spacing and the selection of pipe supports.

- The intake piping contains as a minimum, pressure, temperature and flow transmitters for condition monitoring.

#### Intake Filter System

- A cartridge type air intake filter which can be easily and safely removed for operation and maintenance is fitted for both conveying and instrument air compressors.

- Differential pressure monitoring equipment across filter elements are provided by the Contractor with the alarm and maximum differential pressure indicated.

#### Discharge Piping

- The discharge piping delivers instrument air to the respective unit.

- Each unit has a dedicated instrument air pipe.

  - Instrument air:

    - All instrument air compressors are able to supply air to any unit.

    - All instrument air compressors are able to supply air through any of the instrument air receivers.

- Discharge piping includes immediately after the compressors a:

  - Safety relief valve.

  - Non-return valve.

  - Blow off valve including silencer (directed out of the building).

  - Shut off valve.

- Isolation valves are provided in conjunction with measuring and monitoring devices to enable isolation of these devices such that maintenance can be performed on them while the piping is pressurised.

- The Contractor conducts a pipe stress analysis for hot and cold operation, deadweight and vibrational loads to optimise the spacing and the selection of pipe supports.

- The discharge piping includes a pressure transmitter and a pressure indicator for pressure monitoring, and a drain valve to release the pressure when performing maintenance.

- The Contractor ensures the discharge piping is lagged and insulated in accordance with 240-56247004 for safety and to prevent condensation of air inside the discharge piping.

#### Air Receivers

- All air receivers are designed and constructed in accordance with the latest revision of ASME BPVC “Boiler and Pressure Vessel Code” and categorised in accordance with SANS 347 “Categorisation and conformity assessment criteria for all pressure equipment”.

  - Each air receiver is sufficiently protected from harsh weather conditions and has its own dedicated.

    - Automatic condensate drains.

    - Designated safety valves.

    - Pressure relief valves.

    - Drain valves.

    - Pressure indicators and transmitters.

    - Manhole.

#### Air Dryers

- Heat of compression, twin tower desiccant air dryers are preferred.

- The air dryers dry air to a pressure dew point of -30 to -40 °C.

- Each desiccant air dryer is provided with a :

  - Coalescent type pre-filter and post-filter assemblies.

    - Filters have differential pressure transmitters to inform the plant operator when the filter needs to be cleaned/purged as well as automatic drain valves enabling automatic blow down

  - Pressure transmitters.

  - Pressure gauges.

  - Safety relief valves.

- Each air dryer contains dew point measurement to indicate the dryness of air.

- The air dryer towers are designed and constructed in accordance with the latest revision of ASME BPVC “Boiler and Pressure Vessel Code” and categorised in accordance with SANS 347 “Categorisation and conformity assessment criteria for all pressure equipment”.

#### Cooling System (0.61/2, 21.61/55309, 21.61/54505, 0.61/96027 Sheet 6)

- The cooling towers contain a forced draught fan with a spray water pump in an open circuit which sprays water over the closed circuit heat exchanger.

- The Contractor provides closed circuit towers which circulates demineralised water with corrosion inhibitors through the compressors and air dryers.

- Each cooling tower has automatic valves on their discharge to switch between towers on standby and towers in operation.

- The cooling towers have instruments for pond level control and detection, and to control the concentration of salts inside the tower.

- Temperature transmitters are present on the outlet of the towers to monitor the performance of the towers and for trip/ alarm purposes.

- The Contractor provides and commissions flow transmitters to the inlet and the outlet of the cooling system for monitoring and leakage detection, as well as interfacing to the DCS.

- The cooling system receives demineralised water from the high pressure demineralised water manifold at the water treatment plant [LOSS-EE-08-02]

- A one (1) cubic meter make-up galvanised steel head tank is supplied for the closed circuit demineralised water supply to serve as a buffer in the event of leaks occurs. The water in the tank is circulated using the closed circuit pumps and is not left standing in the tank. The tank has level instrumentation for alarms and monitoring along with an overflow and a drain line.

- The cooling system receives potable water make up supply from unit 6 emergency potable water head tank. [LOSS-EE-08-03]

- The blow down for the cooling water system is sent to the storm water drains [LOSS-06-08-05]

- The cooling system open circuit has an automatic dosing system and doses into the cooling tower pond

- The cooling system closed circuit has a dosing system and is dosed directly into the make-up head tank.

- Each closed circuit cooling water pump has isolating and non-return valves, and instruments for pump protection/ trips.

### Conditioning Plant (Drawings 0.61/96075, 0.61/96078, 21.61 55242 Rev. 3)

#### Conditioner Feed System

- The Contractor takes cognisance of the range of bulk densities as specified in 3.4.2 of dry fly ash when specifying the ash flow control device.

- The conditioner feed system physically constrains the maximum flow of material (not through the control system or a flow control valve) such that the conditioner capacity cannot exceed 200 Tph (wet at 20% moisture content)

- Between the bunker outlet and the conditioner the following is installed in the following order starting at the ash bunker outlet:

  - A manual operated isolation slide gate.

  - An actuated slide gate.

  - A drop box.

  - An actuated flow control valve.

  - An Air Activated Gravity Conveyor (AAGC) (according to specification in section 6.2.5.2).

    - The air required for the air slides is supplied by the ash bunker aeration system blowers.

  - A motorised double flap valve.

  - A manually operated isolation slide gate.

- No moisture or air is to enter the ash bunker via the ash feed system to the conditioner.

  - Any system that permits reverse-flow of moist air to the ash bunker is not accepted.

- The system utilised to feed ash from the ash bunkers to the conditioner is designed to prevent flooding of the conditioners.

  - Notwithstanding this requirement, the Contractor takes the necessary precautions to ensure that in the event of flooding, no damage is cause to the Plant and Materials e.g. ash ingress into shaft seals, damage to conditioner paddles, etc.

- Where necessary, Plant and Materials are adequately lagged to ensure that the fly ash is maintained above the dew point temperature.

- The actuated flanged butterfly valve is a quick-acting cut off butterfly valve.

  - The closing time from fully open to fully closed is less than five (2) seconds and visa-versa.

  - The valve is to be pneumatically actuated and is to fail closed if there is a loss in instrument air.

- The ash flow control device is installed to control the flow of ash to the conditioners.

  - The ash flow control device is not used for isolation purposes.

  - If a V-notch type gate valve is used as the ash flow device, the Contractor specifies and guarantees the working life of the gate, body spindle and actuator.

    - The working life of the gate, body spindle and actuator is in excess of five (5) years.

    - The V – notch type gate valve to have a close stop device, to prevent this valve from passing its close limits.

- A manually operated knife gate valve is installed at the inlet to each of the conditioners.

  - When closed this valve isolates the conditioner from the system utilised to feed ash from the ash bunkers to the conditioner, this prevents any ash vapour from entering the feed system.

  - Care is taken when designing this valve to ensure that the runners do not block with ash.

- Between the manually operated knife gate and the airslide (AAGC) a motorised double flap valve is installed.

  - The double flap valve ensures that no air or moisture enters the dry ash feed system to the conditioners.

- A system is proposed if the Contractor wishes, which allows the actual flow of dry ash to each conditioner to be monitored.

  - The information received with regards to the actual flow of dry ash to the conditioner is used to control the dry ash throughput and moisture content of the product to the parameters specified.

  - The proposal for the system is submitted to the Project Manager for acceptance.

#### Air Activated Gravity Conveyors – Airslides

- The minimum angle of any Air Activated Gravity Conveyors (AAGCs) is 7°.

- The feed of material into the AAGC is at an angle.

- The AAGC membrane fabric is protected top (impact zones) and bottom by means of a grating so as to prevent abrasion of the fabric and to protect the fabric.

- The AAGC membrane fabric used is able to operate continuously at 160°C and is capable of operating for short periods of temperatures peak occurring in the system of up to 200°C, a high temperature (higher than 250°C) fabric is not permitted.

  - Asbestos containing fabric is not permitted.

- The casings of the AAGCs are manufactured as interchangeable sections. Each casing is provided with:

  - Handles to manipulate/align the sections during maintenance.

  - Lifting lugs.

  - Hinged inspection hatches.

  - One (1) pair of inspection windows, the locations of these windows are indicated on the drawings.

- The casing top, sides and base have a minimum wall thickness of 4 mm.

- The Contractor identifies the high wear areas in the AAGCs and explains what precautions have been taken to minimise wear in these areas.

- Provision is made to detect dust and to facilitate cleaning of the area beneath the fabric membranes in the case where ash passes through the fabric due to a damaged or worn membrane.

- The system design ensures that under no circumstances is fly ash allowed to remain in the AAGCs casings after a trip, where the dust can cool down.

- The AAGC aeration air is supplied from the hopper aeration blowers for the units on either side of the specific ash bunker that the AAGC is situated within.

- The air is distributed to the AAGC segments by a series of manual (lockable) throttle valves, these valves are set at commissioning.

#### Conditioners

- The conditioners are required to produce a consistent (in time and across the conditioner width) homogeneous mix of dry fly ash and water, for all ash quantities and moisture settings.

  - For this reason the Contractor checks that the design ensures adequate conditioner length, blade pitch, speed of rotation and ash retention time.

- The conditioners are of the contra-rotational type.

- Square type paddle shafts are preferred.

- A deflector plate suspended from the top cover of the conditioner near the conditioner inlet is fitted which directs the flow of ash downward into the first, work-agitated, zone in the trough.

- A second deflector plate is fitted at the discharge end of the conditioner trough to prevent material being compressed into, and wearing the end plate.

- Conditioning water is evenly distributed evenly over the ash, throughout the conditioner, as the ash is agitated and transported along the central portion of the trough.

- Short lengths of continuous worm-type paddles are fitted to the paddle shafts at the ash feed end.

  - These provide positive conveying of the ash into the first agitating zone where most of the conditioning water is added.

- The conditioners and associated plant is designed to facilitate quick removal and replacement utilising the Plant and Materials for lifting within the conditioning plant only.

  - Removal and installation of a new conditioner is to take no longer than four (4) days.

  - The Conditioning System is designed as a module with quick release couplings, compensators and is mounted on a common base plate.

  - Layout and connections of all piping, ducting etc. serving the conditioners is neatly arranged so as to facilitate easy removal of the complete conditioners with minimal disturbance to or removal of associated plant.

  - All shaft to shaft connections are easily removable, no hollow shaft connections are accepted.

- The drive unit for the conditioner consists of the electric drive, gearbox as well as the bull gears.

  - The drive unit is positioned on the side of the conditioner where the conditioned ash exits the conditioner.

  - If the drive unit is fitted with a support member to support the weight of the drive, then this support member has the capability of a minimum of two (2) degrees of freedom to minimise loads transmitted due to misalignment of the drive.

- The gearbox is shaft (flange) mounted and, together with the motor, fixed to a common base frame.

- The drive arrangement is sized to enable a fully loaded conditioner to be started up after a 30 min. standing time, for example after a power failure.

- Removable wear liners are fitted to each conditioner.

  - Care is taken to prevent corrosion occurring between the liners and the conditioner outer walls, the Contractor states how such corrosion is prevented.

  - The liners are a minimum of 6 mm thick throughout (including the exit/discharge chute areas).

    - Stainless steel (3CR12) liners are preferred.

- Hinged inspection doors are provided on the top of each conditioner to facilitate inspections, maintenance, cleaning, etc.

  - In addition smaller inspections hatches are provided to prevent injury and system trips.

- The Contractor ensures that the conditioners discharge centrally onto the conditioner conveyor belts to prevent any belt misalignment and that the ash stream does not touch the walls of the conditioner discharge chute.

  - To achieve this the Contractor can (but is not limited to):

    - Allow for alignment of the conditioner.

    - Take due consideration of the paddle configuration.

    - Review conditioner discharge chute design.

  - The use of defection mechanism in the discharge chute is not allowed

#### Conditioning Shaft Paddles

- The conditioning paddles are attached to the shaft in the simplest way possible.

  - Bolts with threads and nuts, which are easily damaged (caked in ash) and are therefore difficult to remove, are to be avoided.

  - Clamp type connectors, where the paddles are connected to a clamp which is clamped to the conditioners shafts are preferred.

  - The conditioner paddles are to be easily replaceable with the shafts in situ.

- Steel paddles with the curved section of the paddle covered with tungsten welded tips are preferred.

  - Tests conducted with UHMWPE paddles showed that they did not achieve an acceptable life.

- The Contractor states and guarantees the life expectancy of the paddles, a life of 3 years or greater is required.

- The Contractor specifies the method of attachment of the wear resistant material to the paddles, and guarantees the method of attachment for the duration of the wear life.

- One (1) or more paddles with reverse pitch are located at the discharge end of the shafts to prevent the ash mixture from building up on the end plate of the conditioner.

#### Bull gears

- Bull gears are used to synchronise the paddles shafts.

  - These gears are oil bath lubricated and are completely enclosed.

  - The oil baths have an oil level indicated/site glasses clearly showing the level of the oil.

  - Particular attention needs to be placed on the shaft seals for the oil bath, adequate sealing is required to prevent oil leaks.

#### Shaft Seals

- Where the conditioner paddle shafts pass through the conditioner casings, adequate sealing is provided to prevent any ash and grease leakages from the conditioners.

  - Preferred shaft seals are of either horizontal or vertical split labyrinth design.

- Deflector plates are installed inside the conditioners to deflect ash away from the seals.

#### Bearings

- The main bearings supporting the shafts are of a split roller bearing type.

  - The conditioners are designed such that the paddle shafts complete with paddles, can be lifted out of the conditioners for refurbishment.

- All bearings are designed for an L10 life of 50 000 operating hours.

- The plummer blocks are protected against an ash environment.

- The distance between the shaft seals and the plummer blocks is maximised to minimise the possibility of contamination entering the plummer blocks if there is a leakage or catastrophic failure of the shaft seals.

  - A physical barrier is installed between the shaft seals and the plummer blocks.

- Grease is to be fed continuously to the shaft seals and bearing plummer blocks by an automatic centralised grease distribution system.

#### Isolation of Vibration

- The Contractor takes every care to reduce vibration to a minimum.

- Anti-vibration mountings and isolators/compensators are provided to prevent any vibrations being transferred to the conditioning floor and all ducting etc. serving the conditioners.

#### Water Spray System

- Sizing of the nozzles is based on the water quality shown in section 3.4.3.

  - For poor water quality, nozzles are sized accordingly to minimise the chance of nozzles getting blocked by either particles carried in the water or by scale build resulting from calcium deposits, etc.

- Damp ash tends to cake and harden up on non-working nozzles and this ash sets hard and will hence impede water flow upon return to normal operation.

  - For this reason the installation/removal of nozzles is a task that is easily accomplished when inspection or cleaning is required.

#### Ash Vapour Scrubbers

- Each conditioner is equipped with a dedicated ash vapour scrubbing facility, which continuously extracts dust and water vapour arising from the conditioning process.

- The ash vapour scrubber consists of multiple stages.

- The ash vapour scrubber materials of construction take the following into consideration:

  - The scale build-up properties of the ash.

  - Corrosion resistance.

  - Polypropylene is an acceptable material.

- The ash vapour scrubber unit fits within the existing conditioning plant area and is mounted on a common base plate with the conditioner.

- The “clean” air discharge from the ash vapour scrubber is discharged to atmosphere (outside of the conditioning plant area) via a short stack.

  - The “dirty” water draining from the ash vapour scrubber unit is gravitated back to the conditioner to form part of the conditioning water addition.

- Potable water and effluent water (with the same quality as the conditioning water) supplies are available for the ash vapour scrubber units.

  - The quality of water is considered when selecting nozzle sizes and material.

  - The ash vapour scrubber unit are designed to minimise the use of potable water.

- No ash vapour scrubbers which utilises a cartridge type filters which require frequent cleaning are accepted.

#### Conditioner Discharge Chutes

- Negative angle chutes are considered.

- Chutes have a minimum of two (2) inspection ports.

- If modifications are required to the Dust Cover for the installation of online moisture analyser, the modifications made do not negatively affect the operation of the Dust Cover.

#### Conditioning Plant Crawl Beams

- The new crawl beams are able to lift a conditioner that is full of conditioned ash with a moisture content of 20%.

- The ash bunker structure is assessed to confirm the impact on the structure.

- Crawl beams are able to lift and lower a conditioner without assistance from other lifting equipment (e.g. mobile crane supporting the conditioner).

#### Conditioning Water Supply

- Conditioning water supply pumps are electrically driven.

- The branch of the conditioner water supply system to each conditioner is designed such that it constrains the maximum flow of water (not through the control system or a flow control valve) to each conditioner such that the flow cannot exceed the quantity required for the conditioner to operate at 200 Tph (wet at 20% moisture content)

##### Piping

- The material of construction is of HDPE and only flanged bends or fittings are allowed, no segmented bends or fittings are allowed.

- The conditioning water supply system is a recirculation system.

  - The piping is suitably sized to prevent any undissolved solids settling within the conditioning water supply piping.

  - There is a dedicated conditioning water supply pipe for each ash bunker and a common return pipe.

  - The Contractor provides a self-cleaning reverse flow strainer in the discharge line to filter undissolved solids from the ash conditioning water.

  - A suitable actuated valve is fitted in close proximity to the discharge of the return pipe to regulate back pressure.

  - The return pipe is fitted with a hydrostatic screen which filters the water to exclude solid particulate before the water is returned to the effluent sump.

- The piping to each ash conditioner is equipped with flow controllers and meters to ensure that the correct quantity of water is supplied to each conditioner.

#### Online Moisture Analysers

- The online moisture analyser utilises microwaves to determine the moisture content of the ash.

- The online moisture analysers are able to operate in dusty (which is generally moist) environment.

  - There can potentially be a build-up of a moist ash layer on the transmitter or receiver.

- The instrument has:

  - An accuracy of 0.3% or greater at one (1) standard deviation and an ultimate achievable accuracy of 0.1% or greater.

  - Can operate in an environment of 0 – 95% relative humidity (not condensing)

- The instrument is IP65 rated.

#### Belt Mass Meter

- Belt mass meters have a measuring accuracy of less than ±5%.

- The belt mass meters are able to operate with the configuration and troughing angle of the existing conveyor idlers without significant modifications.

### Valves

Each valve has a serial number stamped on the body of the valve.  A unique identification number (AKZ) is provided at the valve, clearly identifying the valve.

All valves unless otherwise specified in the Works Information have a minimum operating life of 10 years.

The Contractor supplies the following test certificates:

- Material certificate

- Pressure test certificate

- Leak test certificate

- Test methods used are stated on the certificates.

- Table 23 below lists valves that the Contractor uses for the piping containing compressed air.

Table 23 Valve Types

| Up to 50 mm NB |  |  |  |
| --- | --- | --- | --- |
| System | Valve type | Material | Ends |
| Instrument air | Ball | Stainless steel | Screwed/Threaded |
|  | Butterfly | Stainless steel | Wafer/ Flanged |
| Fire protection | Gate | Cast iron | Screwed/Threaded |
| Auxiliary cooling | Butterfly | Stainless steel | Wafer/ Flanged |
| Closed circuit demineralised water compressor cooling | Butterfly | Stainless steel | Wafer/ Flanged |
| Above 50 to 150 mm NB |  |  |  |
| System | Valve type | Material | Ends |
| Instrument air | Ball | Stainless steel | Flanged |
|  | Butterfly | Stainless steel | Wafer/ Flanged |
| Fire protection | Gate | Cast iron | Flanged |
| Auxiliary cooling | Butterfly | Stainless steel | Wafer/ Flanged |
| Closed circuit demineralised water compressor cooling | Butterfly | Stainless steel | Wafer/ Flanged |
| Above 150 mm NB |  |  |  |
| System | Valve type | Material | Ends |
| Instrument air | Ball | Stainless steel | Flanged |
|  | Butterfly | Stainless steel | Flanged |
| Fire protection | Gate | Cast iron | Flanged |
| Auxiliary cooling | Butterfly | Stainless steel | Flanged |
| Closed circuit demineralised water compressor cooling | Butterfly | Stainless steel | Flanged |

### Fire Protection and Detection

The Contractor is to provide and fit the buildings with early warning smoke detection and emergency evacuation alarm systems where applicable, according to SANS 10400, SANS 10139, NFPA 850 and applicable regulatory requirements. Fire protection system design complies with Eskom Standard 240-54937450, “Fire Protection & Life Safety Design Standard”, 240-54937439, “Fire Protection/Detection Assessment Standard” , 240-56737448, “Fire Detection and Life Safety Design Standard”, and 240-56737654, “Inspection Testing and Maintenance of Fire Detection Standard”.

Specific information:

- Switchgear room housing the main switchgear and control panels are separated from all the other adjoining areas with a 2-hour firewall.

- HVAC room houses HVAC equipment and electronic control equipment are separated from all the other adjoining areas with a 2-hour firewall, including switchgear room

Buildings include the following features, to aid/add to the fire safety of the occupants and buildings:

- The site has a pumped fire water main with well-placed fire hydrants close to the substation buildings, all site hydrants give adequate coverage in order to cater for the expected fire load.

- Passive fire protection measures in order to ensure occupant safety.

- Smoke ventilation from the main switchgear room.

- Approved emergency locking devices fitted to escape doors, and

- Safe escape routes out of the building.

#### Locking Devices

All locking devices fitted to all doors forming part of the escape routes are of the type approved by the fire department. Exit doors are fitted with approved thumb turn devices.

#### Marking and Signposting

Emergency Signposting consisting of adequate SABS approved symbolic safety signs are provided in accordance with SANS 1186, in order to instruct and indicate the location of:

- All escape routes

- Fire hydrants

- Hose reels and

- Fire extinguishers

Signage is also erected on exterior escape doors with the words “Fire Exit – Keep Clear” on the exterior of the building. Illuminated signs, which are provided at all exits, intended to be used in an emergency situation and all escape routes, are so illuminated that they indicate the escape routes unambiguously.

#### Service Shafts

All cable penetrations through the floor slab are sealed off on floor penetrations or in firewall penetrations with either fire retardant plugs or seals.

Firewall penetrations for ventilation are as small as possible and are protected to maintain the required rating of the wall by the installation of fire dampers, or in the case of small penetrations by intumescent bands or covering. Floor coverings, wall finishing and ceilings are classified as non-combustible material.

#### Smoke Control

According to Section TT42.1 of SANS 10400 any room with a floor area greater than 500 m2 is fitted with a form of smoke ventilation system.

#### Access to Fire Fighting Equipment

All fire fighting equipment; fire hydrants, fire extinguishers and other equipment; is easily accessible without any obstruction. Adequate access is also available to emergency service personnel and their equipment.

#### Fire Fighting Equipment

- Fire Extinguishers

Adequate numbers of fire extinguishers of the appropriate type and size, in accordance with SANS 10400, are provided throughout buildings for use by occupants in controlling and extinguishing small fire and to prevent large conflagrations. The extinguishers are laid out according to regulations within the SANS 10105 code of practice which specifies a maximum distance of 23 m between any point in the building and the closest fire extinguisher.

- Hose Reels

According to SANS 10400, hose reels for the purposes of fire fighting are installed in any building of two (2) or more storeys in height or in any single-storey building of more than 250 m2 in floor area at a rate of 1 hose reel for every 500 m2 or part thereof of floor area of any storey: Provided that such hose reels are not required in any building classified H4 or in any dwelling unit in occupancy classified H3 where such unit is provided with independent access to ground level. Hose reels may be replaced with fire extinguishers if in accordance with SANS 10400.

- Fire Hydrants

Fire hydrants are located close enough to the building to reach it with a hose length of less than 60m. Existing fire hydrants may be re-used. The Contractor reviews if the current installation satisfies this requirement. If not Contractor installs additional fire hydrants from the existing fire main system.

- Deluge Systems

Automatic water spray (deluge) is used for fire protection of the oil-filled transformers. The system employs dry pilot type heat detectors. The detectors are mounted in a pressurized air-line which is piped from the pressurized upper chamber in the deluge control valve to the detector. The piping from the deluge valve to the open spray nozzles is empty until one of the detectors senses excessive heat. When the detectors are tripped, they release the pressurized air in the line from the detector to the deluge control valve. This allows the deluge valve to open and flood the area via the interconnecting piping and spray nozzles. Deluge spray nozzles are open at all times.

### HVAC

- The Contractor makes provisions for a dirty/blocked filter alarm to be interfaced with the HVAC DCS.

- Heating is supplied via the heat pump. Where ambient temperature is too low for operation of the heat pump the method of LP protection is introduced (i.e. a hot-gas bypass or preheating of air entering evaporator).

- The minimum filtration efficiency complies with MERV-9 as defined in ASHRAE 52.2-2007.

- The system is equipped with a flow monitoring device to indicate when the filters are blocked or      the fan unit has failed.

- Concrete plinths for Plant and Materials within the HVAC systems are provided with a steel base frame and the floor sloping to prevent water flooding

- The supply and extract air units are positioned external to the substation buildings to withstand the      prevailing conditions at Tutuka P.S. The supply unit is ducted to supply conditioned air to the substation.

- The system is supplied complete with the following:

  - R410A or equivalent refrigerant gas

  - Advanced control board

  - ON/OFF scroll compressor

  - EC plug fans

  - Condensing fan speed control  (HP control)

  - Areolating rubber feet

  - Dehumidification control

  - Compressor anti-short cycle

  - Air flow switch

  - Dirty filter alarm

  - Evaporate leaving temperature control

  - Low ambient protection

  - G3 & F9 filters

  - Phase sequence relay

  - Free-cooling

#### HVAC General

The minimum general Plant and Materials design criterion that is to be met is as follows:

- The Plant and Material is designed to facilitate efficient manufacture, inspection, transportation, installation, maintenance, cleaning and repairs.

- The Plant and Materials are designed to prevent undue stresses being produced by expansion and contraction due to temperature change and other local natural and manmade conditions.

- The Plant and Materials are designed such that all material from which the Plant and Materials are manufactured from is compatible with the intended duty and service conditions. All Plant and Materials are suitable treated and protected from corrosion.

#### DX Air Conditioning units

The unit is provided with the following as a minimum:

- An ON/OFF facility with the ability to select full air conditioning and fan operation only.

- A fan speed selector with a HIGH/MEDIUM/LOW setting.

The controls are clearly marked and easy to operate.

The unit is provided with an adjustable temperature controller with an adjusting range of 20-25ºC. The sensitivity of this temperature controller are such that it controls in a differential band of 2°C (adjustable 1 to 4°C, factory set at 2°C), 1°C on either side of the set points. The temperature controller is clearly marked in which way to adjust the room temperature.  The temperature controller switches on the heater or compressor automatically in accordance with the load.

Install the control facilities within a suitable draw box recessed into the wall/partition, with the control cable reticulated within an enclosed conduit.

##### Operating range

Fan delivery does not decrease more than 10% when filters are dirty and the operation point is on the stable part of the curve.

Units operate continuously without damage or malfunction for the following range of conditions at local altitude:

- Condensing Unit:	Entering Air Temperature :  0°C - 52°C

A “low ambient” condensing control is incorporated in the unit if specified as such in the schedule.

Safety protection is provided for the fan motors as follows, unless otherwise specified:

- Single phase motors: 	Thermal overload protection.

- Three phase motors:	Combined thermal overload and phase failure protection.

Fan motors are non-overloading at any operating point of their performance curves.

Both indoor and outdoor units are fully protected and to fail safe. Minimum safety protection, caused by possible external abnormal conditions is provided for the following, and requires manual or automatic reset after fault occurrence:

- High discharge pressure.

- Low Suction pressure/anti-freeze protection.

- Crankcase heater.

- Thermal overload protection for all motors.

- Current overload protection on compressor.

- Re-starting time delay for compressor.

- Auto re-starts on power supply interruption.

##### Technical restraints

The unit coils are provided with the following minimum requirements:

- The AHU coil is aluminium fins mechanically bonded to seamless copper tubes. The fin spacing is greater than 2 mm. Ensure no "water carry over" during any operation condition.

- The outdoor coils are hail-proof.

- Coil and refrigerant piping is protected from freezing in ambient temperatures down to -15°C.

Heating to be provided by a reverse cycle "heat pump feature" if specified as such in the schedule

Compressors are either semi-hermetic, suitable for field servicing or hermetically sealed.

The unit’s electric heaters have the following minimum requirements:

- Manual reset thermal cut-out device set between 60 – 80°C with reset button, labelled and operable without removing any terminal box cover.

- Elements to have an adequate resistance to earth, with due regard to the possible condensation of moisture during the cooling cycle.

The refrigerant piping system is provided with the following minimum requirements:

- Refrigerant pipe sizing calculations are submitted where the length exceeds 15 m.

- The necessary traps are installed in the refrigerant lines to ensure oil return for applications where the outdoor unit is installed higher than indoor unit.

- Flare connections are to be used at the indoor and outdoor unit.

- Three (3) way valves with service port are installed at the outdoor unit for connection of standard refrigerant pressure gauges.

- Fit a filter in the liquid line with a sight glass and moisture indication thereafter.

- Provide facilities for charging the units with refrigerant and measuring the refrigerant pressures of the unit using standard refrigerant gauges.

- Units which are not pre-charged are evacuated to a vacuum of not less than 4 mm Hg before charging.

- The insulation for the refrigerant piping is of the "ultra-violet resistant" type. Insulation exposed to outside weather is finished off with ultra-violet resistant plastic tape or paint.

Drainage of condensate from the units is collected by the following means:

- A pan of sufficient size to catch all condensate which may emanate from the unit.

- Drainage via gravity feed from this pan to a suitable connection; or booster pump assisted drainage where indicated on the relevant drawings or in the accompanying schedule.

  - The drain pan is fabricated from galvanised sheet steel and painted internally to prevent condensation on the external surface.

- Drain piping is fixed and routed to the nearest suitable drain point to ensure positive drainage.

- Drain piping is resistant or protected against weather elements or people traffic.

The electrics and controls have the following minimum requirements:

- All electrically powered elements within the unit have an adequate resistance to earth, with due regard to the possible condensation of moisture and comply with statutory requirements.

- Interconnecting wiring from the outdoor unit to the indoor unit is via conduits or suitable special cable.

- Power supply from the local isolator is protected against the elements by means of conduit or suitable cable.

- Confirm adequacy of the power supply at Plant and Materials submission stage.

- A manual override facility is provided on the indoor unit if a remote wireless temperature/control unit is offered.

##### Installation restraints

Install units in accordance with manufacturer's recommendations and be capable of being fitted into the spaces indicated.

The unit does not drum, vibrate or leak under any operating conditions. Noise level in the conditioned space through the operation of the unit at any operation point is not to exceed NC 40 with an 8 dBA room attenuation factor in each octave band.

All penetrations through building structures are sealed against ingress of water and air.

All piping/conduits/wiring/supports are neatly and securely fixed to the building structure. Method of fixing is submitted to Project Manager prior to installation.

##### Measurement to confirm Plant and Materials compliance with specification

Contractor submits with the tender, certified performance date sheets for capacity and power consumption at either AREO conditions or local conditions by the SABS or a similar organisation.

Performance is based on the actual mounting details and location where installed.

Performance testing of each unit is done in a certified "on line" test facility. The minimum tests include compressor running amps, entering and leaving temperatures, a leak test, the heater amperage, all controls for function and calibration of thermostat. All results are properly recorded against the serial number of the unit and signed off by the responsible person for quality.

#### Fans

##### Operating range

The operation point is in the stable part of the curve.

Safety protection is provided for the motors as follows, unless otherwise specified:

- Single phase motors:		Thermal overload protection.

- Three phase motors:		Combined thermal overload and phase failure protection.

##### Reliability and availability

The maximum allowable downtime for installed fans is such that replacement does not take longer than 2 hours when executed by qualified building maintenance staff.

Contractor submits service, maintenance, troubleshooting and testing instructions to the Project Manager in order to obtain acceptance. Documentation is indexed in accordance with the equipment part of the operating & maintenance manuals.

##### Technical restraints

The fan is complete with standard flanges.

Bearings are of the permanently lubricated type.

Air flow arrow indicators are installed for each fan unit.

Fan is direct driven or belt drive as required by equipment schedules, suitable for mounting at any angle and mounted on vibration areolation mountings.

Motor rating is greater than  the maximum power required by the fan at any operating point between zero (0) and break off capacity.

Fan casing are insulated with high density acoustic insulation to limit break out noise to the occupied space.

The fan motors are provided with manually adjustable speed controller to deliver the specified air quantity where required.

##### Installation restraints

Install fan assembly in accordance with manufacturer's recommendations.

##### Measurement to confirm equipment compliance with specification

The Contractor supplies the necessary field testing instruments and detailed description of field testing arrangement to prove a capacity/performance measurement accuracy of ± 5% for the fan acceptance testing.

Certified test results are plotted on the official published and certified equipment performance graph/table to confirm that claimed performance is achieved.

The various tests as required by the QMS are demonstrated and accessible to the Supervisor at all times for monitoring.

#### Low pressure air distribution system

##### Operating range

Maximum allowable variation between actual air flow and specified air flow does not exceed 5%.

Leakage does not exceed 4% under operating conditions.

Ducting system attenuates the total sound power fed into the system by the fan to provide the specified noise levels in the spaces supplied by the ducting system either directly or indirectly (duct break out and noise or air outlet noise).

All isolating, fire, smoke and balancing dampers have external easy accessible position indicators, with locking and sealing means when required, and means of resetting after tripping.

Inspection doors are provided to inspect damper and/or equipment operation for which external indication is impossible or impractical.

##### Reliability and availability

Duct system control and safety equipment such as automatic dampers, booster fans, etc., requiring service and possible removal/replacement are installed in such a way that the downtime of the duct system does not exceed 1 hour when either service/repair or removal and re installation are required.

Duct system control and safety equipment requiring service, maintenance, trouble shooting and periodic replacement etc., are documented in accordance with the equipment part of the operating & maintenance manuals.

##### Technical restraints

The ducting system complies in all respects with:

- SANS 1238 1979 "Standard Specification for Air Conditioning Ductwork

- SANS 10173 1980 "Code of Practice for the Installation, Testing and Balancing of Air

Conditioning Ductwork".

- Low Velocity Duct Construction Standards-SMACNA.

- SANS 10400 Section TT 43.2.

Additional sound attenuating elbows, attenuators, internal acoustic material are installed if a sound analysis - in accordance with Chapter 32 Sound and Vibration Control of ASHRAE 1984 System's Volume - for the actual sound power generation of the selected fan, selected fittings and duct construction details indicate that it is required to maintain the specified noise level in the space.

Flexible ducting complete with insulation are constructed of non-combustible material as required in terms of the building regulations provided that:

Approved combustible flexible connections are used where the length of such connection does not exceed 1.5m and such connection does not pass through any wall or floor which is required to have a specified fire resistance.

Approved combustible flexible joints of not more than 250 mm in length are used in any system room where such system room are protected by a smoke detection system.

##### Installation restraints

Ducting systems are isolated from actual or potential vibration generating equipment and building components to eliminate transmission of vibrations.

##### Pressure testing

Duct work is pressure tested as follows:

- The duct pressure is at least 2 times maximum operating pressure, or 150 Pa, whichever is greater.

- Smoke is introduced into the duct section under test.

- All leaks letting out visible smoke are closed up with approved duct sealing compound.

- A further pressure test is performed at the above specified duct pressure and leaks sealed until a maximum allowable leakage rate of 4% are reached, suitably de-rated for the volume handled by the duct section being tested

- Pressure testing is performed with the spigots installed, temporarily capped, before application of the external insulation.

##### Measurement to confirm Plant and Materials compliance with specification

The testing and balancing of the ducting system are executed in the presence of the Employers  Supervisor and/or  a representative delegated by the Project Manager..

The method instrumentation, procedure, recording are documented in a testing, balancing, adjusting procedure book.

Minimum requirements for testing procedures in accordance with SANS 10173 and/or Procedural Standards National Environmental Balancing Bureau and/or CIBSE are submitted for acceptance

On completion of testing and balancing of the ducting system a signed reports submitted by the Contractor to the Project Manager listing all the results to prove that the system are balanced as specified.

The Contractor submits to the Project Manager proven and necessary calibration certificates that measurements have an accuracy within 5%.

#### Refrigerant piping system

The refrigerant piping system is designed and engineered in detail in accordance with the design criteria laid down in:

- Trane Reciprocating Refrigeration Manual 1977, and/or

- Carrier Systems Design Manual Piping Design Chapter 3, Refrigerant Piping.

The refrigerant accessories are fully catalogued products and the documentation to include performance curves or selection tables, for the expected range of operational conditions.

The Contractor submits to the Project Manager certified detailed selection shown on these performance tables or curves.

The Contractor submits to the Project Manager full documentation and calculations for acceptance of Plant and Materials submission, showing all detailed pressure loss and velocity calculations for the entire refrigerant piping system and accessories under full load and minimum load conditions, including the temperature/pressure curves and balance points for evaporator, compressor and condenser.

Where reduction in pipe size are necessary to provide sufficient gas velocity to entrain oil upwards in vertical risers at part load, and at full load the pressure drop exceeds specified design limits, a double riser incorporating an oil trap are necessary.

The system is designed:

- To minimise loss of lubricating oil from compressor at all times.

- To ensure lubricating oil return to compressor, at the same rate at which it leaves under all load conditions.

- To prevent lubricating oil being trapped in system.

- To prevent liquid refrigerant from entering the compressor during operation and shutdown.

- For minimum pressure drop and noise generation. The suction, discharge and liquid lines are sized so that the pressure drops do not cause a change in saturation temperature of refrigerant greater than 1.1°C in each respective line.

- For handling the specified capacities from 100% down to minimum load at specified suction and discharge/condensing temperature.

Refrigerant piping accessories and connections are selected to ensure no leakage from refrigerant piping system during its operational life.

Refrigerant piping system is complete with all necessary isolating valves to enable repairs and maintenance to be carried out on any one section of the system.

The refrigerant accessories are connected and installed into the refrigerant piping system that either a sub component replacement or total removal or reinstallation of the accessory does not take longer than 2 hours by qualified refrigeration mechanics.

Piping system, including accessories, thermal insulation, hangers, supports and vibration isolators are selected and installed to give a minimum working life of 15 years under normal building service conditions.

The entire refrigerant system is subjected to a leak pressure test with a suitable gas, e.g. clean dry air or nitrogen.  It is permissible to add system refrigerant to enable leakages to be more easily detected.

Prior to carrying out this test, the Contractor verifies by examination of the various parts of the components of the system that the test pressure to which they were subjected at the manufacturer's works, are adequate for the required duties.

Incorporate a safety valve or rupture disc in the piping system.

Rupture discs have a specified and certified bursting pressure at a specified temperature and marked accordingly on the disc.

The system complies with the Safety Code for Refrigerant Piping ASA B31.35–1962, with the requirements of ASME, with Occupational Health and Safety Act as amended, and with local authority’s by laws.

Piping is stored and handled on Site to prevent dirt from entering piping system. Open ends are plugged.

Tubing is protected against oxidation during silver soldering by use of dry nitrogen flowing through tubing.  Solder to be silver solder.

Where required for connection to gauges and control devices, tubing not larger than nominal 10 mm are type K soft (annealed) with flared tube fittings suitable for high pressure.

Accessories connected to copper tubing have solder type ends or flanged ends and soldered flange adaptors.

Piping is installed so as to allow for expansion and contraction.  Suction and discharge lines are installed so that the first point of support is six (6) pipe diameters in each of three (3) directions from the unit.

System vibration areolation are in accordance with sound and vibration control requirements

Thermal insulation of suction line is in accordance with insulation requirements

Piping is installed parallel or perpendicular to building construction, while maintaining the required gradients.

Refrigerant piping between indoor and outdoor units are supported along its entire length by a galvanised perforated cable tray of sufficient size to allow pipe work to be neatly laid out and insulated. The cable trays are supported clear of fixing surface by galvanized brackets allowing air space between cable tray and mounting surface.

Where piping and insulation are exposed to damage or located externally to the building, a galvanized sheet metal cover having a minimum thickness of 0.8 mm are neatly formed and secured to the cable tray brackets.  Joints are lapped by a minimum of 30 mm and to have a minimum clearance of 10mm over insulation.

All necessary pressure gauges are installed in refrigerant lines to check pressures and temperatures for load monitoring function of various accessories and possible blockages of strainers.

Isolate accessories requiring regular inspection, cleaning and removal by shut off valves to enable this without pump down of the entire refrigeration system.

##### Accessories

Liquid receivers are offered with the following minimum requirements:

- Each receiver has sufficient capacity to hold all refrigerant in the system to which it is connected, except that in systems having two (2) or more separate refrigerant circuits, cross connected by pump out piping.

- The receiver has sufficient capacity to hold all refrigerant in the largest circuit.  Receiver capacity is based on not over 85% of its internal volume being occupied by liquid. Receiver is complete with liquid level indication.

Liquid suction interchanger has the following minimum requirements:

- Heat exchangers for field assembled systems are standard products of a reputable manufacturer.  Field fabrication of heat exchangers is not permitted.

- Heat exchangers for field assembled systems are shell and tube, shell and coil or double tube type.

- Tubes are seamless copper, plain or with integrally formed fins.  Shells are welded steel, conforming to the requirements of the latest edition of the Mines and Works Act or the Machinery, Factories and Building Work Act and Regulations, covering pressure vessels. Gas passages are arranged to prevent trapping of oil.

Refrigerant driers have the following minimum requirements:

- Refrigerant driers for field assembled systems are of the angle type with removable cartridges that can be renewed without disturbing pipe connections. Driers have brass or steel bodies and solder joint connections. Bonnets are flanged and bolted. Cartridges are charged with dry silica gel or activated alumina, held securely in place without restraining normal expansion, and provided with suitable means for distributing the refrigerant evenly through the charge. Unless otherwise indicated driers are installed in liquid lines close to the receiver outlets and be provided with valves on the inlet and outlet connections. Valves by-passes are also provided unless the driers are of a type guaranteed by the manufacturer to operate indefinitely without dusting of the desiccant or appreciable increase in pressure drop.  Install a liquid sight glass and moisture indicator of the colour change type in the liquid line, close to each drier.

- Select each drier so that the pressure drop through the drier does not exceed 14 kPa when operating at full connected evaporator capacity.

- Drier cartridges are not installed until after pressure and vacuum tests have been completed but immediately prior to charging

Thermostatic expansion valves have the following minimum requirements:

- In field assembled systems, each evaporator circuit is provided with a thermal expansion valve of the gas charged type.

- Valves have external equalizer connections, external superheat adjustments with seal caps and solder joints or flanged pipe connections.

- Valves move from fully open to fully close with not more than 3 °C superheat change. Superheat setting is at 6 °C at full load.  Each valve is provided with an external strainer, regardless of any internal strainer that may be incorporated in the construction. Strainers are to be as specified under "Refrigerant Strainers".

Oil separators have the following minimum requirements:

- Each reciprocating compressor having suction and/or liquid mains more than 15 m long is equipped with a discharge line oil separator.

- Separators are made of welded steel and have an effective impingement type separating element, an oil sump and a float operated return trap connected to them to return oil to the compressor automatically.

Refrigerant stop and shut-off valves have the following minimum requirements:

- Refrigerant stop valves generally are back seating key operated, sealed cap type. Valves which are opened and closed in regular operation have packless type hand wheels.

Refrigerant strainers have the following minimum requirements:

- Refrigerant strainers are angle type, cleanable without disturbing pipe connections. 40 mm NB strainers and smaller have brass bodies and solder joint connections. 50mm NB strainers and larger brass or rust proofed steel or iron bodies and flanged connections. Connections are to be flanged and bolted.

- Screens are bronze metal with perforations not larger than 0.25 mm for liquid lines and 0.5 mm for gas lines. The free area of each screen is not to be less than 5 times the area of the strainer inlet pipe.

Charging valves are located in the liquid line between the receiver shut-off valve and expansion valve.

The Contractor provides external gauge connections at inlet and outlet of condenser, evaporator coil and compressor to enable evaluation of system pressures at commissioning and for normal maintenance inspections.

All gauges are connected to the refrigerant piping system through isolating shut off valves.

Liquid indicators are sight glass - double port with seal cap type - of full size in the main liquid line before the thermostatic expansion valve.

The solenoid valves have manual override to enable the system to continue to operate in case of solenoid coil failure.

Vibration isolators (flexible connectors) have the following minimum requirements:

- Suction and discharge lines from the compressor are fitted with flexible connectors of the bronze braided hose type, having sweat-ends, to fit over copper tubing having the same size as the line in which they are installed.

- Locate flexible connector as close as possible to the compressor and parallel to the compressor shaft. It is not subjected to compression or extensions.

- For refrigeration installation utilising a remote air cooled or evaporative condenser, hot gas mufflers are used to remove pulsations from the hot gas discharge and thereby reduce noise and vibration from the piping system.  The hot gas muffler is installed to prevent accumulation of oil.

##### Testing, charging and evacuation

Complete system is pressure tested with dry nitrogen and leak test carried out.  Test pressure is maintained for 24 hours with no loss in pressure. The complete system is evacuated and proved to be free of moisture. The system stands for a minimum of 12 hours with no change in vacuum. System is liquid charged on high side following purging of connections to the estimated total charge.

The following method is recommended for pressure leak testing:

- Use a mixture of nitrogen & trace refrigerant in conjunction with one of the following suitable

leak detection methods: Acceptable leak test methods include, Liquid submersion testing, soap bubble leak detection, fluorescent leak detection & electronic leak testing or any acceptable standard.

- Pressurise the complete system with dry nitrogen & leak test using any acceptable method.

- Having ensured there are no leaks using a) or b) above, the system is pressurised to a

safe test pressure. Observed over a period of time, relative to the size of the system that no pressure drop occurs, having due regard to temperature variation throughout the system.

- After determining that there are no refrigerant leaks when the system is pressurised, the

system is evacuated to remove moisture & air. Evacuation is deep evacuation method, or triple evacuation using dry nitrogen only as the moisture absorber. To be witnessed by Supervisor.

- DEEP VACUUM METHOD: Pull a deep vacuum to a pressure of less than 13 Pa absolute (100

microns of mercury). After isolation the vacuum pump, allow the system to stand for 60 minutes to ensure the vacuum are maintained at or below 16 Pa absolute (120 microns of mercury), OR

- TRIPLE EVACUATION METHOD: Use a vacuum pump to pull a vacuum to a pressure of at

least 260 Pa absolute (2,000 microns of mercury). Break the vacuum with dry nitrogen & allow the system to stand. Re-evacuate the system & repeat the procedure twice more, breaking the vacuum each time with dry nitrogen.

- The final evacuation is held for twelve hours with no loss of vacuum. After the system

has been evacuated the vacuum pump is isolated from the system and as guide, with constant ambient conditions the vacuum does not rise more than 13 Pa absolute (100 microns of mercury) in one hour. A greater rate of rise may indicate a leak. Absolute vacuums are measured using accurate measuring Equipment selected for the specific application.

Expansion valves and solenoids are stripped before welding refrigerant pipes to avoid overheating and associated damage to seals, or they are to be kept at constant temperature by means of damp rags.

Should the refrigerant piping run longer than normal, the amount of refrigerant oil is to be increased in the pipe system as per the manufacture’s specification.

### Fuel Oil Piping

- The fuel oil piping is designed and tested in conformance with EN 13480.

  - BS EN ISO 23251:2007+A1:2008 is also utilised for the design.

- Fuel oil piping is classified as per SANS 347.

- Fuel oil piping and pipe support design takes into account expansion and contraction of the pipework and components in the system based on a maximum operating oil temperature of 160°C.

- Neither threaded nor cast iron fittings are used on fuel oil piping.

- Flanged joints are only used where they are essential for maintenance or inspection purposes. Where flanged joints are required suitable oil resistant gaskets are used.

- All piping is arranged to enable the draining of sections for maintenance purposes without having to break flanged joints. All pipe fittings are easily accessible for maintenance.

- Pipes are properly supported to prevent undue stress being imposed on the pipework or on other components.

- Fuel oil piping is routed above ground level where possible. If fuel oil lines are routed below ground level, trenches are protected against flooding and ingress of dirt and ash. Routing below ground is only allowed if it is unavoidable and is accepted by the Project Manager.

- Piping is insulated as per the specification 240-56247004.

- Vents are provided at the highest portion and drains on the lowest portion.

  - Vents and drains are located in areas where they are operable without special temporary access being required.

  - Vents and drains discharge in such a manner that spillage can be controlled.

- Where compensators are required to cater for thermal expansion of pipelines or any misalignments, they are metallic bellows type and are fitted with restraining bolts to cater for the pipeline stresses and limit axial movement without over-stressing of the bellows.

- Fuel oil valves

  - Valves are steel, fire safe, preferable rising spindle type

  - Valve to be easily accessible for maintenance or in case of emergency (e.g. Fire)

  - Glands are able to be repacked without the removal of the valve from the piping.

  - Suitable oil resistant gaskets are used between the pipe flange and the valve.

- Fuel oil piping is flushed before it is commissioned, flushing is done with an appropriate fluid.

  - A fuel oil flushing procedure is submitted to the Project Manager for acceptance.

- Testing of fuel oil piping includes as a minimum.

  - 100% X-ray testing.

  - 100% surface crack testing.

## Electrical Engineering Works

The Contractor provides the complete electrical system for the works, interface the works and supply to the respective Plant and Materials in the scope.

This section specifies the relevant regulations and standards to be applied for the engineering design, construction, and testing of the Plant and Materials forming the electrical system.

The Contractor provides all the necessary material and equipment for correct works operation, with high availability and maintainability, safe in use and correctly selected according to environmental and site conditions.

### Voltage Levels

The rated voltage levels of the Plant and Materials are as follows:

- MV Switchgear	:	11kV and 3.3kV

- LV Switchgear	:	380V and 690V

- UPS System	:	380/220V

- DC System	:	220/24V

All AC Plant and Materials of the auxiliary system, except where otherwise specified, is capable of continuous operation at a voltage level in the range 90% to 110% of the nominal voltage, and short-time operation at 75% of the nominal voltage during motor starting without deterioration.

DC Plant and Materials is capable of normal operation in the range of 110% to 85 % of nominal voltage without deterioration.

### Cabling and Racking

The Contractor provides cables and racking in accordance with 240-56227443: Requirements for Control and Power Cables for Power Stations Standard.

The Contractor provides all documentation as required in the VDSS in Appendix B.

The Contractor supplies, and install all cable accessories such as terminations and jointing kits, cable glands, lugs, bolts, washers and nuts for terminations, sleeves and other ancillary material for fitting the cables into position.

#### Cable Schedules

The Contractor routes all cabling, compiles the cable and termination schedules, supplies and installs the cables, labels them, test the cables, complete the quality documentation and issue it to the Project Manager for acceptance.

The cable schedule includes the cables that will have to be removed from the existing ash bunker boards.

#### Cable Management System, Pull Slips and Drawings

The Contractor performs a detailed design for the size, length and route of the cabling and compiles and submits cable schedules for acceptance by the Project Manager. The schedules indicate the general cable requirements i.e. application, power, fault levels, cable termination details and special routing requirements.

The cable schedules are utilised as the primary documents for dictating the cabling requirements of the works.

The Contractor installs the cables, test, terminate the Plant and Materials for the electrical system and complete the cable pull slips. The cable pull slips indicate the number of joints in the cables.

The cable pull slips contain the as-built status of the cables and the drum number from which the cable has been pulled. The Contractor red-lines the cable block diagrams and submit such diagrams together with the as-built cable schedules as per the cable pull slips to the Project Manager.

The Contractor provides and implements a cable drum management system. The Contractor compares this to the Project Manager’s cable delivery to Site management system and consolidates on a regular basis.  All cable deliveries to the Site are logged on a cable drum delivery schedule provided by the Contractor and accepted by the Project Manager. The cable drum delivery schedule is signed by the Project Manager.

#### Marking of Cables

Cables are legibly marked in accordance with the requirements of SANS 1339 and SANS 1507 as applicable, but the marking includes the specification number to which the cable has been manufactured, the word “ESKOM”, the conductor size in mm2 and material e.g. Cu (copper).  The PVC sheathed cables have a colour coded stripe in accordance with SANS 1339 and bear the SABS mark.

The cables are sequentially marked at one (1) meter intervals with the length indicated.

### Low Voltage Switchgear

The LV switchgear complies with 240-56227516: LV Switchgear and Control Gear Assemblies and Associated equipment for voltage up to and Including 1000V AC and 1500V DC standard and IEC 60439 as a minimum.  The Contractor provides all documentation as required in the VDSS in Appendix B.

The Contractor makes use of 240-56227516 and technical schedules A and B (part of 240-56227516) for writing the procurement specification or scope of work for the Contractor’s Subcontractors.

The LV switchgear and control gear assemblies are of factory built assemblies, type tested assembly (TTA) type that complies with the requirements of technical schedules (i.e. schedules A and B) and 240-56227516: LV switchgear and Control Gear Assemblies and Associated Equipment for voltage up to and including 1000V AC and 1500V DC standard. The assemblies are of the free standing, front-operated, and rear-access cabling type. Cable entry is from the bottom.

The LV switchgear complies with the design and construction requirements of 240-56227516. The low voltage AC switchboards consist of metal enclosed side by side placed metallic columns firmly jointed. The switchboards are easily extendable at both ends. Each column is divided into modular elements which contains the interrupting devices.

LV switchgear assembly that contains a bus-section is arranged with a double bus-section for safety of isolation.

The LV switchgear system main incomers and bus sections (double bus section) circuits is of the fixed type compartment and withdrawable breakers and is electrically interlocked to prevent the paralleling of two incoming supplies to a switchboard.

The cubicles of motor starters rated below 37kW are of the withdrawable type while motor starters rated above 37kW are of the fixed type design.

The types and quantities of spare circuits are decided upon between the Contractor and the Project Manager during the development of the LV switchgear procurement / scope of work that is provided to the Subcontractor.  The procurement specification is subjected to acceptance of the Project Manager.

The Contractor ensures that the LV switchgear lengths are such that they can be accommodated within the existing ash bunker substations.

The Employer provides typical schematic diagrams (refer to drawing 0.61/56743) which the Contractor uses to develop standard schematic drawings.

The critical motors require protection via IEDs.

The LV switchgear is rated at 50kA for 1 second. The protection devices comply with 240-56357424: MV and LV Switchgear Protection Standard. Protection and control schemes in accordance to 240-56357424: MV and LV Switchgear Protection Standard.

The Contractor groups motor starter types based on size. Motor starter type grouping is performed to minimise the required motor spare and space requirements in the most cost effective way. The Contractor provides a motor starter standardisation policy which demonstrates the reasoning behind the motor starter groupings.

The control circuit voltage is 230V AC and is bus wired throughout the length of the board. The voltage is supplied from the main busbar via a dip proof inverter (DPI) to prevent the contactors falling out during voltage dips. Incomer circuit breaker protection relays and critical motor protection relays require 220V DC control supply.

### Low Voltage Motors

#### General

The Contractor provides LV motors that comply with 240-57617975: Procurement of Power Station Low Voltage Electric Motors Specification and IEC 60034 as a minimum. The Contractor provides all documentation as required in the VDSS.

The Contractor makes use of 240-57617975 and technical schedules A and B (part of 240-57617975) for writing the procurement specification or scope of work for the Contractor’s Subcontractors.

The Contractor only tenders designs that have successfully been implemented and used in a similar application for at least 2 years in service (including all components within the design). If a design has a component that has not been successfully implemented and used for at least two years in service, the affected parts and the extent of their experience is declared in the tender.

The Contractor provides a completed Part B of technical schedule A&B as per Appendix P of this document at tender phase, and technical schedule A&B as per Appendix C of 240-57617975, at detailed design phase.

The Contractor completes all deviations schedules for the technical schedules A and B.

#### Testing

The Contractor ensures that all type testing is witnessed by the Supervisor.

The first motor of each size and type manufactured is performance tested to prove compliance with the quoted performance. Type test certificates on identical motors, may, at the Project Manager’s discretion, be accepted in lieu of these tests.

All performance tests are in accordance with IEC 60034-1 and SANS 1804.

The Contractor submits all routine and type test certificates to the Supervisor for acceptance thirty (30) days before the delivery date of the motors.

The Contractor provides test certificates to show the power factor and efficiency figures calculated from the test results for 100%, 75% and 50% of full load conditions.

The Contractor records all motor test results on the Employer’s standard form which is attached to Annexure D and E in 240-57617975.

### Transformers

Oil type transformers comply with 240-53113666: Medium Power Transformers Used in Power Stations Standard. Dry type transformers comply with SANS 60076-11: Power Transformers Part 11: Dry-type Transformers.  The Contractor provides all documentation as per the VDSS in Appendix B.

The Contractor makes use of 240-53113666 and technical schedules A and B (Refer to Table P1 in Appendix P) for writing the procurement specification or scope of work for the Contractor’s Subcontractors.

Transformers with 690V on the secondary side are oil type transformers. Oil type transformers are installed outside and adjacent to the substation.

Transformers with 400V on the secondary side are dry type transformers. Dry type transformers are installed inside the substation and may form part of the switchgear.

The Contractor supplies all the components required to move transformers in and out of their respective bays (e.g. wheels and steel frames). The system is designed such that a transformer is removed from its bay in the fastest time possible.

The design and layout considers ease of access for operational and maintenance activities. The transformers are accessible for operating and routine inspections from floors and platforms provided by the Contractor.

Main MV/LV transformers are sized to feed all main LV switchboards during normal operation (bus section open and the other incomer closed), in case of emergency conditions (bus section closed and the other incomer opened) and allowing the start-up of the biggest motor and inside permissible voltage range.

The vector group of MV/LV transformers is Dyn11.

Connection between MV/LV transformers and LV switchboards is through LV cables.

The MV/LV transformers neutral point on the low voltage winding is solidly grounded.

An impact recorder is attached to the top of each transformer tank as well as the active part for the duration of the transport process. The recording is date and time stamped until the transformer is in its final position.

### Lighting and Small Power

The lighting and small power complies with 240-55714363 Coal Fired Power Stations Lighting and Small Power Installation Standard as a minimum. The lighting and small power system includes the distribution boards, single and multi-core cables, conduits, wiring, luminary brackets, luminaries, and switch socket outlets.

Lighting designs are performed with personnel safety as first criteria and in compliance with SANS 10114-1.  The completed installation provides adequate lighting to allow the Employer’s employees in their work stations to do their work safely and efficiently. The illumination levels used are those recommended by SANS 10114-1, “Interior lighting”. These recommendations are specified and are law under the OHS Act.  The Occupational Health and Safety Act (OHS Act) specify minimum illumination levels for safety.

In large size rooms, easy change of the bulbs and lamps has to be considered.

The number of different luminaries used is minimised as far as possible.

Where the rooms or corridors have more than one (1) entrance/exit, multiple point switching is provided (one at each access).

The Contractor provides daylight switches (photo-sensitive) on all outside lighting installations, for example substations, equipment buildings and DHP, to ensure lights are only switched on when required.  Manual override facilities are provided.

The Contractor provides distribution boards in accordance with 240-55714363. The distribution boards utilised outdoors is IP65 rated and indoors IP55 rated. Locate small power panel boards in a central location to reduce the extent of low voltage wiring for lighting and small power needs. The distribution boards include 20% spare capacity for future expansion.

On completion of the installation, a certificate of compliance as stipulated in SANS 10142-1 is issued to the Employer in terms of the Occupational Health and Safety Act, (OHS Act 85 of 1993). The qualified Contractor’s Occupational Hygienist performs illumination measurements as recommended in SANS 10114. Illumination measurement reports are produced and submitted to the Project Manager.  The measurements need to be performed at night after the installation has been completed.

### Earthing and Lightning Protection

The earthing and lightning protection complies with 240-56356396: Earthing and Lightning Protection Standard as a minimum.

The Contractor ensures that all metal non-current carrying parts of the Plant and Materials are effectively connected to earth. It is done by means of their mounting arrangement or by means of a special earthing conductor.

Conductors utilised for earthing are appropriate for the site’s soil conditions.

The Contractor is responsible for the earthing of the Plant and Materials. The Contractor performs earthing continuity tests as part of the quality control process. The tested earthing points are marked and recorded for reference purposes (plant earthing maintenance purposes). All installation plans are submitted to the Project Manager for testing witnessing purposes.

The Contractor clearly defines the design, philosophy and implementation (installation) plan with drawings, calculation, software applied and all supporting documentations for:

- Lightning protection

- Equipment earthing

- System earthing (interfaces)

For equipment and personnel safety the Contractor performs earthing work in accordance with applicable standards and submits to the Project Manager for acceptance of the design and all installations.

The Contractor is responsible for connecting the new buildings earth mats to the station earthing mat.  The Contractor connects the new building earthing mat to the station earthing mat and the points of connection will be decided upon between the Contractor and the Project Manager.

### Essential Power Supplies

The uninterruptable power supplies, battery chargers, batteries and battery cabinets comply with the following as a minimum:

- 240-53114248: Thyristor and Switch Mode Chargers, AC/DC to DC/AC Converters and Inverter/Uninterruptible Power Supplies Standard

- 240-56360086: Stationary Vented Nickel Cadmium Batteries Standard

- 240-56176852: Capacity of Essential Power Supplies for Power Stations Standard

The Contractor makes use of technical schedules A and B to specify UPSs, battery chargers, batteries and battery cabinets in accordance with the Employer’s standards mentioned within this section.

A secure AC power supply (uninterruptible power supply) system is provided for the operation of control and instrumentation equipment and all other equipment requiring AC uninterruptible power.

Each complete system is rated to supply the load from its UPS (for normal operation) and simultaneously the load of the other UPS (in case of failure, for maintenance purpose or any reason).

The control scheme automatically transfer the AC load from the inverter to a back-up supply on inverter failure.

The UPS is equipped with at least two (2) RS232 ports to facilitate local and remote communication. In addition, to the RS232 ports, the RS485 and ethernet ports are provided as options.

The Plant and Materials are of a type tested design as per 240-53114248, as a minimum.

The Contractor makes use of nickel cadmium batteries with recombination units. The batteries have a standby time of four (4) hours each.

The batteries are installed in battery cabinets in accordance with 240-56360086.

During charging hydrogen is released from the batteries as a result of electrolysis of the battery water. Sufficient ventilation of the battery cabinet is ensured by the provision of ventilation louvers.

In accordance with the requirements of SANS 10119, Reduction of explosion hazards presented by electrical equipment — Segregation, ventilation and pressurization, the hydrogen concentration limit inside the battery cabinet is maintained below 0.8%.

The Contractor calculates the minimum ventilation requirements as per Appendix G of 240-56360086.

If the required natural ventilation cannot be obtained, forced ventilation is used venting the cabinet directly to a safe area.

The effectiveness of the forced ventilation is monitored. If the ventilation is not fully operational the failure of the forced ventilation must alarm and the boost and/or equalise charging disabled. The Contractor makes use of extraction fans to remove the air from the cabinets.

The battery cabinet is classified based on the principles stipulated in 240-56360086, Classification of battery rooms. If forced ventilation cannot achieve the required ventilation then the battery cabinet is zoned as per SANS 10108.

The alarms and indications are as per 240-53114248.

### Variable Speed Drives (VSD’s)

The Contractor makes use of MV and LV VSD technical schedules A and B (Refer to Table P1 in Appendix P) to specify VSD’s, that might be incorporated into the design. Two speed motors have to be used on the transfer conveyors and bucket elevators.

## Control and Instrumentation Works

### Overall System Technical Requirements

#### Introduction

The works includes the upgrading of the existing DHP systems (including C&I) currently installed in unit 1, 2, 3, 4, 5 & 6.

The Contractor provides all equipment and services and executes all work necessary to fulfil all requirements specified in this Works Information.

The hoppers conveyors, transfer conveyors and bucket elevators Local Control Stations must be replaced as well as the supports. The new Local Control Stations should have the same controls and should have motor current meters. The bucket elevator creep speed operation Local Control Panels must also be replaced with the same functions as the existing ones.  All new switch gears must have time/hour meters so that the chain conveyors and bucket elevators running hours are noted for chain replacement purposes. These running hour meters should be resettable when chains are replaced. New controls must be available for the new B transfer conveyor and it should have a local control station.

The bucket elevators must have chain elogation switches which will give the desk operator an alarm that the relevant bucket elevator chain needs to be shorten.

Units 1 to 3 are using the Siemens Teleperm C / Iskamatic B C&I system and units 4 to 6 are using the ABB PROCONTROL P14 - DCS. The Siemens are obsolete and upgrades are required on this system whereas the ABB is still supported and implementation of the new philosophy can be achieved. All the inputs and output signal cables to the field equipment and the limit switches and speed switches replacements on the plant for all six units. The dust plant control station and the new hopper aeration air control station is at the units control rooms and the units control rooms must have the ash bunkers level indications. The dust and water ingress prevention rating should be IP65.

All the ash conditioners with its aeration air blowers, scrubbers and the conditioner conveyors with its moving heads are operated from the Outside Plant Control Room.  All input and output signals and plant feedback signals are going to the Outside Plant Control Room. The outside plant DCS is the Yokogawa Centrum VP and there are new control cables towards the six additional ash conditioners. The existing Local Control Station just needs upgrade to handle two ash conditioners each.  However, the contractor is to ensure that the existing control and signal cables and Local Control Station are sufficient and whether it would needs upgrade. Yokogawa systems are still supported and implementation of the new philosophy can be achieved. The only issue is with the Yokogawa systems is that this version is outdated and any additional plant will result in implementation of the latest versions.

The Contractor informs the Project Manager of all changes required to the existing operating, maintenance and control philosophies and obtains his acceptance prior to making these required changes to the existing system.

The Contractor ensures that the C&I interface provides for total automation of the DHP and hopper aeration system through the Unit DCS. The Contractor ensures that the C&I interface provides for total automation of the instrument compressor and conditioner/scrubber plant through the OPCR DCS. The C&I solution provides for interlocks to prevent incorrect operation of the DHP, hopper aeration, instrument compressor, conditioner/scrubber plant systems by the system controller or operator.

The Contractor is responsible for the design, procurement, and installation of new C&I equipment and systems for the works.

The Contractor provides termination schedules for the junction boxes/enclosures and switchgear to the Project Manager.

The designs, plans, and procedures for testing communication between the HMI and the PIS are the responsibility of the Contractor.

The Contractor submits, as a minimum, the following documentation for review and acceptance as defined in Appendix B (VDSS):

- P&ID’s & PFD’s

- Functional I/O block diagrams

- Instrumentation schedule and I/O lists

- Actuator and Drive schedules

- Equipment lists

- C&I equipment load list

- Alarm lists

- Proposed instrument, drives and equipment datasheets

- Proposed instrument, panel, JB, equipment & drive locations

- Typical or proposed cable routing and cable rack layout drawings

- JB, LCP and control cubicles general arrangements layout drawings including specification and materials

- General arrangement layouts drawings  junction boxes, DCS cubicles (expansion details of DCS for Units 4 to 6 and OPCR DCS (including GA layout drawings)) and local control panels

- Proposed instrumentation hook-up diagrams

- Cable specification

- Cable block diagram

- Functional design specification, narrative control & operating philosophies and functional logic diagrams

- HMI mimic diagrams and description together with alarm management and other related concepts

- Proposed loop connection diagrams or device interface concepts

- Typical earthing, lightning protection drawings

- Data communication and network architecture drawings

- Control system hardware conceptual structure and functional distribution

- Control system and network systems manuals

- Design, installation and commissioning QCP. Quality manual including list of tests to be performed.

- The preliminary list of tags required for the PIS

- List of recommended spares with their MIN and MAX ratings

- Troubleshooting manual for possible faults on the C&I systems

- Typical power supply drawings or power requirements (concepts)

- Typical maintenance strategy document for C&I equipment

- CV’s of all C&I engineering resources

- The basis for the supply of all documentation relevant to the different project stages is stated in the VDSS, appendix B.

The Contractor submits the information requested in the form of the template format that is supplied by the Project Manager, see appendix J.

- 240-61379718 – Instrument schedule  template

- 240-61379755 -  Drive and actuator schedule template

- 240-72350241 – C&I panel interface list template

Alarm list supplied by the Contractor adhere and follows the Employer’s Alarm Management Guideline, 240-56355466.

The works complies with professional engineering practice and standards for fossil fuel power plants listed in Appendix E, and are designed for the environmental conditions prevailing at Tutuka P.S. Site.

The detailed scope of supply for the works is defined by a combination of performance, functional and equipment specifications such that a complete functioning system is provided.  The C&I specifications are captured in this section of the Works Information.

The Contractor, throughout the execution of the various contract activities addresses the following and obtains acceptance from the Project Manager:

- Make recommendations and proposals for process control concepts and plant performance improvements.

- Recommends cost-effective proposals.

- Mark-up and red lining of all additional items on the P&ID during system engineering and production activities of the works. The Contractor updates the P&ID’s

### Control System

Table 24 Summary of C&I Terminal Points

| SUMMARY OF C&I TERMINAL POINT (PLANT AREAS) |  |  |  |
| --- | --- | --- | --- |
| # | PLANT AREA | LOCAL CONTROLLER/DCS | CONTROL ROOM |
| 1 | Tutuka DHP System | Unit DCS | Unit Control Room (UCR) |
| 2 | Instrument Air Compressor Plant | Local Compressor PLC interfacing with OPCR DCS-Yokogawa | Outside Plant Control Room (OPCR) |
| 3 | Hopper Aeration System | UNIT DCS | UCR |
| 4 | Conditioner Plant | OPCR DCS-Yokogawa | OPCR |
| 5 | Conditioner conveyors | OPCR DCS-Yokogawa | OPCR |
| 6 | Ash bunker & Conditioner aeration air blowers | OPCR DCS-Yokogawa | OPCR |
| 7 | Conditioning effluent water system | WTP DCS - Yokogawa | Water Treatment Plant Control Room |

Table 24 above indicates a summary of the C&I interface terminal points for all the plant areas affected by the works. The unitised DHP system is controlled from the Unit Control Room (UCR) via the Unit DCS. The compressor plant is monitored and controlled from the OPCR by interfacing each compressor PLC to the OPCR Yokogawa DCS via the remote I/O panel (The interfacing philosophy follows that of the existing Yokogawa DCS).

The hopper aeration system is a unitised system which is completely new and is controlled from the UCR via the Unit DCS.

The conditioner plant is controlled and monitored from the OPCR via the Yokogawa DCS system.

Conditioning effluent water system is part of the water treatment plant and is controlled and monitored from the Water Treatment Plant Control Room via the Yokogawa DCS system.

#### Control system performance

##### Life Expectancy

The Contractor provides details regarding the lifespan (minimum of 20 years) of all control, hardware and software within the scope, with respect to timelines for respective migration, upgrade and system obsolescence (ie last-call). The Contractor ensures that control system hardware provided is similar to or a better version of the existing control system.

#### Control System Requirements

The control system is configured as a fully operational system and is workable in all respects and implemented in a consistent and integrated manner.  The control system provides all information, protection, control and local control facilities to enable the operator to execute his tasks safely, reliably and consistently from the HMI.

Alarms (Including Alarm Lists) follows the Employer’s alarm management system guideline 240-56355466.

The C&I DHP interface will provide for total automation of the new DHP and aeration air plant system through the Unit DCS. The C&I solution by the Contractor provides for interlocks to prevent incorrect operation of the plant by the unit controller.

The Contractor follows and adheres to Tutuka philosophy in terms of wiring of control and instrumentation/protection signals.

The Contractor develops the control, operating philosophies and functional design specifications for the works for implementation in the DCS.

New DCS cubicles follows existing philosophies and have the same rules/functionality as the existing cubicles for other plants in Unit 4-6, OPCR and WTPCR.

##### Unit 1 - 3 Control system requirements

DHP upgrade scope is included in this scope of work.

##### Unit 4 - 6 Control system requirements

The Contractor expands the existing ABB P14 DCS for the control and monitoring of the existing upgraded DHP and the unitised hopper aeration system. The control system design and Plant and Materials are in accordance with the existing ABB P14 DCS installation specifications and requirements.

The Contractor’s design provides for later expansion of the control system to readily incorporate future changes and enhancements to the DHP and the unitised hopper aeration system.

The Contractor provides for the following in the design at design freeze without reconfiguring the design:

  - 20% reserve physical space (slot capacity) and

  - 30% software reserve capacity.

  - 10 % installation capacity across the system from the field to the DCS cubicles

The Contractor submits and confirms conformance to the above in writing to the Project Manger during design freeze. Any spare capacity absorbed as part of modifications on the part of the Employer is documented by the Contractor as part of the design change process.

##### Outside Plant Control System Requirements

This section addresses control system requirements for common compressor plant and conditioner/scrubber plant.

Each compressor is automatically controlled by a PLC that is interfaced to the YOKOGAWA DCS. The Contractor provides the Project Manager with two copies of backups after commissioning of all the PLC/Controller related systems within the compressor plant. The Contractor provides and demonstrates the recovery procedure for the PLC/Controllers associated with the compressor plant.

Common plant such as the compressor and conditioner/scrubber plant systems are interfaced to the OPCR DCS for control, protection and monitoring.

The Contractor designs for the new DCS control cubicles for the compressor plant. The Contractor’s design provides for future expansion, changes and enhancements.

Yokogawa DCS has catered for DCS cubicles for 12 conditioners as per the existing conditioning plant P&ID (e.g. 0.61/57592). The Contractor is responsible for the interfacing of the conditioning/scrubber system in the existing DCS cubicles. There are six conditioners currently interfaced to these cubicles. The Contractor is responsible for supplying all Plant and Materials (I/O’s) for new signals of the conditioning/scrubber system.

The C&I system design for the common plant is in accordance with the existing OPCR YOKOGAWA DCS installation specifications and requirements.

The Contractor provides for the following in the design at design freeze without reconfiguring the design:

  - 20% reserve physical space (slot capacity) and

  - 30% software reserve capacity.

  - 10 % installation capacity across the system from the field to the DCS cubicles

The Contractor submits and confirms conformance to the above in writing to the Employer during design freeze.  Any spare capacity absorbed as part of modifications on the part of the Employer is documented by the Contractor as part of the design change process.

#### Human Machine Interface

A fully functional HMI Hardware (screens) that includes control functionality, indication, alarming, trending, on-line plant performance information and event recording is provided under this scope, since there will be a new DCS installation in Unit 1-3 by others; this is existing and provided for by the Employer in Unit 4 – 6 and the OPCR DCS.

The Contractor designs and integrates the new DHP and hopper aeration system HMI mimics into the existing Unit 4 – 6 HMI in the control room for control, protection and monitoring of the DHP and hopper aeration system.

A fully functional HMI is supplied by Others for Unit 1 – 3, the Contractor designs the new DHP and hopper aeration system HMI mimics and interface with the Others to integrate the mimics into the HMI screens in the control room for Units 1 – 3.

The Contractor designs and integrates the compressor and conditioner/scrubber plant system HMI mimics into the existing HMI in the OPCR for control and monitoring of these systems.

The Contractor takes full responsibility to ensure correct implementation of the HMI mimics in the units DCS and OPCR even though he is required to interface/liaise with Others in Unit 1-3.

The Contractor complies to 240-56355728, HMI design requirements standard.

#### Plant Information System (PIS)

The Contractor provides for a link from the Unit 4 - 6 DCS HMI to the existing PIS to accommodate for the new inclusion of DHP and hopper aeration system signals / tags.

The Contractor provides for a link from the OPCR HMI to the existing PIS to accommodate for the inclusion of the compressor and conditioner/scrubber plant systems.

#### Data Acquisition

The Contractor is responsible for implementing a data acquisition system and processing of signals from field mounted transmitters and any other field or interfacing devices. The data acquisition should monitor the condition of the measurements and faults reported by the transmitters. Signal distribution and transmission to other systems requiring the measurements and fault data are done by the Contractor as part of the data acquisition. The data acquisition is to form part of the respective automation unit and interface to the PIS.

Time stamping is to be done at the lowest level of the relevant DCS control system and as close as possible to the source of the signal, with a time resolution of one (1) millisecond.

#### Redundancies

All hardware, software and control network redundancy with regard to the control system and power supplies is configured to match the redundancies of the various mechanical process areas. The C&I system redundancies are consistent with the mechanical plant and electrical power redundancy and distribution configuration to minimise the effects of equipment failure on the overall unit. Through functional distribution of equipment, the C&I system is designed and configured for the following reliability:

- Safety

No individual C&I fault or no two (2) concurrent faults endanger the safety of the people, plant or jeopardise the integrity of the major plant.

- Unit trip/Load Loss

No individual C&I fault causes the unit load to drop below 45% MCR, or causes a forced outage or unit trip.

- Multi-Unit Trip

No individual C&I fault or two concurrent faults cause a multi-unit trip.

- Operator Interface

No individual C&I fault causes loss of operator work station or control and operator information.

#### Fire Detection System

The Contractor is SAQCC certified as per the department of labour to design a Fire Detection System. The Contractor designs for the fire detection system of the new compressor and unitised blower houses. The compressor house is used to accommodate the DHP instrument air compressors whereas the unitised blower houses will accommodate the blowers for hopper aeration system. The Contractor integrates the new fire detection system with an existing BMS.

The Contractor ensures that Eskom Fire and Life Safety is governed by the following standards:

| 240-54937439 | Fire Protection - Detection Assessment Standard |
| --- | --- |
| 240-54937450 | Fire Protection and Life Safety Design Standard |
| 240-54937454 | Inspection Testing and Maintenance of Fire Protection Systems Standard |
| 240-56737448 | Fire Detection and Life Safety Design Standard |
| 240-56737654 | Inspection Testing and Maintenance of Fire Detection Systems Standard |
| 240-54937439 | Fire Protection - Detection Assessment Standard |

### Field Equipment and Cabling

The Contractor supplies all the required new field equipment and cabling for the works.

The Contractor terminates the field cabling in the junction boxes and enclosures such as a splitter box.

All field instruments and equipment are installed in accordance with the requirements of the Field Instrument Installation Standard, 240-56355754 Rev 1.

Temperature measurement systems installations are installed in accordance with the Employer’s standard 240-56355888 Rev 1.

Pressure measurement systems installations are installed in accordance with the Employer’s standard 240-56355843 Rev 1.

The requirements for junction boxes, local control panels, and local control stations are in accordance with the Employer’s standard 240-56355815 Rev 1.

The Contractor proposes which of the existing cable tray/rack/manholes are re-used in his design. The Contractor needs acceptance from the Project Manager to re-use existing cable racks/trays.

Cable racks control and power cabling conforms to the requirements of the standard 240-56227443, Rev 1.  The Contractor shields and protects all cabling exposed to direct sunlight with appropriate covers.

The Contractor adheres to the Employer’s 240-56356396, earthing and lightning protection standard with regards to the details of earthing concept and lightning protection that will be employed for all cabling and racking, panels/cabinets and C&I equipment such as the junction boxes.

Field equipment cabling is configured with a minimum cable of two (2) pairs, no single pairs is accepted, the field cabling provides for a minimum of a single pair spare (in the case of UVG 2).

Instrumentation and field equipment (such as actuators) supplied by the Contractor supports standardisation on existing instrumentation/field equipment in the outside plant and Unit 4 - 6, as well as instrumentation which is provided by Others on Unit 1 - 3.

The Contractor ensures that all field equipment for the works is interconnected to the DCS as required by the Works Information to realise a fully functional system.  Field equipment and their electrical connections are housed in strong water and dust proof cases rated IP 65 or better as per SANS 60529.  Additional protection hoods and enclosures protect those transmitters situated outdoors or in adverse environments.  Instrumentation cabling between the instrument and the junction box runs inside the conduit (for a single instrument), trunking is used where there is accumulation of a number of field cables. Cable trays and racking are only allowed as trunk cabling supports between the DCS cubicles and the junction boxes.

The routes for C&I cabling, power supply cabling and the racking is a consistent and integrated design particularly taking into account different cabling and racking routes for common modes of failure.

The Contractor submits typical maintenance strategy document for all C&I related instruments and equipment for DHP, hopper aeration, compressor and conditioning plants during tender.

### C&I Power Supply Requirements

All instrumentation is loop powered and is power supplied from the DCS.

For special application that requires a 220 VAC (to be accepted by the Project Manager), bulk supply is available from the existing UPS’s for all 6 Units which the Contractor can utilize, in the Contractor’s design. The Contractor determines the load that needs supply from the existing UPS’s and submits the power supply design calculations to the Project Manager.

Unit 4 to Unit 6

The Contractor designs and extends power supply to the new ABB P14 cubicles.

The new DCS cubicle is supplied from the redundant 24VDC boards housed in Unit’s DC room. Power supply requirements are pre-determined for a new DCS cubicle and equipment that needs power.

Hopper Aeration Blower Plant

Loop powered instruments in the hopper aeration blower plant are supplied from the unit DCS and all the non-loop powered instruments power supply are catered for by the Contractor in his design.

Conditioner/scrubber system

Loop powered instruments in the conditioner/scrubber system are supplied from the OPCR DCS and all the non-loop powered instruments power supply are catered for by the Contractor in his design.

Pneumatic compressor system

The Contractor caters for the redundant 24VDC power supply requirement on the remote IO panel that will be sufficient for the 24VDC requirements of his design.

### Impulse Piping & Accessories

Impulse process piping, tubing and accessories are installed in accordance with the requirements of the Employer’s standard, 240-89147446.

### The Simulator Plant Requirements

The update of simulator for the Works is provided for by Others under a separate contract.  The Contractor provides all the information required for the modelling and update of Unit plant simulator with the new Plant and Materials designs within the Contractor’s scope. The Contractor provides all the information required 3 months prior to the first unit breaker open for modelling and update of the Unit simulator, the information required includes but is not limited to plant logics, control philosophy and P&IDs (with HMI Mimics).

The updating includes as a minimum the modelling software of the new DHP and the hopper aeration system.  OPCR DCS does not have a simulator.

### Licenses

All licenses required by the Employer covering the Plant and Materials, standard software and application software, forming part of the works, are supplied by the Contractor.

On sectional completion Contractor provides a software register with a contents reference to software, software revision, operating system and reference to operating system AKZ.

Licenses for the Plant and Materials and software provided include the Contractor’s Subcontractor or third party licenses for the life of the control system and are site licensed for use at Tutuka P.S.

The Contractor provides all upgrades of software and the associated licenses throughout the duration of the works.

### C&I Training Requirements

See section 5.2.8.1 for C&I training requirements.

## Process control and IT works

Human machine interface (HMI) requirements are as detailed in section 6.4.2.3.

Plant Information System (PIS) requirements are as per section 6.4.2.4.

The Contractor designs for the expansion of PA/telephone system of the new compressor and unitised blower houses. The Contractor integrates the PA/telephone system with the existing BMS.

Time synchronisation of the added hardware is the responsibility of the Contractor for Unit 4-6 and common plant. For Unit 1-3 it is the responsibility of Others.

The Contractor provides virus protection programs/philosophies for Plant and Materials that is exposed to the risks and complies with cyber security standard for OT (240-55410927).

The Contractor retrofits plant with the latest version of Software and Firmware.

## Constructability, Supportability, Operability, Reliability, Availability and, Maintainability

The Contractor has a structured process in place for constructability analysis, for the optimum use of construction knowledge and experience in planning, design, procurement, and field operations to achieve the Employers objectives of the works. The Contractor ensures qualified people with adequate skills with construction knowledge and experience are involved from the very beginning of the project, to maximize the benefits of the constructability analysis. This process includes examining design options that minimise construction costs while maintaining standards of safety, security, quality, and schedule, and is initiated in the front end planning process.  The Contractor completes rigging studies prior to start of construction.

### Supportability

The Contractor is able to fully support the system utilising resources from within the Republic of South Africa with regards to:

Technical service and support.

Maintenance requirements.

System configuration.

Management and coordination of DHP, conditioning plant and hopper aeration system repairs and equipment.

Supply of spares or replacement parts.

### Reliability, Availability and Maintainability (RAM)

The Employer regards reliability, availability, maintainability, and accessibility of its generating units of prime importance. The Contractor performs reliability, availability, and maintainability (RAM) studies on the complete design (including electrical and C&I systems) of the works. The emphasis is on providing simple, properly engineered control strategies and inherently reliable systems where faults can be quickly located and repaired.

All these studies/analyses are to be submitted to the Project Manager for acceptance.

The Contractor utilises the following specifications as inputs into the design and RAM model developed by the Contractor.

#### Reliability

The works is designed and configured for the following reliability:

All Plant and Materials in the works are designed for operation in a power station environment with a minimum requirement for maintenance and operator attention. The system and equipment temperatures and operation is stable over the full load range for all boiler equipment.

All parts, including electrical and process control components, are of the class most suitable and designed for working under local operating conditions, and designed in accordance with the local applicable codes.  All parts function without distortion or deterioration or the setting up of undue strains in any parts, such as to affect the efficiency and reliability of the works.

All Plant and Materials supplied are designed with due regard to the need for satisfactory operation under such sudden variations of furnace draught as may be encountered during the operation of the plant including start-up, load follow, full load, and shutdown.

Compressors are designed for long life with minimal maintenance.

The Plant and Materials are designed using components with mean time between failures (MTBF) and mean time to repair (MTTR) that meet or exceed internationally published data and guidelines (Contractor is to provide suitable references). Based on the above requirements the system and the individual sub-systems do not have more than two (2) failures (complete generating unit shut down) during the six (6) year operation period between general outages.

No individual C&I fault or no two (2) concurrent faults endanger the safety of the plant or people, or jeopardize the integrity of major plant.

No individual C&I fault is to cause a load loss more than once in a year, per unit.

The C&I design provides for independence, junction boxes, cabling and control modules are structured and designed to ensure the separation between functions and hardware between the RH and LH casing’s systems units.

No individual C&I fault is to cause a multi-unit trip.

No individual fault is to cause a system loss of the operator information or control system for the operator.  No loss of information for operator observation, control or data logging.

#### Availability

The Contractor configures the works and associated control system to meet the availability described below including provisions for on-line maintenance or replacement of equipment and components.

The system is considered unavailable when the failure impacts the correct operation of the functional elements of the works. Therefore the time dependent inherent and operational availability of the complete works will be established.

The inherent availability of the works consisting of the individual sub-systems over its life, in percentage of time, is 98% or greater. Each subsystem has an inherent availability, in percentage of time, of 98% or greater. The availability study takes into account the impact of planned and unplanned maintenance.

The Contractor configures the works control system to minimize the effects of equipment failure on the overall plant and mimics the mechanical plant configuration. Field device availability matches that of the control system, so that it does not constitute a weak link.

Access to field equipment does not require shutdown of plant or operational limitations to perform maintenance.

#### Maintainability

The maintainability of the works conforms to the following requirements adhered to by the Contractor:

The maintenance of the systems is possible within the existing maintenance structures.

The system is configured such that it supports on-line maintenance.

The Contractor establishes a suitable maintenance regime and maintenance philosophies and manuals. These are provided for the works by the Contractor.

All similar items of the works and all similar wearing parts and components are interchangeable to the extent possible. This is to ensure that the replacement of a complete unit or of a worn or damaged part can be carried out with a minimum of fittings and a minimum of spares stock holding.

Where possible, auxiliary plant components such as motors are designed for the same duty, without compromising the design intent, and with maximised efficiencies (SANS 60034-30) in order to reduce the number of essential spares that are stocked.

The works are designed with due regard to the need for safe and easy access, monitoring, inspection, frequent cleaning and repair.

All inspection and maintenance access in the form of ladders / platforms are provided with due regard to safety of personnel, and in accordance with applicable safety standards (OSH Act 85).

The Contactor as a minimum ensures that there is permanent access to any area where Plant and Materials is manually operated by an operator.

Design is consistent with existing scheduled unit / equipment shutdown frequencies and durations.

Design includes Plant and Materials for plant access / monorails / cranes / other lifting equipment.

All Plant and Materials monitoring provisions (e.g.vibrations monitoring) is provided.

Compatibility of maintenance philosophy for new systems and equipment with existing use and maintenance philosophy.

Coordination of the project with any maintenance projects.

Note: For maintainability purposes, hotline swapping of processor and communications modules is included in the Contractors design.

#### Reliability, Availability and Maintainability (RAM) Studies

These studies are in accordance to 240-49230111, 240-49230046, as well as 240-49230030 and 240-49230100.

Detailed RAM (reliability, availability and maintainability) studies of the complete system and subsystems for the works are performed in order to meet the requirements in the section above.  All Plant and Materials, including electrical and C&I, are included.

These studies are to be submitted by the Contractor to the Project Manager for acceptance

The objectives of these studies are to achieve the following:

Predicting the availability, reliability, throughput, and sensitivity of each subsystem and the complete system

Determining the optimized maintenance philosophy for the systems and equipment making up the complete system

Performing redundancy studies on the systems

Using the above studies to optimise the system spares holding

Essential to the above process is the construction of an ABD (availability block diagram) of the system and forms part of the RAM study.  The overall works ABD shows the interconnections between all subsystems and equipment for each of the subsystems making up the system.  All redundancies are shown.

The VisualSPAR latest version reliability simulation software package is used in performing the RAM analysis.

The following is supplied by the Contractor to the Project Manager:

All RAM documentation including all assumptions, as well as the operating and maintenance philosophy for the complete system in the works.  The report includes all the models, model results, programming logic flow-charts, plant design down to equipment level.

A presentation of the results

Detailed RAM models and programming logic flow-charts per the VDSS. The Contractor presents the RAM models and documentation, in draft format for comment, to the Project Manager two (2) weeks prior to compiling the final RAM assessment and package.

Process description of the system and subsystems.

Availability, reliability, throughput and sensitivity analysis of the system and the subsystems derived from the model output. The reason and mitigation for high sensitive components as derived from the model is also provided. The actual logic to determine these parameters must be programmed in the bubble logic.

Optimised maintenance philosophy as specified in 3.8.2 for the systems and equipment. Aging of equipment is taken into account. The “probabilistic ageing” feature of the VisualSPAR model is used and the process taken to arrive at the optimised maintenance philosophy is also shown.

ABD’s of the complete system and subsystems in the works, in order to achieve the objectives described above. The ABD shows the interconnections between the equipment of the systems and subsystems concerned.

The complete ABD model’s software logic (all VisualSPAR input files, bubble logic files and output files) – i.e. the actual ABD VisualSPAR latest version software models. The ABD models and software logic is provided by the Contractor, as part of the works, and is supplied in their entirety and is sufficient for the Employer to replicate or re-create all the ABD calculations and models using only the VisualSPAR latest version software.

MTTF (mean time to failure) for each type of equipment provided as part of the works and the type of failure distribution i.e. exponential or weibull.

MTTR (mean time to repair) or MDT (mean down time) for each type of equipment provided as part of the works.

Optimised spares holding for the complete system using the VisualSPAR optimizer (SPARopt) tool to optimise the system spares holding.  Costs and availability targets are considered as well as the process taken to arrive at the optimised spares holding are shown

#### Maintenance Philosophy

The maintenance philosophy applicable is a combination of time-based maintenance as well as condition-based maintenance. All maintenance practices happen within the Employer regulations frame work. Routine maintenance practices are based on the original equipment manufacturer’s specifications and recommendations. It is the Employer’s intention to adopt an absolute minimum spares holding philosophy for the plants. Therefore it is a requirement that a full list of critical strategic spares be provided by the Contractor as per section 3.8.2.1.

The FMEA analysis assists in establishing what type of preventative maintenance task is done (if any). This is done by considering all the functional failures of the plant and the applicable failure modes. Each functional failure and applicable failure mode are analysed. From this an applicable and effective preventative maintenance task is identified for the component (if any).

Each preventative maintenance task and interval is included in the VisualSPAR RAM model. The preventative maintenance tasks are correctly handled in VisualSPAR by taking into account the Plant and Materials downtime and re-setting the ages of the components. The ages of the components following the preventative maintenance task are set as appropriate and may not be necessarily be “as good as new”. Different preventative maintenance intervals are tested in the VisualSPAR model.  Cost and plant downtimes are compared for the different scenarios and the most effective interval established.  The re-setting of the component ages following the preventative maintenance tasks is performed in the VisualSPAR bubble.

As a result of the VisualSPAR simulation, a comprehensive list of maintenance activities, typically maintenance cycles resource requirements (including spares required) and associated timeframes are included.  Categorisation of outages is provided as part of the Contractors scope of work.

### Technical Risk Assessments

The Contractor performs HAZOP Studies, and failure mode, effects and criticality analysis (FMCEA) on the complete design (including electrical and C&I systems) of the works. The emphasis is on providing simple, properly engineered control strategies and inherently reliable systems where faults can be quickly located and repaired.

All these studies/analyses are to be submitted to the Project Manager for acceptance.

#### Failure Mode Effects and Analysis (FMEA)

Formal failure mode effects analysis (FMEA) studies are carried out on all systems. These studies are done (during detail design phase) in accordance with the requirements as laid down in the Employer’s FMEA Guideline: 240-49230046.

These studies are submitted to the Project Manager for acceptance.

#### Hazard and Operability Studies

Formal hazard and operability (HAZOP) studies are carried out, by the Contractor, on all systems. These studies are done (HAZOP four (4) are conducted in detail design phase post contract award) in accordance with the requirements as laid down in the Employer’s HAZOP Guideline: 240-49230111.

These studies are to be submitted to the Project Manager for acceptance.

# List of drawings

## Drawings issued by the Employer

This is the list of drawings issued by the Employer which apply to this contract.

Note:  Some drawings may contain both Works Information and Site Information.

| Drawing number | Revision | Title |
| --- | --- | --- |
| 0.61/2 | 18 | Tutuka Power Station Layout |
| 0.61/8991 | 3 | Tutuka Power Station Dust Hoppers |
| 0.61/3648 | 6 | Fly Ash Bunker - Sections and Elevations |
| 0.61/3650 | 9 | Fly Ash Bunker - Roof, Ground Floor - Concrete Detail and Sections |
| 0.61/8715 | 2 | Tutuka Power Station Concrete Details to Roof Stab, Precast Roof Beams and Support Beams for Bucket Elevators Fly ash Bunker No 1 |
| 0.61/13814 | 1 | Tutuka Power Station Concrete Details to Roof Stab, Precast Roof Beams and Support Beams for Bucket Elevators Fly ash Bunker No 2 & 3 |
| 0.61/13816 | 0 | Tutuka Power Station Concrete Details to Roof Stab, Precast Roof Beams and Support Beams for Bucket Elevators Fly ash Bunker No 2 & 3 |
| 0.61/7779 | 0 | Boiler 1 Dust Handling Plant General Arrangement Plan |
| 0.61/7780 | 0 | Boiler 1 Dust Handling Plant General Arrangement Plan |
| 0.61/7781 | 0 | Boiler 1 Dust Handling Plant General Arrangement Elevation and Sections |
| 0.61/7782 | 0 | Boiler 1 Dust Handling Plant General Arrangement Sections |
| 0.61/7783 | 0 | Boiler 1 Dust Handling Plant General Arrangement Plan and Elevations |
| 0.61/7777 Sheet 1 | 1 | Dust Handling Plant Conveyors Civil Supports Arrangement and Details Sheet 1 |
| 0.61/7778 Sheet 2 | 1 | Dust Handling Plant Conveyors Civil Supports Arrangement and Details Sheet 2 |
| 0.61/23067 | 0 | Tutuka Power Station Plan on Dust Handling plant – Under Precips A5 and B5 |
| 0.61/24418 | 0 | Tutuka Power Station Plan on Dust Handling plant – Under Six Precips A and B |
| 0.61/24419 | 0 | Tutuka Power Station Unit 6 – Elevations on North of Precipitators A & B Showing Also Dust Handling Cable Racking |
| 0.61/9303 | 0 | Dust Handling Plant Precipitator Conveyor Steelwork and Walkways Arrangement |
| 0.61/9304 | 0 | Dust Handling Plant Precipitator Conveyor Steelwork and Walkways 5-8 Arrangement and Details |
| 0.61/9305 | 0 | Dust Handling Plant Precipitator Conveyor Steelwork and Walkways Elevation and Section |
| 0.61/9306 | 0 | Dust Handling Plant Elevator Pit Structural Steelwork Details |
| 21/.61/54801 | 0 | Tutuka Power Station Unit 6 East ESP Dry Ash Discharge Conveyor System P&ID |
| 0.61/57586 | 0 | Tutuka Power Station Electrostatic Precipitator Dry Ash Conveyor & Bucket Elevator System P&ID |
| 0.61/12063 | 1 | Dust Handling Plant Boilers 1 And 2 Elevator Support Guide Bracket Cast In Plates Details |
| 0.61/12064 | 0 | Dust Handling Plant Boilers 3-6 Elevator Support Guide Bracket Cast In Plates Details |
| 0.61/9318 Sheet 1 | 3 | Boiler 1 Dust Handling Plant Elevator Support Steelwork General Arrangement and Details |
| 0.61/9319 | 0 | Dust Handling Plant Elevator Boiler 1 Support Structural Steelwork Details |
| 0.61/9320 | 0 | Dust Handling Plant Elevator Guide Frames Boiler 1 Support Structural Steelwork Details |
| 0.61/56646 Sheet 1 | 2 | Fly Ash Bunker 1-3 3 Tonne Crawl Beams At Bunker Roof (+1657,900 Level) Plinth Concrete, Reinforcement Details and Schedule |
| 0.61/56646 Sheet 2 | 2 | Fly Ash Bunker 1 3 Tonne Crawl Beams at Bunker Roof (+1657,900 Level) General Arrangement |
| 0.61/54997 | 0 | Tutuka Power Station Ash Handling Plant Section Through Conditioner |
| 0.61/56665 | 0 | Tutuka Power Station Ash Handling Plant General Arrangement of Ash Conditioners |
| 0.61/55955 | 0 | Tutuka Power Station Ash Handling Plant Existing Position of Conditioners General Arrangement |
| 0.61/23527 Sheet 1 | 1 | Tutuka Power Station General Arrangement of Ash Conditioner Bunker No. 1 |
| 0.61/23527 Sheet 2 | 0 | Tutuka Power Station General Arrangement of Ash Conditioner Bunkers No. 2 & 3 |
| 0.61/17901 | 2 | Tutuka Power Station G.A. of Conditioner Water Feed System Boiler 1 & 2 |
| 0.61/14016 | 2 | Tutuka Power Station G.A. of Crawl Beams for Ash Conditioning Plant |
| 0.61/57665 | 0 | Tutuka Power Station Bunker 2A Conditioner 3A Dry Storage System P&ID |
| 0.61/57592 | 0 | Tutuka Power Station Bunker 1B Conditioner 2B Dry Storage System P&ID |
| 0.61/57664 | 0 | Tutuka Power Station Bunker 2B Conditioner 4B Dry Storage System P&ID |
| 0.61/54812 | 0 | Tutuka Power Station Bunker 3B Conditioner 6B Dry Storage System P&ID |
| 0.61/54813 | 1 | Tutuka Power Station Bunker 3A Conditioner 5A Dry Storage System P&ID |
| 21.61/55241 Sheet 1 | 1 | Tutuka Power Station Common Plant Ash Conditioning Effluent Water System P&ID Sheet 1 |
| 21.61/55241 Sheet 2 | 2 | Tutuka Power Station Common Plant Ash Conditioning Effluent Water System P&ID Sheet 2 |
| 0.61/55242 | 0 | Tutuka Power Station Common Plant Ash Conditioner Water Supply P&ID |
| 0.61/55242 | 3 | Tutuka Power Station Common Plant Ash Conditioner Water Supply P&ID |
| 0.61/55957 | 0 | Tutuka Power Station Ash Handling Plant Water & Air Supply to Conditioners |
| 21.61/55309 | 0 | Tutuka Power Station Common Plant Ash Heater Washing System P&ID |
| 21.61/54505 | 1 | Tutuka Power Station Common Plant Feedwater Makeup Storage and Reticulation System P&ID |
| 0.61/54822 | 1 | Tutuka Power Station Units 1-6 Fly Ash Aeration System P&ID |
| 0.61/13586 | 1 | Tutuka Power Station G.A. Aeration System in Bunker for Boilers 1 - 6 |
| 0.61/17899 | 5 | Tutuka Power Station General Arrangement of Fly Ash bunker Aeration Pipework unit 1 |
| 0.61/1119 Sheet 2 | 10 | Tutuka Power Station Station Cable Servitudes |
| 0.61/1119 Sheet 13 | 2 | Tutuka Power Station Unit 1 I.D. Fans, Cable Tunnel & Trenches Layout |
| 0.61/1119 Sheet 15 | 1 | Tutuka Power Station Unit 2 I.D. Fans, Cable Tunnel & Trenches Layout |
| 0.61/1119 Sheet 16 | 0 | Tutuka Power Station Unit 3 I.D. Fans, Cable Tunnel & Trenches Layout |
| 0.61/1119 Sheet 17 | 0 | Tutuka Power Station Unit 4 I.D. Fans, Cable Tunnel & Trenches Layout |
| 0.61/1119 Sheet 18 | 0 | Tutuka Power Station Unit 5 I.D. Fans, Cable Tunnel & Trenches Layout |
| 0.61/1119 Sheet 19 | 0 | Tutuka Power Station Unit 6 I.D. Fans, Cable Tunnel & Trenches Layout |
| 0.61/1119 Sheet 21 | 0 | Tutuka Power Station Bulk Oil And Lighting Up Plant East Cable Tunnel and Trench Layout |
| 0.61/16341 | 3 | Tutuka Power Station Ash Bunkers 2 & 3 Access to South Face Staircase |
| 0.61/19155 | 0 | Tutuka Power Station Fly Ash Bunkers No 2 & 3 Details of Stairways - External |
| 0.61/19156 | 0 | Tutuka Power Station Fly Ash Bunkers No 2 & 3 Details of Stairways- Internal |
| 0.61/19170 | 1 | Tutuka Power Station Fly Ash Bunker No 2 Platform for Conditioner Floor |
| 0.61/19171 | 1 | Tutuka Power Station Fly Ash bunker No 2 Details of Staircase Trestles Conditioner Floor |
| 0.61/8658 | 4 | Tutuka Power Station Fly Ash Bunker No 1 Details of Stairways – External |
| 0.61/8662 | 3 | Tutuka Power Station Fly Ash Bunkers No 1 Details of Stairways- Internal |
| 0.61/10310 Sheet 1 | 8 | Tutuka Power Station Ash Handling System Details of Steelwork for Conditioner Conveyors |
| 0.61/13276 Sheet 1 | 7 | Tutuka Power Station Ash Handling System General Arrangement of Conditioner Conveyors. |
| 0.61/96245 Sheet 1 | 0 | Tutuka Power Station Fabric Filter Plant Compressor Room and ID Fan Area GPR Scan Results with Reflections |
| 0.61/96245 Sheet 2 | 0 | Tutuka Power Station Fabric Filter Plant Compressor Room and ID Fan Area GPR Scan Results Without Reflections |
| 0.61/10145 Sheet 1 | 14 | Tutuka Power Station Ash Handling System General Arrangement of Transverse Conveyors Stage 1 |
| 0.61/17427 Sheet 1 | 3 | Tutuka Power Station Ash Handling System General Arrangement of Transverse Conveyors Stage 2 |
| 0.61/20009 Sheet 1 | 3 | Tutuka Power Station Ash Handling System General Arrangement of Transverse Conveyors Stage 4 |
| 0.61/20011 Sheet 1 | 3 | Tutuka Power Station Ash Handling System General Arrangement of Transverse Conveyors Stage 5 |
| 0.61/20013 Sheet 1 | 3 | Tutuka Power Station Ash Handling System General Arrangement of Transverse Conveyors Stage 6 |
| 0.61/37092 Sheet 1 | A | Tutuka Power Station Ash Handling System General Arrangement of Transverse Conveyors |
| 0.61/37113 Sheet 1 | 2 | Tutuka Power Station Ash Handling System General Arrangement of Transfer House TT01 |
| 21.61/55242 | 3 | Tutuka Power Station Ash Handling Plant Common Plant Ash Conditioner Water Supply System P&ID |
| 0.61/96022 | 5 | Tutuka Power Station Fly Ash Handling Plant FFP and DHP Layout Requirements |
| 0.61/96025 | 2 | Tutuka Power Station Dust Handling Plant P&ID |
| 0.61/96023 | 2 | Tutuka Power Station Dust Handling Plant Pipe Routing |
| 0.61/96026 | 3 | Tutuka Power Station Dust Handling Plant Discharge to Fly Ash Bunker P&ID |
| 0.61/96075 | 1 | Tutuka Power Station Dust Handling Plant Bunker * Conditioners *A and *B Dry Dust Storage System P&ID |
| 0.61/96078 | 0 | Tutuka Power Station Dust Handling Plant Fly Ash Bunker Conditioning Floor Layout |
| 0.61/96061 | 1 | Tutuka Power Station Dust Handling Plant Ash Hopper Aeration Air Piping & Instrumentation Diagram |
| 0.61/96027 Sheet 1 | 0 | Tutuka Power Station Dust Handling Plant Units 1-6 Pneumatic Conveying Air System Sheet 1 |
| 0.61/96027 Sheet 2 | 0 | Tutuka Power Station Dust Handling Plant Pneumatic Conveying Air System Sheet 2 |
| 0.61/96027 Sheet 3 | 0 | Tutuka Power Station Dust Handling Plant Pneumatic Conveying Air System Sheet 3 |
| 0.61/96027 Sheet 4 | 0 | Tutuka Power Station Dust Handling Plant Pneumatic Conveying Air System Sheet 4 |
| 0.61/96027 Sheet 5 | 0 | Tutuka Power Station Dust Handling Plant Units 1-6 Pneumatic Conveying Air System Sheet 5 |
| 0.61/96027 Sheet 6 | 0 | Tutuka Power Station Dust Handling Plant Pneumatic Conveying and Instrument Compressor Cooling System P&ID |
| 0.61/96028 Sheet 1 | 0 | Tutuka Power Station Dust Handling Plant Units 1-6 Instrument Air System Sheet 1 |
| 0.61/96028 Sheet 2 | 0 | Tutuka Power Station Dust Handling Plant Instrument Air System Sheet 2 |
| 0.61/96028 Sheet 3 | 0 | Tutuka Power Station Dust Handling Plant Units 1-6 Instrument Air System Sheet 3 |
| 0.61/96083 | 0 | Tutuka Power Station Dust Handling Plant Blower House Elevation Views |
| 0.61/97161 | 0 | Field Alterations Tutuka Unit 6 FFP Casings A & B PJFF Hopper Modifications Sections & Views |
| 0.61/97200 Sheets 1 to 2 | 0 | Tutuka Power Station FFP and DHP Compressor House HVAC P&ID |
| 0.61/97205 Sheets 1 to 40 | 0 | Tutuka Power Station FFP and DHP Compressor House |
| 0.61/57566 | 0 | Unit 4 East Fuel Oil Pump House System Piping and Instrumentation Diagram |
| 0.61/57567 | 0 | Unit 4 Fuel Oil Supply To Burners System Piping and Instrumentation Diagram |
| 0.61/14473 | 2 | Tutuka Power Station Part Layout of Fuel Oil Line System From Tanks To Boilers |
| 0.61/22965 | 0 | Tutuka Power Station Boilers 4-6 Fuel Oil Pipeline Support Bridge at Precipitators Details Part A |
| 0.61/22966 | 0 | Tutuka Power Station Boilers 4-6 Fuel Oil Pipeline Support Bridge at Precipitators Details Part B |
| 0.61/93922 | 1 | Tutuka Power Station MV & LV Electric Diagram |
| 0.61/1703 | 8 | Tutuka Power Station Unit 1 LV Electric Diagram |
| 0.61/96067 | 0 | Tutuka Power Station Unit 3 LV Electric Diagram |
| 0.61/96069 | 0 | Tutuka Power Station Unit 5 LV Electric Diagram |
| 0.61/21138 | 4 | Tutuka Power Station G.A. of Venting from Bunker to Precipitator Inlet Ducts |
| 0.61/97384 | 0 | Tutuka Power Station Unit Hopper Aeration Blower House Building Site Layout |
| 0.61/96029 Sheet 1 | 3 | Tutuka Power Station Unit 1 Hopper Aeration Blower House Building Floor Plan |
| 0.61/96029 Sheet 2 | 2 | Tutuka Power Station Unit1 Hopper Aeration Blower House Sections A-A and BB |
| 0.61/96.29 Sheet 3 | 3 | Tutuka Power Station Unit 1 Hopper Aeration Blower House Building Elevations |
| 0.61/96029 Sheet 3 | 1 | Tutuka Power Station Unit 1-6 Hopper Aeration Blower House Door Schedule and Door D2 Details |
| 0.61/97936 | 0 | Tutuka Power Station Unit 2 Hopper Aeration Blower House Building Floor Plan |
| 0.61/97936 | 0 | Tutuka Power Station Unit 2 Hopper Aeration Blower House Sections A-A and BB |
| 0.61/97936 | 0 | Tutuka Power Station Unit 2 Hopper Aeration Blower House Building Elevations |
| 0.61/97937 | 0 | Tutuka Power Station Unit 3 Hopper Aeration Blower House Building Floor Plan |
| 0.61/97937 | 0 | Tutuka Power Station Unit 3 Hopper Aeration Blower House Sections A-A and BB |
| 0.61/97937 | 0 | Tutuka Power Station Unit 3 Hopper Aeration Blower House Building Elevations |
| 0.61/97938 | 0 | Tutuka Power Station Unit 4 Hopper Aeration Blower House Building Floor Plan |
| 0.61/97938 | 0 | Tutuka Power Station Unit 4 Hopper Aeration Blower House Sections A-A and BB |
| 0.61/97938 | 0 | Tutuka Power Station Unit 4 Hopper Aeration Blower House Building Elevations |
| 0.61/97939 | 0 | Tutuka Power Station Unit 5 Hopper Aeration Blower House Building Floor Plan |
| 0.61/97939 | 0 | Tutuka Power Station Unit 5 Hopper Aeration Blower House Sections A-A and BB |
| 0.61/97940 | 0 | Tutuka Power Station Unit 5 Hopper Aeration Blower House Building Elevations |
| 0.61/97940 | 0 | Tutuka Power Station Unit 6 Hopper Aeration Blower House Building Floor Plan |
| 0.61/97940 | 0 | Tutuka Power Station Unit 6 Hopper Aeration Blower House Sections A-A and BB |
| 0.61/97940 | 0 | Tutuka Power Station Unit 6 Hopper Aeration Blower House Building Elevations |
| 0.61/97393 Sheet 1 | 0 | Tutuka Power Station Units 1-6 Hopper Aeration Blower House Building General Arrangement of Steelwork |
| 0.61/97393 Sheet 2 |  | Tutuka Power Station Units 1-6 Hopper Aeration Blower House Building Crawl Beam Steelwork |
| 0.61/97393 Sheet 3 | 0 | Tutuka Power Station Units 1-6 Hopper Aeration Blower House Building Structural Steelwork Connections |
| 0.61/97393 Sheet 4 | 0 | Tutuka Power Station Units 1-6 Hopper Aeration Blower House Building Concrete Floor Slab and Beams Layout |
| 0.61/97393 Sheet 5 | 0 | Tutuka Power Station Units 1-6 Hopper Aeration Blower House Building Concrete Substructure Elevations and Sections |
| 0.61/97393 Sheet 6 | 0 | Tutuka Power Station Units 1-6 Hopper Aeration Blower House Building Foundation Layout Elevations and Reinforcement Details |
| 0.61/97393 Sheet 7 | 0 | Tutuka Power Station Units 1-6 Hopper Aeration Blower House Building Floor Slab, Beams and Columns Reinforcement |
| 0.61/97393 Sheet 8 | 0 | Tutuka Power Station Units 1-6 Hopper Aeration Blower House Building Bending Schedules |
| 0.61/97172 Sheet 1 | 2 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Plan lvl -0.595 & 0.000 |
| 0.61/97172 Sheet 2 | 2 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Plan lvl +2.125 & 3.570 |
| 0.61/97172 Sheet 3 | 2 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Sections and Roof Plan |
| 0.61/97172 Sheet 4 | 2 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Elevations East and West |
| 0.61/97172 Sheet 5 | 2 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Elevations North and South |
| 0.61/97172 Sheet 6 | 2 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Finishes; Window and Door Schedules |
| 0.61/97400 Sheet 1 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Column Foundations – Layout and Details |
| 0.61/97400 Sheet 2 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Wall Foundations – Layout and Details |
| 0.61/97400 Sheet 3 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Ground Slabs, Plinths and Trenches - Layout |
| 0.61/97400 Sheet 4 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Slabs at 2.125m; 3.57m; 6.705m - Layout |
| 0.61/97400 Sheet 5 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Beams at 5.695 Level Concrete Layout and Details |
| 0.61/97400 Sheet 6 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Concrete Layout at +8.650m Level Girder and Portal Frame Connections |
| 0.61/97400 Sheet 7 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House General Arrangement of Steelwork Roof Plan |
| 0.61/97400 Sheet 8 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House General Arrangement of Steelwork East and West Elevations |
| 0.61/97400 Sheet 9 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House General Arrangement of Steelwork North and South Elevations |
| 0.61/97400 Sheet 10 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House General Arrangement of Steelwork Sections and Details |
| 0.61/97400 Sheet 11 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Structural Steelwork Connection Details |
| 0.61/97400 Sheet 12 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Crane Maintenance Access Platform General Arrangement and Details |
| 0.61/97400 Sheet 13 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Access Staircase Type 1 Details |
| 0.61/97400 Sheet 14 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Access Staircase Type 2 & 3 Details |
| 0.61/97400 Sheet 15 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House – Grid Lines C-E x13.1-14.1 Platform AT +2.075m |
| 0.61/97400 Sheet 16 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House – Ramp at Southern Entrance – Layout and Details |
| 0.61/97400 Sheet 17 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House – Ground Slabs Joint Layout and Details |
| 0.61/97400 Sheet 18 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Engineering drawings 1 |
| 0.61/97400 Sheet 19 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Engineering drawings 1 |
| 0.61/97400 Sheet 20 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Engineering drawings 3 |
| 0.61/97400 Sheet 21 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Engineering drawings 4 |
| 0.61/97400 Sheet 22 | 0 | Tutuka Power Station Fabric Filter Plant Pulse Air and Dust Handling Plant Compressor House Water Tower General Arrangement and Details |
| 0.61/3200 | 12 | Tutuka Power Station Standard Pipe Diagram and C&I Diagram Symbols |
| 0.61/5299 | 8 | Tutuka Power Station Fire Control Pump House Schematic Diagram |
| 0.61/9095 | 2 | Tutuka Power Station Fire Control Pump House Layout |
| 0.61/9264 | 10 | Tutuka Power Station Schematic Diagram of Fire Control Systems and Associate Services |
| 0.61/10563 | 3 | Tutuka Power Station Ra Water & Potable Water Supplies To Fire Control Pump House, Layout & Sections |
| 0.61/1101 | 4 | Tutuka Power Station Survey Beacon Setting Out |

# Appendix A – Required Deliverable for the Contractor

The Contractor is to complete and submit the following table to the Employer with the Contractors tender submission. The Contractor is to include all reference documentation that is required by questions in the table below.

| Required Deliverable Number | Required Deliverable from the Contractor | Deliverable Answer or Supporting Document Submitted? (Yes/No) | Supporting Document Reference Number, if applicable |
| --- | --- | --- | --- |
| 1. | The Contractor supplies a reference list (including as a minimum: client, contact details of client, commissioning date, capacity and location) indicating the Contractors capability and experience in the complete design, construction and commissioning of a En-Massa conveying system for power station fly ash, with a capacity of more than 80 Tph , operating for a period of more than 1 year. |  |  |
| 2. | The Contractor supplies a reference list (including as a minimum: client, contact details of client, commissioning date, capacity and location) indicating the Contractors capability and experience in the complete design, construction and commissioning of an ash conditioner system, with a conditioning capacity of at least 200 Tph (wet) per conditioner, operating for a period of more than 1 year. |  |  |
| 3. | Does the Contractor have or will have access to an En-Massa conveying test facility where the En-Massa conveying characteristics of fly ash can be determined? |  |  |
| 4. | Does the Contractor have or will have access to the En-Massa conveying characteristics of a typical “South African” fly ash? |  |  |

# Appendix B – Vendor Document Submittal Schedule (VDSS)

# Appendix C – Limits of Supply and Services (LOSS)

# Appendix D – Employers RBO Template

# Appendix E – Applicable Standards

The Contractor applies the latest versions of the following codes and standards unless a particular version is specified below.

| Standard Number | Revision | Title |
| --- | --- | --- |
| 240-57859210 | 1 | Alarm system performance of digital control systems for fossil plant standard |
| 240-56355535 | 1 | Process calibration equipment standard |
| 240-56355728 | 1 | Human Machine Interface Design requirements standard |
| 240-56355754 | 1 | Field instrument installation standard |
| 240-56355815 | 1 | Field instrument installation standard: Junction boxes and cable termination |
| 240-56355843 | 1 | Pressure measurement systems installation standard |
| 240-56355888 | 1 | Temperature measurement systems installation standard |
| 240-56737654 | 2 | Inspection testing and maintenance of fire detection systems |
| 240-89147446 | 1 | Instrument piping for fossil and hydro power plant standard |
| SSZ 45-17 | 2 | Medupi Power Station Corrosion Protection Specification |
| 240-61227631 | 1 | Piping and Instrumentation Diagram Standard |
| 240-86973501 | 1 | Engineering Drawing Standard - Common Requirements |
| 240-53113685 | 2 | Design Review Procedure |
| 240-53114026 | 2 | Project Engineering Change Management Procedure |
| 240-66920003 | 1 | Documentation Management Review and Handover Procedure |
| 32-6 | 1 | Eskom Document and Record Management Procedure |
| 240-54937439 | 2 | Fire Protection/Detection Assessment Standard |
| 240-56737448 | 2 | Fire Detection and Life Safety Design Standard |
| 240-54937450 | 2 | Fire Protection & Life Safety Design Standard |
| 240-54937454 | 2 | Inspection Testing and Maintenance of Fire Protection Systems Standard |
| 240-49230111 | 1 | Hazzard and Operability Analysis Guideline |
| 240-49230046 | 2 | Failure Mode and Effect Analysis Guideline |
| 240-49230030 | 2 | Reliability Engineering Analysis Guideline |
| 240-49230100 | 1 | Safety Engineering Analysis Guideline |
| 240-53113666 | 1 | Medium Power Transformers Used in Power Stations Standard |
| 240-55714363 | 1 | Small power and lighting Coal Fired power station installation standard |
| 240-56176852 | 1 | Essential Power Supplies for Power Stations Standard |
| 240-56227443 | 1 | Requirements for Control and Power Cables for Power Stations Standard |
| 240-56227516 | 1 | LV Switchgear and Control Gear Assemblies and Associated Equipment for Voltage up to and Including 1000V AC and 1500V Standard |
| 240-56356396 | 1 | Earthing and Lightning Protection Standard |
| 240-56357424 | 1 | MV and LV Switchgear Protection Standard |
| 240-57617975 | 1 | Procurement of Power Station Low Voltage Motors Specification |
| 240-53114248 | 2 | Thyristor and Switch Mode Chargers, AC/DC to DC/AC Converters and Inverter/Uninterruptible Power Supplies Standard |
| 240-56360086 | 1 | Stationary Vented Nickel Cadmium Batteries Standard |
| 240-56247004 | 1 | Thermal Insulation Standard |
| 240-56246601 | 2 | Qualification, Certification and Accreditation Requirements for Personnel and Entities Performing Welding Related Work on Eskom Plant Standard |
| 240-72273656 | 1 | Power Generation Asset Criticality Classification Standard |
| 240-56241933 | 2 | Control of Welding during Construction, Repairs and Maintenance Activities Standard |
| 240-56241639 | 2 | Construction and Repair Welding of Primary Air, Induced and Forced Draught Fans Standard |
| 240-56355225 | 2 | Welding of High Pressure Temperature Tube and Pipework Standard |
| 240-77196678 | 1 | Heat Treatment of Welded Components Standard |
| 240-62937990 |  | Tutuka AKZ Plant Labelling Guideline |
| 240-56355466 | 1 | Alarm Management System Guideline |
| SANS 121 |  | Hot dip galvanized coatings on fabricated iron and steel articles - Specifications and test methods |
| SANS 62-1 |  | Steel pipes Part 1: Pipes suitable for threading and of nominal size not exceeding 150 mm |
| SANS 347 |  | Categorization and conformity assessment criteria for all pressure equipment |
| SANS 719 |  | Electric welded low carbon steel pipes for aqueous fluids (large bore) |
| SANS 1123 |  | Pipe Flanges |
| SANS 1200 D |  | Standardized specification for civil engineering construction Section D: Earthworks |
| SANS 10400 (All Parts) |  | The application of the National Building Regulations |
| SANS 10139 |  | Fire detection and alarm systems for buildings - System design, installation and servicing |
| SANS 1186 |  | Symbolic safety signs |
| SANS 10105 |  | The use and control of fire-fighting equipment |
| SANS 60034-30 |  | Rotating electrical machines Part 30: Efficiency classes of single-speed, three-phase, cage-induction motors (IE-code) |
| SANS 1424 |  | Filters used in General Air-Conditioning |
| SANS 1238 |  | Air Conditioning Ductwork |
| SANS 10142-1 |  | The wiring of premises Part 1: Low-voltage installations |
| SANS 10173 |  | Installation, Testing and Balancing of Air-conditioning Ducting |
| SANS 10147 |  | Refrigeration Code |
| SANS 1287-1 |  | Ventilation brattices and ducting Part 1: Flexible ducting |
| SANS 1287-2 |  | Ventilation brattices and ducting Part 2: Brattices, unsupported |
| ISO 11650 |  | Performance of refrigerant recovery and/or recycling equipment |
| SANS 204 |  | Energy Efficiency in Buildings |
| SANS 10140 |  | Identification colour markings |
| SANS 1091 |  | National Colour Standard |
| Occupational Health and safety |  | Act (Act No. 85 of 1994) as amended |
| National Health |  | Act, 2004 (Act No. 61 of 2003) |
| VGB R171, | 2010 Edition 2 | Guideline for the Supply of Technical Documentation for Fossil-Fired and Regenerative Power Stations |
| VGB R170 B(0-6)e |  | Design standards for instrumentation and control equipment. |
| VGB R170 C |  | Function related documentation of power plant instrumentation and control in line with operating requirements |
| ISO 10007 |  | Guideline for Configuration Management |
| ISO 9001 |  | Quality Management System – Requirements |
| ISO 5167 |  | Measurement of fluid flow by means of pressure differential devices inserted in circular cross-section conduits running full |
| ISO 11650 |  | Performance of refrigerant recovery and/or recycling equipment |
| ASHRAE G1 |  | Guideline for Commissioning Air Conditioning Systems |
| ASHRAE 62 |  | American Society of Heating Refrigeration and Air Conditioning Engineers. Ventilation for acceptable indoor air quality |
| ASHRAE 52/76 |  | Standard Test Method for filters |
| CIBSE Commissioning Codes A |  | Air Distribution |
| CIBSE Commissioning Codes C |  | Automatic Controls |
| CIBSE Commissioning Codes R |  | Refrigeration Systems |
| ASME BPVC |  | Boiler and Pressure Vessel Code |
| NFPA 850 |  | Recommended Practice for Fire Protection for Electric Generating Plants and High Voltage Direct Current Converter Stations |
| AWS D1.1 |  | Structural welding code – steel |
| SANS 1921-3 |  | Construction and management requirements for works contracts, Part 3: Structural steelwork |
| SANS 50025-2 |  | Hot rolled products of structural steels – Part 2- Technical delivery conditions for non-alloy structural steels |
| SANS 1700 SET |  | Fasteners |
| SANS 10162 |  | The structural use of steel |
| SANS 2001-CS1 |  | Construction works Part CS1 : Structural steelwork |
| BS EN 10210-2 |  | Hot Finished Structural Hollow Sections of Non-Alloy and Fine Grain Structural Steels |
| SANS 10160-1 |  | Basis of structural design |
| SANS 10160-2 |  | Self-weight and imposed loads |
| SANS 10160-3 |  | Wind actions |
| SANS 10160-5 |  | Basis for geotechnical design and actions |
| SANS 10160-6 |  | Actions induced by cranes and machinery |
| SANS 10160-7 |  | Thermal actions |
| SANS 10160-8 |  | Actions during execution |
| SANS 10161 |  | The design of foundations for buildings |
| Eurocode 3, EN 1993-6(2007 |  | Design of steel structures, crane supporting structures |
| SANS 10100-1 |  | The structural use of concrete Part 1: Design |
| SANS 10143 |  | Building Drawing Practice |

# Appendix F – Stock Item Forms

# Appendix G – PM Change Form

# Appendix H – Master Document list (MDL)

| Master Document List (MDL) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Document Type(s): |  |  |  | XXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date of Report: |  |  |  | XXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Supplier(s) number: |  |  |  | XXX |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Eskom number: |  |  |  | xxx |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Revision: |  |  |  | x |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Document No: | Rev: | Latest Rev: | Document Type: | Eskom No: | Eskom Doc Type: |  | Eskom Rev: | Title: | Reason For Issue: | Source Tx: | Source Tx Date: | Eskom Tx: | Eskom Tx Date: | Authorisation Status | Authorisation Date: | Approval Status: | Approval Date: | Date Preliminary: | Date Approval: | Date - Contract Programme: | Date - Released For Construction: | VDSS Reference: | Plant Breakdown Structure | Discipline: | Division: |

# Appendix I – Control Philosophy and Functional Description

Control and protection philosophies (including Functional Description), but excluding the compressor house HVAC system control philosophy (found in the document Z0419-000132-225), are the responsibility of the Contractor.

# Appendix J – Control and Instrumentation Templates to be used by the Contractor.

| Number | Title |
| --- | --- |
| 240-61379718 (Rev 2) | Control & Instrumentation Instrument Schedule |
| 240-61379755 (Rev 2) | Control & Instrumentation Drive & Actuator Schedule Template |
| 240-72350241 (Rev 1) | Panel Interface List |

# Appendix K – Terminal Point Register

# Appendix M – Training Manual Template

# Appendix N – HVAC Equipment Specification Schedule

# Appendix O – Detailed Design Report Template

# Appendix P – Additional Electrical Schedules

Table P1: Table of Technical Schedules A&B

| Document Title | Document Number |
| --- | --- |
| TUTUKA POWER STATION DUST HANDLING PLANT DRY TYPE TRANSFORMER TECHNICAL SCHEDULE A&B | 360-1165 |
| TUTUKA POWER STATION DUST HANDLING PLANT OIL TYPE TRANSFORMER TECHNICAL SCHEDULE A&B | 360-1166 |
| TUTUKA POWER STATION DUST HANDLING PLANT MV VSD TECHNICAL SCHEDULE A&B | 360-1168 |
| TUTUKA POWER STATION DUST HANDLING PLANT LV VSD TECHNICAL SCHEDULE A&B | 360-1169 |

Table P2: Table of other schedules

| Document Title | Document Number |
| --- | --- |
| TUTUKA POWER STATION DUST HANDLING PLANT ELECTRICAL LOAD LIST | 360-1167 |
| TUTUKA POWER STATION DUST HANDLING PLANT ELECTRICAL COMPLIANCE SCHEDULE | 360-1170 |
| ELECTRICAL CABLE SCHEDULE TEMPLATE | 240-56176097 |
| ELECTRICAL TERMINATION SCHEDULE TEMPLATE | 240-77302094 |
| ELECTRICAL LV LIST OF SWITCHBOARDS TEMPLATE | 240-56356465 |
| ELECTRICAL LV LOAD SCHEDULE TEMPLATE | 240-77301384 |

# Appendix Q – CADD Design Tool Deliverable Required from the Contractor

- The following data submission format table is completed by the Contractor and returned as part of the tender:

| Data Submission Format |  |  |  |
| --- | --- | --- | --- |
| Discipline | Application to be Used | Graphic File | Object Properties (Extension) |
| (Example for 3D Modelling) | PDS Frame Works Plus SmartPlant 3D Alias piping data SP Spoolgen | dri, dgn vue idf, pcf, pod | drv, tag drv, tag drv, tag |
| 3D Modelling |  |  |  |
| Electrical Design |  |  |  |
| Control and Instrumentation (C&I) |  |  |  |
| Piping and Instrumentation Diagrams (P&ID) |  |  |  |
| 2D Drawings (GA’s, Layout, Isometrics, etc.) |  |  |  |

- Submit CV’s of the CADD personnel that clearly describes their experience in the use of the proposed 3D CADD Design Tools and other tools as per the Data Submission Format Table (minimum of three).

- Provide a list of projects, of a similar or greater scope, where the proposed 3D CADD Design Tools and other tools, as per the data submission format table, were used (minimum of five projects).

- Provide comprehensive representative examples demonstrating the use of the proposed design tools and other tools as per the data submission format table (minimum of five examples). The examples include as a minimum:

- Screenshots of the 3D model demonstrating the extent and complexity of the project

- Screenshots showing the model breakdown structure.

- Examples of Single Line Diagrams, Instrument Loop Diagram, P&IDs, GAs, and Isometrics

- Complete the table below : Compliance to SmartPlant  2D Design Integration Technical Specifications (SmartPlant Data Take_On Standard 240-107305502– Paragraphs 3 to 5)

| Compliance to Requirements and Deliverables SmartPlant Data Take_On Standard 240-107305502 Paragraphs 3 to 5 |  |  |
| --- | --- | --- |
| No. | Requirement | Confirm Compliance: Yes/No |
| 5.1 | The Contractor agrees to comply with the requirements and deliverables in SmartPlant Data Take_On Standard 240-107305502 - Paragraph 3.2 Plant Key Parts List |  |
| 5.2 | The Contractor agrees to comply with the requirements and submit the documents as specified in SmartPlant Data Take_On Standard 240-107305502 – Paragraph 3.3 Technical/Design Document Submission. |  |
| 5.3 | The Contractor agrees to comply with the requirements and submit the documents as specified in SmartPlant Data Take_On Standard 240-107305502 – Paragraph 4.1 General Requirements P&ID Drawings. |  |
| 5.4 | The Contractor agrees to comply with the requirements and submit the documents as specified in SmartPlant Data Take_On Standard 240-107305502– Paragraph 4.2 General Requirements Control and Instrumentation Drawings. |  |
| 5.5 | The Contractor agrees to comply with the requirements and submit the documents as specified in SmartPlant Data Take_On Standard 240-107305502– Paragraph 4.3 General Requirements Electrical Drawings. |  |
| 5.6 | The Contractor agrees to comply with the requirements and submit the documents as specified in SmartPlant Data Take_On Standard 240-107305502– Paragraph 5 SmartPlant 3D Design Integration with Other 3D Design Tools. |  |

- The Contractor provides a comprehensive method statement as to how he will comply with the requirement to submit the final design in SmartPlant as specified  Paragraph 3.3.1 in the Works Information:

“The final design is submitted in SmartPlant in the Employer’s SmartPlant Environment. The 3D model is fully integrated with S3D, SPO, P&ID, SPRD+, SPEL and SPI. It incorporates all associated intelligence.”

# Appendix R – Electrical Project Drawings

Figure R1: Proposed Unit 1&2 Ash Bunker Substation layout

Figure R2: Proposed Unit 3&4 Ash Bunker Substation

Figure R3: Proposed Unit 5&6 Ash Bunker Substation

# Appendix S – Tutuka Instructions to Tender, DHP Unit 4-6 Field Equipment and DCS

# C3.2	Contractor’s Works Information

This section of the Works Information will always be contract specific depending on the nature of the works. It is most likely to be required for design and construct contracts where the tendering contractor will have proposed specifications and schedules for items of Plant and Materials and workmanship, which once accepted by the Employer prior to award of contract now become obligations of the Contractor per core clause 20.1. Typical sub headings could be a) Contractor’s design b) Plant and Materials specifications and schedules c) Other

This section could also be compiled as a separate file.

The contractors design and any other information submitted by him will be included under this section.