{"text_format":"3","workbook":"xlsx","n_sheets":3,"sheets":["Schedule - Fittings","Deviation Schedule","Test Schedule"],"not_rendered":{"defined_names":7},"read":"whole","date_system":"1900"}

{"sheet":"Schedule - Fittings","index":0,"n_rows":90,"n_cols":7,"rows_kept":90,"merged":[[0,0,0,6],[1,1,1,6],[2,1,2,6],[3,1,3,6],[4,1,4,6],[5,1,5,6],[8,2,8,3],[9,2,9,3],[10,3,10,4],[19,3,19,4],[23,3,23,4],[34,3,34,4],[37,2,37,4],[38,2,38,4],[39,3,39,4],[42,3,42,4],[49,3,49,4],[78,1,78,3],[79,1,79,6],[81,1,81,3],[83,1,83,3],[87,1,87,3]]}
["ESKOM TENDER E2719DXLIMOU"]
[null,"Technical Schedules A and B for"]
[null,"TURNBUCKLE,EYE TONGUE 120kN  D7007"]
[null,"ESKOM SAP No 0164300"]
[null,"Schedule A:  Purchasers specific requirements"]
[null,"Schedule B:  Guarantees and technical particulars of equipment offered"]
[]
[null,1,null,2,null,3,4]
[null,"Item ","Description",null,null,"Schedule A","Schedule B"]
[null,1,"Product Information"]
[null,1.1,"·","Purchasing details"]
[null,"1.1.1",null,"ESKOM SAP No",null,{"v":164300,"d":"0164300"},"xxxxxxxxxx"]
[null,"1.1.2",null,"Manufacturer",null,"xxxxxxxxxx"]
[null,"1.1.3",null,"Manufacturer's Product Code",null,"xxxxxxxxxx"]
[null,"1.1.4",null,"Manufacturer’s Drawing number & Revision number",null,"xxxxxxxxxx"]
[null,"1.1.5",null,"Manufacturer’s indelible identification mark on product as per SANS 61284",null,"YES"]
[null,"1.1.6",null,"Compliance to all dimensions and requirements of Eskom Buyer's Guide Drawings ","Eskom D-DT-7007","YES"]
[null,"1.1.7",null,"Item sample required",null,"YES","xxxxxxxxxx"]
[]
[null,1.2,"·","Mechanical Properties"]
[null,"1.2.1",null,"Mechanical failing load","kN",120]
[null,"1.2.2",null,"Material Grade",null,"EN8 (080M40)"]
[]
[null,1.3,"·","Coupling interfaces  and dimensions (where applicalbe)"]
[null,"1.3.1",null,"1st Coupling Type on fitting",null,"Eye"]
[null,"1.3.2",null,"2nd Coupling Type on fitting",null,"16L Tongue"]
[{"$nulls":3},"Coupling length"]
[null,"1.3.3",null," -  Minimum coupling length","mm",370]
[null,"1.3.4",null," -  Maximum coupling length","mm",540]
[null,"1.3.5",null,"Oval Eye and Tongue thicknes","mm",16]
[null,"1.3.6",null,"Oval Eye opening","mm",22]
[null,"1.3.7",null,"Oval Eye length","mm",48]
[null,"1.3.8",null,"Tongue hole diameter","mm",17.5]
[]
[null,1.4,"·","Hot Dip Galvanising (where applicalbe)"]
[null,"1.4.1",null,"Average minimum galvanising thickness on product body to SANS 121",null,"YES"]
[]
[null,2,"Documentation (to be submitted with tender)"]
[null,null,"Note:  All documentation to be provided in electronic format."]
[null,2.1,"·","General"]
[null,"2.1.1",null,"Outline drawings of item","Sets",1]
[null,"2.1.2",null,"Material grade certification","Certification Submitted","YES"]
[null,2.2,"·","Test Reports (where applicable)",null,"Required","Report\nNumber"]
[null,"2.2.1",null,"Visual examination (SANS 61284 Clause 7)","Test Report Submitted","Yes"]
[null,"2.2.2",null,"Dimensional & material verification (SANS 61284 clause 8)","Test Report Submitted","YES"]
[null,"2.2.3",null,"Verification of Eye/Tongue (SANS 60471)","Test Report Submitted","YES"]
[null,"2.2.4",null,"Hot dip galvanizing (SANS 61284 clause 9 & SANS 121)","Test Report Submitted","YES"]
[]
[]
[null,2.2,"·","Test Reports (Continue)",null,"Required","Report\nNumber"]
[{"$nulls":3},"Material Properties test and verification"]
[null,"2.2.6",null," - Charpy V-notch impact energy test 240-60777474 (ASTM A370 or equivalent)","Test Report Submitted","YES"]
[null,"2.2.7",null," - Tensile test (240-60777474 and ASTM A370 or equivalent)","Test Report Submitted","YES"]
[null,"2.2.8",null," - Hardness test (240-60777474 & SANS 61284 Clause 10)","Test Report Submitted","YES"]
[{"$nulls":3},"Mechanical Tests "]
[null,"2.2.6",null," - Damage and failure load test (SANS 61284 clause 11)\nNote:Specified minimum damage load SMDL tot be 67%","Test Report Submitted","YES"]
[]
[null,3,null,"Packaging requirement ( Eskom 240-60777474)"]
[null,3.1,"·","Packaging "]
[null,"3.1.1",null,"Supplied in wooden boxes or crates",null,"YES"]
[null,"3.1.2",null,"Supplied in plastic bags",null,"NO"]
[]
[null,3.2,"·","Pallets"]
[null,"3.2.1",null,"Gross mass (maximum)","kg",800]
[null,"3.2.2",null,"Handling by fork lift trucks",null,"YES"]
[null,"3.2.3",null,"Capable of two way entry",null,"YES"]
[null,"3.2.4",null,"Reversible",null,"YES"]
[]
[null,3.3,"·","Marking"]
[{"$nulls":3},"All boxes or pallets numbered consecutively from one upwards and marked generally in accordance with the following:"]
[null,"3.3.1",null,"Supplier's name",null,"YES"]
[null,"3.3.2",null,"Order number",null,"YES"]
[null,"3.3.3",null,"Gross weight",null,"YES"]
[null,"3.3.4",null,"Description of material and quantity",null,"YES"]
[null,"3.3.5",null,"Project name",null,"YES"]
[null,"3.3.6",null,"Delivery address",null,"YES"]
[]
[]
[null,"ESKOM TENDER E2719DXLIMOU"]
[null,"NOTE:  DEVIATION SCHEDULE CONTINUE ON NEXT PAGE.\n             IF NO DEVIATIONS ARE MENTIONED ON THE DEVIATION SCHEDULE IT WILL BE ACCEPTED\n             THAT THE SUPPLIER AND MANUFACTURER FULLY COMPLIES WITH THE REQUIREMENTS OF\n             THE ESKOM SPECIFICATON(S)."]
[]
[null,"SIGNATURES"]
[]
[null,"Supplier"]
[]
[{"$nulls":3},"Name (Print)",null,"Sign","Date"]
[]
[null,"Manufacture"]
[]
[{"$nulls":3},"Name (Print)",null,"Sign","Date"]

{"sheet":"Deviation Schedule","index":1,"n_rows":47,"n_cols":7,"rows_kept":47,"merged":[[1,1,1,6],[2,1,2,6],[3,1,3,6],[4,0,4,6],[5,0,5,6],[6,2,6,6],[7,2,7,6],[8,2,8,6],[9,2,9,6],[10,2,10,6],[11,2,11,6],[12,2,12,6],[13,2,13,6],[14,2,14,6],[15,2,15,6],[16,2,16,6],[17,2,17,6],[18,2,18,6],[19,2,19,6],[20,2,20,6],[21,2,21,6],[22,2,22,6],[23,2,23,6],[24,2,24,6],[25,2,25,6],[26,2,26,6],[27,2,27,6],[28,2,28,6],[29,2,29,6],[30,2,30,6],[31,2,31,6],[32,2,32,6],[33,2,33,6],[34,2,34,6],[35,2,35,6],[36,2,36,6],[39,0,39,1],[40,0,40,1],[42,0,42,1],[43,0,43,1],[45,0,45,1],[46,0,46,1]]}
[null,null,"ESKOM TENDER E2719DXLIMOU"]
[null,"Deviation schedule"]
[null,"TURNBUCKLE,EYE TONGUE 120kN  D7007"]
[null,"ESKOM SAP No 0164300"]
[]
["Any deviations offered to this specification shall be listed below with reasons for deviation.  In addition, evidence shall be provided that the proposed deviation will at least be more cost-effective that that specified by Eskom."]
["Item","Clause","Description of Deviation"]
{"$rows_empty":30}
["SIGNATURES"]
[]
["Supplier",null,"         "]
[null,null,"Name (Print)",null,"Sign",null,"Date"]
[]
["Manufacturer",null,"         "]
[null,null,"Name (Print)",null,"Sign",null,"Date"]
[]
["Eskom",null,"         "]
[null,null,"Name (Print)",null,"Sign",null,"Date"]

{"sheet":"Test Schedule","index":2,"n_rows":24,"n_cols":5,"rows_kept":24,"merged":[[1,1,1,4],[2,1,2,4],[3,1,3,4],[4,0,4,4],[17,0,17,2],[21,0,21,2]]}
[null,"ESKOM TENDER E2719DXLIMOU"]
[null,"Test Schedule"]
[null,"TURNBUCKLE,EYE TONGUE 120kN  D7007"]
[null,"ESKOM SAP No 0164300"]
[]
[2.2,"Test Reports (where applicable)","Specification reference","Required","Report Number"]
["2.2.1","Visual examination ","SANS 61284 Clause 7","YES"]
["2.2.2","Dimensional & material verification ","SANS 61284 clause 8","YES"]
["2.2.3","Verification of Eye/Tongue","SANS 60471","YES"]
["2.2.4","Hot dip galvanizing ","SANS 61284 clause 9 & SANS 121","YES"]
[null,"Material Properties test and verification"]
["2.2.6"," - Charpy V-notch impact energy test 240-60777474 ","ASTM A370 or equivalent","YES"]
["2.2.7"," - Tensile test 240-60777474","ASTM A370 or equivalent","YES"]
["2.2.8"," - Hardness test 240-60777474","SANS 61284 Clause 10","YES"]
[null,"Mechanical Tests "]
["2.2.9"," - Damage and failure load test ","SANS 61284 clause 11","YES"]
[]
["Supplier"]
[]
[null,"Name (Print)","Sign","Date"]
[]
["Manufacture"]
[]
[null,"Name (Print)","Sign","Date"]