RFB 3199/2025: Annexure 1: Bid Specification:

REQUEST FOR BID FOR THE UPGRADE OF MEDIUM VOLTAGE ELECTRICAL INFRASTRUCTURE AT SITA CENTURION AND BETA SITES FOR A PERIOD OF 36 MONTHS.

TECHNICAL, PRICING AND PREFERENCE POINTS REQUIREMENTS

# Contents

1.	Introduction and background	3

1.1.	Purpose	3

1.2.	Background	3

2.	Scope of Bid	3

2.1.	Scope of Work	3

2.2.	Delivery addresses	4

3.	Requirements	4

3.1.	Solution Requirements	4

3.2.	Existing 11kV Electrical Equipment Details	6

3.2.1.	SITA Centurion	6

3.2.2.	SITA Beta	6

4.	Bid Evaluation Stages	7

4.1.	Mandatory Administrative responsiveness (Stage 1)	7

4.1.1.	Attendance of briefing session	7

4.1.2.	Registered Bidder	7

4.2.	Technical returnable documents	7

4.2.1.	Instruction and evaluation criteria	7

4.2.2.	Bid Submission Instructions	7

4.3.	Technical Mandatory Responsiveness (Stage 2)	9

4.4.	Special Conditions of Contract Verification (Stage 3)	14

4.4.1.	Special Conditions of Contract	15

4.4.2.	Declaration of compliance and acceptance SCC	26

Annex A: Bidder substantiating evidence	39

5.	Technical Mandatory Requirement Evidence	39

5.1.	Bidder Certification / Affiliation Requirements	39

5.2.	Bidder Experience and Capability Requirements	39

5.3.	CIDB Registration Requirements	40

5.4.	Key Personnel Qualification	40

5.5.	Installation Electrician Requirement	41

5.6.	Medium Voltage Technicians Certification Requirement	41

5.7.	Equipment Data Sheets	42

5.8.	IEC62271-200 Type Test Certification	42

5.9.	Equipment General Arrangement Drawings	42

5.10.	Special Conditions of Contract	42

5.11.	Preference Points Preferential Goals Evidence	43

Annex B: CIDB Registration Requirement	45

Annex C: Technical Information	46

6.	Technical Information	46

6.1.	Project Specifications	46

6.2.	Project Data Sheets	46

6.3.	Project Drawings	46

Annex D: LOCAL CONTENT REQUIREMENTS	47

7.	Local Content Requirements:	47

Annex E: CIDB BASIC GUIDE GENERAL CONDITIONS OF CONTRACT FOR CONSTRUCTION WORKS (GCC 2004)	48

# Introduction and background

## Purpose

The purpose of this RFB is to invite Suppliers (hereinafter referred to as “bidders”) to submit bids for the Upgrading of the Medium Voltage Switchgear and Auxiliaries at SITA Centurion and Beta with 24 months maintenance support period. The total contract period will be limited to 36 months.

## Background

The electrical infrastructure at the data centre is close to the end of life, which leads to several challenges regarding availability, short to medium-term maintenance planning, and medium to long-term growth planning. The medium voltage infrastructure upgrades will assist the two sites in achieving a higher level of reliability and availability of the electrical power supply for critical computer environments.

# Scope of Bid

## Scope of Work

The scope of work by the bidders is Upgrade of the 11kV Medium Voltage Indoor Switchgear and Auxiliaries at SITA Centurion and Beta sites which includes:

- Design, Manufacture, Testing and Delivery of 2x 11kV Medium Voltage Incomer panels with Quality of Supply meters at SITA Centurion. The panels may be similar to Actom AMV12/AMV12DB or equivalent.

- Design, Manufacture, Testing and Delivery of 4x 11kV Medium Voltage Feeder Panels for 2500kVA Transformers with Quality of Supply meters at SITA Centurion. The panels may be similar to  Actom AMV12/AMV12DB or equivalent.

- Design, Manufacture, Testing and Delivery of Medium Voltage Power Factor Correction Bank at SITA Centurion.

- Provision for Design, Manufacture, Testing and Delivery of 1x 11kV Medium Voltage Power Factor Correction feeder with Power Factor Correction Controller at SITA Centurion. The panels should be Actom AMV12/AMV12DB switchgear similar or equivalent.

- Design, Manufacture, Testing and Delivery of Battery Tripping Unit for indoor Medium Voltage Switchgear at SITA Centurion.

- Site Establishment at SITA Centurion site.

- Design, Manufacture, Testing and Delivery of 2x 11kV Medium Voltage Incomer panels with Quality of Supply meters at SITA Beta. The panels may be  Actom AMV12/AMV12DB or equivalent.

- Design, Manufacture, Testing and Delivery of 4x 11kV Medium Voltage Feeder Panels for 1600kVA Transformers with Quality of Supply meters at SITA Beta. The panels should be The panels may be similar to Actom AMV12/AMV12DB or equivalent.

- Provision for Design, Manufacture, Testing and Delivery of 11kV Medium Voltage Power Factor Correction Bank at SITA Beta.

- Design, Manufacture, Testing and Delivery of 1x 11kV Medium Voltage Power Factor Correction feeder with Power Factor Correction Controller at SITA Beta.

- Design, Manufacture, Testing and Delivery of Battery Tripping Unit for Indoor Medium Voltage Switchgear at SITA Beta.

- Site Establishment at SITA Beta.

- Removal and disposal of existing medium voltage switchgear, battery tripping units and Power Factor system

- Installation and Commissioning within 48 hours change window – SITA Centurion.

- Installation and Commissioning within 48 hours change window SITA Beta.

- Maintenance and service for the period of 24 months.

## Delivery addresses

Table 1: Delivery addresses

| No | Site Name | Physical Address |
| --- | --- | --- |
| 1 | SITA Centurion | 1108 John Vorster Drive, Centurion, Pretoria |
| 2 | SITA Beta | 222 Johannes Ramokhoase, Pretoria |

# Requirements

## Solution Requirements

The supply, delivery and installation of the medium voltage switchgear and associated infrastructure. This will include but not be limited to the following:

  - Preliminary, General and Site Establishment.

  - 11KV Medium Voltage Switchgear:

    - Design of an 11kV, panel switchboards complete with integrated protection and control schemes for minimum requirement as detailed in the following documents:

      - eSDHS-01288 - SITA Medium Voltage Switchgear Specification.

      - SITA Centurion: Proposed New 11kV Single Line Diagram 1001547-0000-DRG-EE-0001- Rev A.

      - SITA Beta: Proposed New 11kV Single Line Diagram 1001547-0000-DRG-EE-0002- Rev A.

      - Switchgear Datasheet - General Requirements.

      - Switchgear Datasheet - Incomer Panel Requirements.

      - Switchgear Datasheet - Transformer Feeder Panel Requirements.

    - Manufacturing and Factory Acceptance Testing of an 11kV, panel switchboards complete with integrated protection and control schemes approved designs and data sheets. Factory Acceptance Testing to be completed at a facility in Gauteng South Africa.

    - Delivery and Off Loading of an 11kV, panel switchboards complete with integrated protection and control schemes.

    - Supply and delivery to site of new Medium Voltage Power and Control Cables for Transformers.

    - Supply and delivery to site of new Medium Voltage Cable Termination Kits.

    - Provision for Supply and delivery to site of trifocating cable joints for PILC to XLPE cables.

    - Preliminary, General and Site Establishment.

    - Disconnecting of existing Medium Voltage Power and Control Cables from the existing switchboard.

    - Removal and disposal of existing medium voltage switchboard.

    - Installation of new medium voltage switchboard.

    - Termination of new and/or existing Medium Voltage Power Cables and Control Cables.

    - Testing of new Medium Voltage Cables.

    - Commissioning of new medium voltage switchboards.

  - Power Factor Correction System (Provision):

    - The design, supply, testing, installation and commissioning of capacitors optimally placed on a capacitor rack within an indoor fully metal enclosure, unearthed 1-stage 1.25MVAr 5th Harmonic filter, with 1.2MVAr (Double Star) capacitor bank configuration for minimum requirement as detailed in the following documents:

      - eSDHS-01289 - SITA Power Factor Correction Specification.

      - SITA Centurion: Proposed New 11kV Single Line Diagram 1001547-0000-DRG-EE-0001- Rev A.

      - SITA Beta: Proposed New 11kV Single Line Diagram 1001547-0000-DRG-EE-0002- Rev A.

      - Switchgear Datasheet - PFC Feeder Panel Requirements.

    - The design, supply, installation and commissioning of harmonic iron core tuning reactors for the 1 x 1.25MVar Harmonic Filters.

    - This includes the supply, installation and commissioning of the neutral transformers on the Capacitor racks.

    - The design, supply, installation and commissioning of a Castell key or equivalent interlocking system, preventing access to the harmonic filter compartment, until the filter bank is discharged and earthed.

    - The supply, installation, termination and commissioning of the required Medium Voltage (MV) power cables, and Low Voltage (LV) control cables for operation of the 11kV Harmonic Filter Systems.

    - The Factory Acceptance Test (FAT) of the 11kV Harmonic Filter Systems at the manufacturer’s facility or any other suitable facility in Gauteng before delivery to Site.

    - The full installation and full Site Acceptance Test (SAT) by the Service Provider to ensure correct operation of the harmonic filter banks and associated equipment.

    - A full cold commissioning in the presence of SITA (or representative) to prove the installation and to ensure stable operation of the Harmonic Filter Control per installation.

    - Contractor’s presence during the hot commissioning of the Harmonic Filter Installation by the SITA and the monitoring of the Harmonic Filter System to ensure stable operation under actual load conditions.

  - Battery Tripping Unit:

    - Design of Battery Tripping Unit for Indoor Medium Voltage Switchgear for minimum requirement as detailed in the following documents:

      - SITA Centurion: Proposed New 11kV Single Line Diagram 1001547-0000-DRG-EE-0001- Rev A.

      - SITA Beta: Proposed New 11kV Single Line Diagram 1001547-0000-DRG-EE-0002- Rev A.

      - eSDHS-01290 - SITA Battery Tripping Units Specification.

      - Switchgear Datasheet – Battery Tripping Unit Requirements.

    - Manufacturing and Factory Acceptance Testing of Battery Tripping for indoor Medium Voltage Switchgear.

    - Delivery and Off Loading of Battery Tripping Unit for indoor Medium Voltage Switchgear.

    - Disconnecting of existing Battery Tripping Unit.

    - Removal and disposal of existing Battery Tripping Unit.

    - Installation of new Battery Tripping Unit including cabling.

    - Testing of new Battery Tripping Unit.

    - Commissioning of new Battery Tripping Unit.

  - Builder’s work, such as creating openings in walls for new cables/ busbars to pass through, heavy-duty epoxy flooring, wall plastering, and painting.

  - Builder’s work, such as creating openings in walls for new cables/ busbars to pass through, heavy-duty epoxy flooring, wall plastering, and painting.

  - On-site Callouts and Emergency Maintenance followed by a Root Cause Analysis.

  - Support and critical repairs with required service level: Availability 24/7/365 during the Twenty-Four (24) months contract period, with a maximum 90-minute incident response time. The service will be “works order based” for known corrective maintenance requirements and be “callout based” followed by purchase order.

  - Upon SITA’s request, the bidder must provide inspection and quality assurance services on other SITA electrical bidders’ work for SITA systems that impact the equipment performance and services on this scope.

## Existing 11kV Electrical Equipment Details

The details for the existing electrical equipment to be removed.

### SITA Centurion

  - Two (2) Incomer Feeder: Air Insulated 11kV Air Insulated Switchgear and Protection Systems

  - Four (4) Transformer feeders: Air Insulated 11kV Air Insulated Switchgear and Protection Systems

  - One (1) Power Factor Correction feeder: Air Insulated 11kV Air Insulated Switchgear and Protection Systems

  - One (1) Power Factor Correction Capacitor Bank

### SITA Beta

  - Two (2) Incomer Feeder: Air Insulated 11kV Air Insulated Switchgear and Protection Systems

  - Three (3) Transformer feeders: Air Insulated 11kV Air Insulated Switchgear and Protection Systems

  - One (1) Power Factor Correction feeder: Air Insulated 11kV Air Insulated Switchgear and Protection Systems

  - One (1) Power Factor Correction Capacitor Bank

# Bid Evaluation Stages

The bid evaluation process consists of several stages, according to the nature of the bid. A bidder must qualify for each stage to be eligible to proceed to the next stage of the evaluation.

The stages are:

Table 2: Bid Evaluation Stages

| Stage | Description | Applicable for this bid YES/NO |
| --- | --- | --- |
| Stage 1 | Mandatory Administrative Responsiveness | YES |
| Stage 2 | Technical Mandatory Responsiveness | YES |
| Stage 3 | Special Conditions of Contract Verification | YES |
| Stage 4 | Costing and Preference Points Evaluation | YES |

## Mandatory Administrative responsiveness (Stage 1)

### Attendance of briefing session

- A Compulsory Virtual Briefing session will be held. The bidder must sign the briefing session attendance register using the same information (bidder company name, bidder representative person name and contact details) as submitted in the bidder’s response document.

Note (1):	A non-compulsory site visit will be arranged on request.

Note(2):   Any bidder who fails to attend the compulsory virtual briefing session will be disqualified.

### Registered Bidder

- Only responses from bidders who are registered as a Bidder on National Treasury’s Central Bidder Database (CSD) in terms of National Treasury’s Instruction Note 4A of 2016/17 will be considered for award on this RFB.

- In the case of joint ventures or consortiums the bidder must demonstrate that at least one of the parties to the bid response attended the briefing session.

- Bidders need to complete all the SBD documents which needs to be submitted as stated in the Invitation to Bid Document.

## Technical returnable documents

### Instruction and evaluation criteria

- The Bidder must comply with ALL the requirements as per the Technical Mandatory Requirements below by providing substantiating evidence in the form of documentation or information, failing which it will be regarded as “NOT COMPLY”.

- The Bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response.

- The Bidder must comply with ALL the TECHNICAL MANDATORY REQUIREMENTS in order for the bid response to proceed to the next stage of the evaluation.

### Bid Submission Instructions

Note that a Two Envelope process will be followed and therefore bidders must submit as follows:

- Envelope 1: RFB Document and Technical / Functionality Response

# The following must be included and submitted in a in a separate envelope:

  - One (1) original file excluding pricing; and

  - One (1) hard copy excluding pricing; and

  - One (1) electronic copy on USB memory stick/ flash drive in Portable Document Format (PDF) of the RFB Document and Technical / Functionality Response.

- Envelope 2: Price Response

# The following must be included and submitted in a in a separate envelope:

  - One (1) original file excluding Technical / Functionality Response; and

  - One (1) hard copy excluding Technical / Functionality Response; and

  - One (1) electronic copy on USB memory stick/ flash drive in Portable Document Format (PDF) of pricing only.

- It is the Bidder’s responsibility to ensure that the information and contents on the electronic copies is the same as in the hard copies.

- To ensure that the electronic copies are not damaged, the bidder must submit the USB’s (memory stick/ flash drive) in a sealed padded envelope and be clearly marked.

- Bidders shall submit Bid responses in accordance with the prescribed manner of submission as specified above. Failure to comply with the above instructions on submitting a proposal will lead to disqualification.

- The RFB Responses (hard and electronic copies) must be clearly marked as follows: Bidder’s Name & Contact Details, RFB Number, RFB Description, and Closing Date.

- All Bids in this regard shall only be accepted if they have been placed in the tender box before or on the closing date and stipulated time.

- Late bids shall not be considered.

- The Bid response must be signed by an authorised employee, agent or representative of the bidder. The Bid response Bid must bear the initials of the signatory at the bottom of every page as an indication that the bidder has familiarised itself with the terms and conditions of this RFB document.

- Faxed or e-mailed bids will not be accepted.

- Bidders shall submit Bid responses in accordance with the prescribed manner of submission as specified in this document. Failure to comply with the bid submission requirements will lead to disqualification.

- Bidders are required to submit all returnable documents/information together with their Bids/proposals on or before the closing time and date of the Bids/proposals.

- All services supplied in accordance with the bidder’s proposal must be in accordance with all applicable legal requirements in terms of South African law, policies and regulations.

## Technical Mandatory Responsiveness (Stage 2)

Table 3: Technical Mandatory Requirements

| Mandatory Requirements |  | Substantiating evidence of compliance (used to evaluate bid) | Evidence reference (to be completed by bidder) |
| --- | --- | --- | --- |
| 1. Bidder Certification/ Affiliation Requirements |  |  |  |
| The Bidder must be registered as an Electrical Contractor with the Department of Labour. |  | Attach to ANNEX A copy of valid letter from the Department of Labour as evidence that the bidder is registered as an Electrical Contractor. NOTE (1): SITA reserves the right to verify the information provided. | <provide a unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.1> |
| 2. Bidder Experience and Capability Requirements |  |  |  |
| The bidder must have executed at least two (2) projects for the Installation of Primary Indoor Medium Voltage Switchgear and Infrastructure at a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Industrial Plant, Power Utility, Municipality or similar High Availability Environments to at least two (2) customers/projects in the past ten (10) years. |  | The Bidder must complete table 10 by providing reference details from two (2) customers/projects to whom Installation of Primary Indoor Medium Voltage Switchgear and Infrastructure at a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Industrial Plant, Power Utility, Municipality or similar High Availability Environments to at least two (2) customers/projects in the past ten (10) years. - Company name; and - Reference Person Name, Tel and/or email; and - Project Scope of Work; and - Project Start and end date. NOTE (1): The Bidder must provide all of the following information when completing table 10 NOTE (2): Failure to comply fully with the abovementioned requirements will result in disqualification. NOTE (3): SITA reserves the right to verify the information provided. | <provide a unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.2, table 10> |
| 3. CIDB Registration Requirement |  |  |  |
| The Bidder must be registered with the Construction Industry Development Board (CIDB) and have a minimum rating of 7EB or 7EP or higher. |  | The Bidder must complete and sign ANNEX B as evidence that the Bidder, is registered with the CIDB with a minimum rating or higher of 7EB, or 7EP NOTE (1): SITA reserves the right to verify the information provided. | <provide a unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.3 and Annex B> |
| 4. Key Personnel Qualification |  |  |  |
| The Bidder must provide a qualified Project Manager with a minimum of five (5) years’ post professional registration. The professional registration be either one (1) of the following: - ECSA, Professional Engineer (Pr Eng), or - ECSA, Professional Certificated Engineer Technician, or - ECSA, Professional Engineering Technologist, or - ECSA, Professional Engineering Technician, or - PMI, Project Management Professional (PMP), or - SACPCMP, Professional Construction Project Managers. |  | Attach to ANNEX A copy of a valid Registration Certificate indicating that the Project Manager has been registered as professional for a minimum of five (5) years of post professional registration. The professional registration be either one (1) of the following: - ECSA, Professional Engineer (Pr Eng), or - ECSA, Professional Certificated Engineer Technician, or - ECSA, Professional Engineering Technologist, or - ECSA, Professional Engineering Technician, or - PMI, Project Management Professional (PMP), or - SACPCMP, Professional Construction Project Managers. NOTE (1): SITA reserves the right to verify the information provided. NOTE (2): SITA reserves the right to verify the consent from the registered person. NOTE (3): The Bidder must also provide registered person contact details by completing table 11. NOTE (3): The Bidder provided registered person will be the contracts manager for the duration of the project. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.4 table 11> |
| 5. Installation Electrician Requirement |  |  |  |
| The Bidder must provide a qualified Installation Electrician or Master Installation Electrician with minimum five (5) years’ experience or longer post registration as Installation Electrician or Master Installation Electrician. (a) Trade Test Certificate; and (b) Installation Electrician (IE) or Master Installation Electrician (MIE) registration card or Department of Labour letter confirming the registration | Attach to ANNEX A, a copy of valid Trade Test Certificate and Wiremans License (Registered Person License) indicating that the Installation Electrician or Master Installation Electrician is qualified with five (5) years of experience post registration and trade test certification. Attach: (a) Trade Test Certificate; and (b) Installation Electrician (IE) or Master Installation Electrician (MIE) registration card or Department of Labour letter confirming the registration The evidence must clearly indicate: (a) The names and ID numbers of the registered person (b) Certificate and licence numbers of the registered person (c) Name of the registration/issuing authority (e.g Department of Labour or QCTO). (d) Date of issue/mandate NOTE (1): SITA reserves the right to verify the information provided. NOTE (2): SITA reserves the right to confirm consent of submission from the electrician person NOTE (3): Failure to provide the two documents will lead to disqualification. |  | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.5> |
| 6. Medium Voltage Technicians Certification Requirement |  |  |  |
| The Bidder must provide a qualified Medium Voltage Technicians (one each) with ten (10) years’ experience post certification. - ORHVS- Authorised Person, and - MV Cable Jointing & Terminating | Attach to ANNEX A copy of valid Certification and a CV for each technician indicating that the person is qualified with ten (10) years of experience post certification. - ORHVS-Authorised Certificate - MV Cable Jointing & Terminating Certificate NOTE (1): SITA reserves the right to verify the information provided NOTE (2): SITA reserves the right to confirm consent of submission from the Medium Voltage technician NOTE (3): Failure to provide the document will lead to disqualification |  | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.6> |
| 7. Equipment Data Sheets |  |  |  |
| The Bidder must comply with the specifications by completing and submitting signed equipment data sheets listed in Annex C. |  | Attach to Annex A a completed and signed Data Sheet as per ANNEX C: - SITA 11kV Main Board - Switchgear Datasheet_ General Requirements - SITA Centurion 11kV Main Board - Switchgear Datasheet - Incomer Panel Requirements - SITA Centurion 11kV Main Board - Switchgear Datasheet - Transformer Feeder Panel Requirements - SITA 11kV Main Board Switchgear Datasheet - PFC Feeder Panel Requirements - SITA 11kV Main Board Switchgear Datasheet – Battery Tripping Unit Requirements - SITA Beta 11kV Main Board Switchgear Datasheet - Incomer Panel Requirements - SITA Beta 11kV Main Board Switchgear Datasheet - Transformer Feeder Panel Requirements. NOTE (1): SITA reserves the right to verify the information provided. NOTE (2): Failure to complete the Data Sheets fully will result in disqualification. | <provide a unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.7> |
| 8. IEC62271-200 Type Test Certification |  |  |  |
| The bidder must confirm compliance with IEC62271-200 Type Test Internal Arc Certification for Primary Distribution Switchgear. |  | Attach to Annex B a copy of IEC62271-200 Type Test Internal Arc Certification for Primary Distribution Switchgear. NOTE (1): SITA reserves the right to verify the information provided. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.8 |
| 9. Equipment General Arrangement Drawings |  |  |  |
| The Bidder must comply with the specifications by submitting Equipment General Arrangement from attached Single Line Diagram 1001547-0000-DRG-EE-0001. - SITA Centurion 11kV Main Board - Switchgear - Incomer Panel - SITA Centurion 11kV Main Board - Switchgear - Transformer Feeder Panel - SITA 11kV Main Board Switchgear - PFC Feeder Panel - SITA 11kV Main Board Switchgear – Battery Tripping Unit |  | Attach to Annex A copies of Equipment General Arrangement drawings of the following Single Line Diagram 1001547-0000-DRG-EE-0001: - SITA Centurion 11kV Main Board - Switchgear - Incomer Panel - SITA Centurion 11kV Main Board - Switchgear - Transformer Feeder Panel - SITA 11kV Main Board Switchgear - PFC Feeder Panel - SITA 11kV Main Board Switchgear - Battery Tripping Unit Note (1): Total four (4) GA drawings that are to be submitted. Note (2): Submitted information will be applicable to all the sites Note (3): SITA reserves the right to verify the information provided. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.9 |
| 10. Special Conditions of Contract |  |  |  |
| Bidder must accept ALL the Special Conditions of contract. |  | The Bidder must accept ALL the Special Conditions of Contract by completing and signing the declaration of Acceptance in Declaration of compliance and acceptance under the Special Conditions (Section 4.4.2). Note (1): Failure to accept ALL the Special Conditions of Contract will result in disqualification. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.10 |

## Special Conditions of Contract Verification (Stage 3)

- The successful Bidder will be bound by Government Procurement: General Conditions of Contract (GCC) as well as this Special Conditions of Contract (SCC), which will form part of the signed contract with the successful Bidder. However, SITA reserves the right to include or waive the condition in the signed contract.

- SITA reserves the right to:

  - Negotiate the conditions; or

  - Automatically disqualify a bidder for not accepting these conditions; or

  - Award to multiple bidders; or

  - Not to award; or

  - To do a partial award.

- In the event that the bidder qualifies the proposal with own conditions and does not specifically withdraw such own conditions when called upon to do so, SITA will invoke the rights reserved in accordance with subsection 4.3. (b) above.

### Special Conditions of Contract

#### Contracting Conditions

- Formal Contract - The Bidder must enter into a formal written contract (agreement) with SITA.

- Right of Award - SITA reserves the right to award the contract for required goods or services to multiple Bidders.

- Right to Audit - SITA reserves the right, before entering into a contract, to conduct or commission an external service provider to conduct a financial audit or probity to ascertain whether a qualifying bidder has the financial wherewithal or technical capability to provide the goods and services as required by this tender.

#### Delivery Address

- The Bidder must deliver the required products or services at as indicated in Section 2.2, Delivery Address

#### Delivery Schedule

  - The scope of work (Section 2.1) and Section 3 (Requirements) must be completed within 26 weeks after the contract has been awarded for decommission, supply, install and commissioning of the new equipment.

  - Construction period will be limited to a period 12 months. The 24 months maintenance and service period will commence immediately after handover and commissioning of the last generator set.

  - The Bidder is responsible for performing the work as outlined in the following Work Breakdown Structure (WBS):

Table 4: Work Breakdown Structure (WBS)

| WBS | Statement of Work | Delivery Timeframe |
| --- | --- | --- |
|  | Design, Manufacture, Testing and Delivery of 2x Medium Voltage Incomer panels with Quality of Supply meters; | 26 Weeks |
|  | Design, Manufacture, Testing and Delivery of 4x Medium Voltage Feeder Panels for 2500kVA Transformers with Quality of Supply meters; | 26 Weeks |
|  | Design, Manufacture, Testing and Delivery of Medium Voltage Power Factor Correction Bank; | 26 Weeks |
|  | Design, Manufacture, Testing and Delivery of 1x Medium Voltage Power Factor Correction feeder with Power Factor Correction Controller; | 26 Weeks |
|  | Design, Manufacture, Testing and Delivery of Battery Tripping Unit for indoor Medium Voltage Switchgear | 26 Weeks |
|  | Site Establishment | 4 weeks prior delivery |
|  | Design, Manufacture, Testing and Delivery of 2x Medium Voltage Incomer panels with Quality of Supply meters; | 26 Weeks |
|  | Design, Manufacture, Testing and Delivery of 3x Medium Voltage Feeder Panels for 1600kVA Transformers with Quality of Supply meters; | 26 Weeks |
|  | Design, Manufacture, Testing and Delivery of Medium Voltage Power Factor Correction Bank; | 26 Weeks |
|  | Design, Manufacture, Testing and Delivery of 1x Medium Voltage Power Factor Correction feeder with Power Factor Correction Controller; | 26 Weeks |
|  | Design, Manufacture, Testing and Delivery of Battery Tripping Unit for indoor Medium Voltage Switchgear | 26 Weeks |
|  | Site Establishment | 4 weeks prior delivery |
|  | Installation and Commissioning – SITA Centurion | 48 Hours during approved downtime period |
|  | Installation and Commissioning – SITA Beta Data | 48 Hours during approved downtime period |
|  | Maintenance and service | 24 months will commence on after commissioning and handover |

#### Penalties

- A penalty of 15% of the monthly contract value or any specific deliverable may be imposed if it is found that the Service Provider failed to meet agreed deliverables, and such failure was not caused by a failure of the client to comply with its obligations.

- Where penalties are imposed, the relevant monthly invoice will be reduced by the penalty amount, or a credit note for the penalty amount will be submitted to SITA within 2 (two) months of the target not being met.

SITA reserves the right to enforce these penalties, or not, depending on the merit of each case.

#### Services and Performance Metrics

  - During Warranty and Maintenance periods the Bidder is responsible to provide the following services as specified in the Service Breakdown Structure (SBS):

Table 5: Service Breakdown Structure

| SBS | Service Element | Service Level |
| --- | --- | --- |
|  | Emergency Contact during warranty and maintenance periods | 24h x 7days x 52weeks |
|  | Incident Response during warranty and maintenance periods | Maximum 90-minutes |

  - During Warranty and Maintenance periods the Bidder is responsible to provide the following services:

- Batteries Maintenance Requirement.  To be completed annually from the date of commissioning according to OEM recommendations. The actual maintenance activities to be confirmed during handover of the switchboards.

#### Bidder Performance Reporting

- The Bidder will report to SITA monthly during the design and manufacturing phase of the project; monthly written reports will be presented to SITA on the progress until delivery of the equipment.

- The Bidder will report to SITA/Client on a bi-weekly basis during the installation and implementation phase of the project; bi-weekly written reports will be presented to the SITA/Client on the progress of the preceding week until the installation process has been completed.

- Quarterly meetings to be scheduled between SITA/Client and service provider during warranty and maintenance periods.

- The Bidder is required to generate regular reports as outputs during the maintenance and support cycle within the following service levels (the report type will drive the service level agreement; definition of the content of each report type will be finalised at the time of concluding the contracted service level agreement).

#### Certification, Expertise and Qualification

  - The Bidder must be registered at the Department of Labour as an Electrical Contractor

  - The bidder must have executed at least two (2) projects for the Installation of Primary Indoor Medium Voltage Switchgear and Infrastructure at a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Industrial Plant Power Utility, Municipality or similar High Availability Environments to at least two (2) customers/projects in the past ten (10) years.

  - The Bidder or subcontractor must be registered with the Construction Industry Development Board (CIDB) with a minimum rating of 7EB or 7EP.

  - The Bidder must provide a qualified Project Manager with a minimum of five (5) years’ post professional registration. The professional registration be either one (1) of the following:

    - ECSA, Professional Engineer (Pr Eng), or

    - ECSA, Professional Certificated Engineer Technician, or

    - ECSA, Professional Engineering Technologist, or

    - ECSA, Professional Engineering Technician, or

    - PMI, Project Management Professional (PMP), or

    - SACPCMP, Professional Construction Project Managers.

  - The Bidder must provide a qualified Installation electrician – Trade Test and Wiremans Licence with five (5) years’ experience or longer post registration.

  - The Bidder must provide a qualified Medium Voltage Technicians (one each) with ten (10) years’ experience or longer post certificate.

    - ORHVS- Authorised Person, and

    - MV Cable Jointing & Terminating

  - The Bidder must comply with the specifications by completing and submitting signed equipment data sheets listed in Annex C.

    - SITA 11kV Main Board - Switchgear Datasheet_ General Requirements

    - SITA Centurion 11kV Main Board - Switchgear Datasheet - Incomer Panel Requirements

    - SITA Centurion 11kV Main Board - Switchgear Datasheet - Transformer Feeder Panel Requirements

    - SITA 11kV Main Board Switchgear Datasheet - PFC Feeder Panel Requirements

    - SITA 11kV Main Board Switchgear Datasheet – Battery Tripping Unit Requirements

    - SITA Beta 11kV Main Board Switchgear Datasheet - Incomer Panel Requirements

    - SITA Beta 11kV Main Board Switchgear Datasheet - Transformer Feeder Panel Requirements

  - The Bidder shall indicate compliance with IEC62271-200 Type Test Internal Arc Certification for Primary Distribution Switchgear by submitting a copy of the certificate,

  - The Bidder must comply with the specifications by submitting Equipment General Arrangement from attached Single Line Diagram 1001547-0000-DRG-EE-0001.

    - SITA Centurion 11kV Main Board - Switchgear - Incomer Panel

    - SITA Centurion 11kV Main Board - Switchgear - Transformer Feeder Panel

    - SITA 11kV Main Board Switchgear - PFC Feeder Panel

    - SITA 11kV Main Board Switchgear – Battery Tripping Unit

  - The Bidder represents that,

    - it has the necessary expertise, skill, qualifications and ability to undertake the work required in terms of the Statement of Work or Service Definition and;

    - it is committed to provide the Products or Services; and

    - perform all obligations detailed herein without any interruption to the Customer.

  - The Bidder must provide the service in a good and workmanlike manner and in accordance with the practices and high professional standards used in well-managed operations performing services similar to the Services;

  - The Bidder must perform the Services in the most cost-effective manner consistent with the level of quality and performance as defined in Statement of Work or Service Definition;

  - Original Equipment Manufacturer (OEM).

    - The Bidder must ensure that work or service for the commissioning of the new equipment is performed by a person who is certified by Original Equipment Manufacturer and the certification will be included in the commissioning reports and handover documents. This will include all the work activities for the new installed switchgear assembly.

    - The bidder must be able to access to the control system for service diagnostics and possible repairs. The bidder must have the latest software as approved by OSM.

#### Logistical Conditions

  - Hours of work, 08h00 – 16h30.

  - Provision to be made for work which will be Saturday and Sunday or weekday after hours.

  - Provision for the installation and commissioning of the equipment to be made during scheduled downtime which will be from Friday midnight to Sunday midnight for at least one weekend. The Supplier to make sure all the resources, tools and equipment are available to work continuously during that period to complete all the scheduled tasks during that period. The downtime period will be limited to 48 Hours. This will be including for overtime and night shift over the allocated time

  - It must be noted that the Data Centres are live/active sites, and downtimes are limited. All site the services will have to be restored at the end of the scheduled downtime.

  - The installation and commissioning activities that does not require downtime, those can be completed during hours in 8(a) or per arrangement as per 8(b).

  - In the event that SITA grants the Bidder permission to access SITA's Environment including hardware, software, internet facilities, data, telecommunication facilities and/or network facilities remotely, the Supplier must adhere to SITA's relevant policies and procedures (which policy and procedures are available to the Supplier on request) or in the absence of such policy and procedures, in terms of, best industry practice.

  - Tools of Trade: The Supplier must bring their necessary tools of trade in order for them to perform their duties adequately.

  - On-site and Remote Support: The Supplier must give off-site and remote support, and only when off-site support is not sufficient, then on-site support will be required upon approval by SITA representative.

  - Support and Help Desk. After hours helpdesk support is required for the period of the first three months per site during weekdays including weekends and public holidays.

  - Provision for Power Recording Evaluation: Accurate information on the SITA Facilities power factor, load profile and reactive power profile were not available at time of this bid. SITA will provide load data as recorded by Vecto 1 power quality recorders to the Service Provider after contract award. The Service Provider shall be responsible for:

    - Evaluate the load data and determine the most optimal capacitor sizes to obtain a power factor of 0.96.

    - Evaluate the harmonic information and determine if filter banks will be required

    - Determine the size and parameters for the filter bank.

  - For this Bid, the Bidders shall use the sizes as stated in this document for pricing purposes. Any subsequent changes in capacitor sizes and the reactor sizes if required will be negotiated with the successful bidder.

  - Designs and Approvals: Detail design drawings shall be submitted for approval before manufacturing may start.  The design includes interfacing detail with the:

  - New switchgear for current transformers, measurements, protection, alarms and interlocking,

  - Inter tripping to upstream and control,

  - Cable and termination schedules for all power, control and auxiliary supply cables shall be submitted as part of the detail design.

  - Power Factor Systems and controls.

  - Battery Terminal Unit system and controls.

  - Manufacture and Supply: Manufacture and delivery to Site is included in the SOW. The Service Provider shall be responsible for all transport risks and arranging for the necessary site access permits.

  - Factory Acceptance Testing: On completion and approval of all pre-FAT documentation, the switchgear supplier will commence with the functional testing of protection schemes. The employer will be notified at least 2 weeks in advance before FAT commences to allow the employer or their representative to witness these tests. Once these tests are completed, the Employer will verify the test results and request to witness specific items.

  - In addition to the inspection at the OEM factory, the Service Provider shall conduct a full integrated Factory Acceptance Testing in Gauteng South Africa. This FAT shall include the switchgear, protection relays and PLC controller.

  - A detailed FAT plan discussing the FAT procedure, role-players, and showing all intended tests and durations shall be submitted for approval three weeks before the FAT.

  - Once the FAT plan is approved, the FAT dates shall be arranged with the attendees and agreed upon.

  - All Low Voltage wiring shall be point-to-pointed and marked off with a highlighter on the latest set of approved drawings. All changes shall be redlined during the FAT. The redlines shall be updated immediately after the FAT. All internal component model numbers shall be verified and marked off on the component list.

  - All interlocking features shall be demonstrated.

  - Test results from the FAT shall be submitted for approval before signing off and release of the equipment.

  - Installation and Pre-Commissioning: The tests shall include, but not be limited to the following:

  - Inter tripping to upstream and control,

  - Installation and commissioning of the equipment under this scope will be limited to 48 hours per site.

  - Installation of the Switchboard, PFC equipment and BTU, power cables, control cables, auxiliary cables and earthing is included. Any Civil work required to do the installation is included

  - A Detailed SAT plan, detailing the various role players, SAT process, commissioning schedule and check sheets shall be submitted for approval 4 weeks before the actual SAT.

  - On completion of installation (after all the equipment have been installed and set up on site), Site Acceptance Testing (SAT) shall be carried out by the Service Provider and witnessed by the Employer and the Project Manager. The SAT shall include cold and hot Commissioning.

  - All power cables need to be tested as required by SANS 10198 Part 13. Insulation test shall be done on all auxiliary and control cables before final termination. All combinations between cores and cores to earth shall be tested and marked off on a test sheet.

  - After termination, all cable cores shall be point-to-pointed and marked off on the cable and termination schedule.

  - After installation is complete, Control and Interlocking shall be function tested and proofed that all is operating according to design.

  - The Service Provider shall perform a pre-SAT to prove the functionality of the system before SITA representatives and Engineers are requested to witness the full-SAT tests.

  - The Service Provider pre-SAT test results will be reviewed and accepted by SITA appointed Engineers before commencing with the full-SAT tests.

  - Cold Commissioning Requirements. The tests shall include, but not be limited to the following:

    - Cable inspection and pressure testing.

    - CT primary testing and mag curve testing

    - Verification of schematic diagrams and cable & termination schedules.

    - Verification of accuracy of nameplate information and application.

    - Test reports & checklists.

    - Testing of earth continuity to substation earth bar.

    - Inspection and testing to ensure no loose connections on primary or secondary circuits.

    - Check list for cleaning of panels.

  - Hot Commissioning Requirements: The Service Provider shall provide experienced test personnel as well as an experienced and competent test Engineer to undertake and supervise all the commissioning tests.  The test Engineer shall work in conjunction with the Employer’s representatives on site and shall always co-operate with these representatives.

    - Check list for cleaning of panels.

    - All operational tests will be verified by the SITA representatives to ensure that the tests have been performed, and the results were acceptable.

    - Final energisation authority and outage co-ordination will be the responsibility of SITA. If applicable, the Service Provider shall submit a request for outage at least 14 days in advance for any further de-energised testing.

    - As a minimum, the following shall be included as hot commissioning tests:

    - Verify the PFC -bank operation at normal voltage.

    - Measure the current unbalance, monitor system voltages.

    - Sign-Off documentation for the tests.

    - SANS 10142 COC by Master Electrician

#### Skills Transfer and Training

  - The Bidder must provide training on the proposed solution to technical staff and operators to enable SITA to operate and support the product or solution after implementation. The training would be informal.

  - The Bidder to submit all the necessary documentation such as COCs, commissioning sheets, record drawings (as built), operation and maintenance manuals for all the equipment.

#### Regulatory, Quality and Standards

- The Bidder must for the duration of the contract ensure compliance with ISO/IEC General Quality Standards, and Protection of Personal Information Act (POPIA).

- The Bidder must for the duration of the contract ensure compliance with General Quality Standards, ISO 9001.

- The Bidder must for the duration of the contract ensure compliance with the project specification and listed standards:

  - eSDHS-01288 - SITA Medium Voltage Switchgear Specification

  - eSDHS-01289 - SITA Power Factor Correction Specification

  - eSDHS-01290 - SITA Battery Tripping Units Specification

#### Company and Personnel Security Clearence Requirements

- Company security screening: The Bidder may be required to undergo a company security screening conducted by the State Security Agency (SSA). Should the SSA find the supplier not suitable after the conduct of the security screening, the business relationship will be terminated. The following documentation will be required for the company security screening process to be conducted:

  - Copy of company registration documentation;

  - Copy(ies) of identity documentation of Director(s), Member(s) or Trustee(s);

  - Copy of valid tax clearance certificate.

- Security suitability check for individuals: SITA may, at its own discretion and in line with its policies and procedures, require employees of the supplier to be subjected to a security suitability check before commencement of a project or delivering of a service. The security suitability check is conducted by SITA in order to ensure that individuals meet the minimum-security requirements and also to verify personal information. The supplier will be required to replace any employee(s) who is found to be not suitable after the conduct of the security screening. The following documentation will be required for the security suitability check:

  - Copy of identity document;

  - Copy(ies) of qualification(s) if SITA requires verification thereof;

  - Fingerprints – will be taken electronically;

  - Signed consent form for the conduct of background checks.

- Security clearance: A security clearance, issued by either the SSA or Defence Intelligence (DI) is required if any employee of the supplier will have or may gain access to classified information throughout the duration of the project or in the process of delivering a service. The level of security clearance required – Confidential, Secret or Top Secret, will be determined at the sole discretion of SITA. The supplier will have to replace any employee who do not qualify for a security clearance or is found not suitable by the SSA or DI. The following documentation will be required for the security clearance process:

  - Completed Z204 or DD1057 security clearance application form;

  - Fingerprints;

  - Personal documentation of the applicant, including but not limited to, identity document, passport, marriage certificate (if applicable), divorce order (if applicable), qualifications, salary advice and bank statements.

#### Confidentiality and non -disclosure conditions

- The Bidder, including its management and staff, must before commencement of the Contract, sign a non-disclosure agreement regarding Confidential Information

- Confidential Information means any information or data, irrespective of the form or medium in which it may be stored, which is not in the public domain and which becomes available or accessible to a Party as a consequence of this Contract, including information or data which is prohibited from disclosure by virtue of:

  - the Promotion of Access to Information Act, 2000 (Act no. 2 of 2000);

  - being clearly marked "Confidential" and which is provided by one Party to another Party in terms of this Contract;

  - being information or data, which one Party provides to another Party or to which a Party has access because of Services provided in terms of this Contract and in which a Party would have a reasonable expectation of confidentiality;

  - being information provided by one Party to another Party in the course of contractual or other negotiations, which could reasonably be expected to prejudice the right of the non-disclosing Party;

  - being information, the disclosure of which could reasonably be expected to endanger a life or physical security of a person;

  - being technical, scientific, commercial, financial and market-related information, know-how and trade secrets of a Party;

  - being financial, commercial, scientific or technical information, other than trade secrets, of a Party, the disclosure of which would be likely to cause harm to the commercial or financial interests of a non-disclosing Party; and

  - being information supplied by a Party in confidence, the disclosure of which could reasonably be expected either to put the Party at a disadvantage in contractual or other negotiations or to prejudice the Party in commercial competition; or

  - information the disclosure of which would be likely to prejudice or impair the safety and security of a building, structure or system, including, but not limited to, a computer or communication system; a means of transport; or any other property; or a person; methods, systems, plans or procedures for the protection of an individual in accordance with a witness protection scheme; the safety of the public or any part of the public; or the security of property; information the disclosure of which could reasonably be expected to cause prejudice to the defence of the Republic; security of the Republic; or international relations of the Republic; or plans, designs, drawings, functional and technical requirements and specifications of a Party, but must not include information which has been made automatically available, in terms of the Promotion of Access to Information Act, 2000; and information which a Party has a statutory or common law duty to disclose or in respect of which there is no reasonable expectation of privacy or confidentiality;

- Notwithstanding the provisions of this Contract, no Party is entitled to disclose Confidential Information, except where required to do so in terms of a law, without the prior written consent of any other Party having an interest in the disclosure;

- Where a Party discloses Confidential Information which materially damages or could materially damage another Party, the disclosing Party must submit all facts related to the disclosure in writing to the other Party, who must submit information related to such actual or potential material damage to be resolved as a dispute;

- Parties may not, except to the extent that a Party is legally required to make a public statement, make any public statement or issue a press release which could affect another Party, without first submitting a written copy of the proposed public statement or press release to the other Party and obtaining the other Party's prior written approval for such public statement or press release, which consent must not unreasonably be withheld.

#### Guarantee and Warranties

The Bidder warrants that:

- as at Commencement Date, it has the rights, title and interest in and to the Product or Services to deliver such Product or Services in terms of the Contract and that such rights are free from any encumbrances whatsoever;

- the Product is in good working order, free from Defects in material and workmanship, and substantially conforms to the Specifications, for the duration of the Warranty period;

- during the Warranty period and Extended Warranty periods any defective item or part component of the Product be repaired or replaced within 3 (three) days after receiving a written notice from SITA;

- the Products is maintained during its Warranty Period and Extended Warranty periods at no additional expense to SITA;

- the Product possesses all material functions and features required for SITA’s Operational Requirements;

- the Product remains connected or Service is continued during the term of the Contract;

- all third-party warranties that the Bidder receives in connection with the Products including the corresponding software and the benefits of all such warranties are ceded to SITA without reducing or limiting the Bidder’s obligations under the Contract;

- no actions, suits, or proceedings, pending or threatened against it or any of its third-party Bidders or sub-contractors that have a material adverse effect on the Bidder’s ability to fulfil its obligations under the Contract exist;

- SITA is notified immediately if it becomes aware of any action, suit, or proceeding, pending or threatened to have a material adverse effect on the Bidder’s ability to fulfil the obligations under the Contract;

- any Product sold to SITA after the Commencement Date of the Contract remains free from any lien, pledge, encumbrance or security interest;

- SITA’s use of the Product and Manuals supplied in connection with the Contract does not infringe any Intellectual Property Rights of any third party;

- the information disclosed to SITA does not contain any trade secrets of any third party, unless disclosure is permitted by such third party;

- it is financially capable of fulfilling all requirements of the Contract and that the Bidder is a validly organized entity that has the authority to enter into the Contract;

- it is not prohibited by any loan, contract, financing arrangement, trade covenant, or similar restriction from entering into the Contract;

- the prices, charges and fees to SITA as contained in the Contract are at least as favourable as those offered by the Bidder to any of its other customers that are of the same or similar standing and situation as SITA; and any misrepresentation by the Bidder amounts to a breach of Contract

#### Intellectual Property Rights

  - SITA retains all Intellectual Property Rights in and to SITA's Intellectual Property. As of the Effective Date, the Bidder is granted a non-exclusive license, for the continued duration of this Contract, to perform any lawful act including the right to use, copy, maintain, modify, enhance and create derivative works of SITA's Intellectual Property for the sole purpose of providing the Products or Services to SITA pursuant to this Contract; provided that the Bidder must not be permitted to use SITA's Intellectual Property for the benefit of any entities other than SITA without the written consent of SITA, which consent may be withheld in SITA's sole and absolute discretion. Except as otherwise requested or approved by SITA, which approval is in SITA's sole and absolute discretion, the Bidder must cease all use of SITA's Intellectual Property, at of the earliest of:

    - termination or expiration date of this Contract;

    - the date of completion of the Services; and

  - the date of rendering of the last of the Deliverables.

  - If so required by SITA, the Bidder must certify in writing to SITA that it has either returned all SITA Intellectual Property to SITA or destroyed or deleted all other SITA Intellectual Property in its possession or under its control.

  - SITA, at all times, owns all Intellectual Property Rights in and to all Bespoke Intellectual Property.

  - Save for the license granted in terms of this Contract, the Bidder retains all Intellectual Property Rights in and to the Bidder’s pre-existing Intellectual Property that is used or supplied in connection with the Products or Services.

  - Provide SITA with the compliant safety file.

#### General

- The parties in this Agreement agree that the offer price of all the equipment shall be at the wholesale price or below wholesale price as agreed with the OEM. Should, at any time during the existence of the agreement that the offered price which is higher than the wholesale price or as agreed with the OEM, SITA client shall be entitled to such wholesale price with the exclusion of the mark-up which the reseller may have charged”.

NOTE: These conditions will form part of the contract obligations and Bidders are expected to comply in order for SITA to conclude an agreement with the potential Bidders. Failure to comply during finalisation of a contract may result to disqualification.

#### Counter Conditions

- Bidders’ attention is drawn to the fact that amendments to any of the Bid Conditions or setting of counter conditions by bidders may result in the invalidation of such bids.

#### Fronting

- The SITA supports the spirit of Broad Based Black Economic Empowerment and recognizes that real empowerment can only be achieved through individuals and businesses conducting themselves in accordance with the Constitution and in an honest, fair, equitable, transparent and legally compliant manner. Against this background the SITA will not condone any form of fronting.

- The SITA, in ensuring that bidders conduct themselves in an honest manner will, as part of the bid evaluation processes, conduct or initiate the necessary enquiries/investigations to determine the accuracy of the representation made in bid documents. Should any of the fronting indicators as contained in the Guidelines on Complex Structures and Transactions and Fronting, issued by the Department of Trade and Industry, be established during such enquiry/investigation, the onus will be on the bidder / contractor to prove that fronting does not exist. Failure to do so within a period of 14 days from date of notification may invalidate the bid / contract and may also result in the restriction of the bidder/contractor to conduct business with the public sector for a period not exceeding ten (10) years, in addition to any other remedies SITA may have against the bidder/contractor concerned.

#### Business Continuity and Disaster Recovery Plans

- The bidder confirms that they have written business continuity and disaster recovery plans that define the roles, responsibilities and procedures necessary to ensure that the required services under this bid specification is in place and will be maintained continuously in the event of a disruption to the bidder’s operations, regardless of the cause of the disruption.

#### Bidder Due Diligence

- SITA reserves the right to conduct Bidder due diligence prior to final award or at any time during the Contract period and this may include pre-announced / non-announced site visits. During the due diligence process the information submitted by the bidder will be verified and any misrepresentation thereof may disqualify the bid or Contract in whole or parts thereof.

#### Preference Goal Requirements conditions

- The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

- The Bidder must sustain, or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

- Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report indicating progress against the Bidder’s Preferential commitments within 30 days of the yearly anniversary of the contract.

- Bidders need to keep auditable substantive records / evidence and upon request by SITA/Department must be made available for audit and, or due diligence purposes.

- SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

- SITA reserves the right to verify information / evidence provided by the Bidder.

- SITA/Department reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA/Department for the prior year if the Bidder fails to comply to paragraphs (a), (b) and (c) above.

### Declaration of compliance and acceptance SCC

I (we), the bidder hereby declare that I (we) accept ALL the Special Conditions of Contract as specified in par 4.4 above and shall comply with all stated obligations:

Name of Bidder: _____________________________	Signature: _________________________

Date: ______________

## Costing and Preference Points Evaluation (Stage 4)

### Costing and Preference Evaluation

- In terms of the SITA Preferential Procurement Policy (PPP), the following preference point system is applicable for this Bid:

  - the 80/20 system (80 Price, 20 Specific Goals) for requirements with a Rand value of up to R50 000 000 (all applicable taxes included); or

  - the 90/10 system (90 Price and 10 Specific Goals) for requirements with a Rand value above R50 000 000 (all applicable taxes included).

- The Bidder must complete either the 80/20 or 90/10 preference point system based on the offer submitted by the Bidder and submit proof of documentation required in terms of this tender.

- SITA reserve the right to apply either the 80/20, or 90/10 preference point system based on the following conditions:

  - If the lowest acceptable bid price is up to and including R50 000 000 (all applicable taxes included) then the 80/20 preferential point system will apply to all acceptable bids; or

  - If the lowest acceptable bid price is above R50 000 000 (all applicable taxes included) then the 90/10 preferential point system will apply to all acceptable bids;

- Points will be allocated for each of the Preferential Goal Requirements for this tender as indicated in table 6.

- Points for this tender shall be awarded for:

  - Price; and

  - Preference points for specific goals.

Table 6: Points allocation

| Description | Points | Points |
| --- | --- | --- |
| Price | 80 | 90 |
| Preference points for specific goals | 20 | 10 |
| Total points for Price and preference points for specific goals | 100 | 100 |

### Costing and Pricing Conditions

- South African Pricing

# The total price must be VAT inclusive and be quoted in South African Rand (ZAR).

- Total Price

  - All quoted prices are the total price for the entire scope of required services and deliverables to be provided by the bidder.

  - All additional costs as well as cost of delivery, labour, S&T, overtime, etc. must be included in this bid.

  - All services, accessories, upgrades and options required by the solution or specified by the client must be included in the quoted price. If not included, Bidders will be required to supply these accessories at no cost to the client.

  - All maintenance service costs are inclusive of traveling, labour, material and tools. The Rate must include the specified service pack, and to perform the specified services.

  - All the maintenance services will be on work order basis and actual quantities might change.

  - The indicative corrective maintenance unit rates will be used for payments of corrective/remedial maintenance.

  - Percentage mark-up on materials and outsourced services to be purchased for corrective/remedial maintenance during 24(twenty-four) months maintenance period may not exceed 20%.

  - SITA reserves the right to negotiate pricing with the successful bidder prior to the award as well as envisaged quantities

- These conditions will form part of the Contract between SITA and the bidder. However, SITA reserves the right to include or waive the condition in the Contract.

- The bidder must complete the declaration of acceptance as per par 4.5 below by marking with an “X” either “ACCEPT ALL”, or “DO NOT ACCEPT ALL”, failing which the declaration will be regarded as “DO NOT ACCEPT ALL” and the bid will be disqualified.

### Bid Pricing Schedule

  - Bidders must complete the bid pricing schedule in the Excel spreadsheet format provided and upload this as part of their submission. The Excel spreadsheet consist of (4) FOUR Sheets:

    - Sheet 1: PRICING SCHEDULE_CENTURION

    - Sheet 2: PRICING SCHEDULE_BETA

    - Sheet 3: MAINTENANCE SUPPORT

    - Sheet 4: TOTALS BID PRICING.

Note:

Bidders must complete and submit bid pricing in the provided Excel spreadsheet format, and any pricing schedule submitted in a different format will not be considered.

### Declaration of Acceptance

|  | ACCEPT ALL | DO NOT ACCEPT ALL |
| --- | --- | --- |
| - The bidder declares to ACCEPT ALL the Costing and Pricing conditions as specified in par 4.5.2 above by indicating with an “X” in the “ACCEPT ALL” column, or - The bidder declares to NOT ACCEPT ALL the Costing and Pricing Conditions as specified in par 4.5.2 above by - - Indicating with an “X” in the “DO NOT ACCEPT ALL” column, and; - Provide reason and proposal for each of the condition not accepted. |  |  |
| Comments by bidder: Provide the condition reference, the reasons for not accepting the condition. |  |  |

  - Preference Requirements

- The bidder must complete in full all the PREFERENCE requirements.

- Allocation of points per requirements: The points allocation of bidders’ responses to the requirements will be determined by the completeness, relevance and accuracy of substantiating evidence.

- Points will be allocated for each PREFERENCE requirement as per the criteria set in table 9A or table 9B  based on the offer submitted by the Bidder.

- The bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response. During evaluation, SITA reserves the right to treat substantiation evidence that cannot be located in the bid response, as “NOT COMPLY”. The evidence needs to be attached to Annex A.

- Preference Goal Requirements

  - The Bidder must complete either the 90/10 or 80/20 preference point system based on the offer submitted by the Bidder and submit proof or documentation required in terms of this tender.

  - The specific Preferential Goal Requirements for this tender is indicated in table 7 or table 8 below.

  - The Bidder must indicate their commitment to claim points for each of the preference points by signing at par 4.5 in the Invitation to Bid document.

  - The Bidder must indicate how they claim points for each of the preference points.

  - Failure on the part of a bidder to submit proof or documentation required in terms of this tender to claim preference points for the Preference Goal Requirements for this tender, will be interpreted to mean that preference points are not claimed.

  - The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

  - The Bidder must sustain, or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

  - Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report indicating progress against the Bidder’s Preferential commitments within 30 days of the yearly anniversary of the contract.

  - Bidders need to keep auditable substantive records / evidence and upon request by SITA must be made available for audit and, or due diligence purposes.

  - SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

  - SITA reserves the right to verify information / evidence provided by the Bidder.

  - SITA reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA for the prior year if the Bidder fails to comply to paragraphs (g), (h) and (i) above.

Table 7: Preference Goal Requirements for (80/20) system (Specific Goals)

| Preference Goal Requirement # | Preferential Goal Requirements | Preferential Goal Requirements for (80/20) system |  |  |
| --- | --- | --- | --- | --- |
|  | Preferential Goal Requirements allocated for this tender | Number of points allocated (80/20) system (To be completed by the organ of state) | Substantiating evidence and evidence reference to be completed by bidder. Evaluation per requirement: Each requirement indicated in the table below must be completed and points will be allocated based on the evidence required below for the (80/20) system | Evidence reference for the (80/20) system |
|  | B-BBEE Requirements |  |  |  |
| 1) | B-BBEE Requirements: Promotion of Transformational Objectives. | 10,0 | Evidence: The Bidder must provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for: - Columns A, B, C and D in table 9A # Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act: - B-BBEE certificate (from a SANAS Accredited Agency/thedtic); # or # Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only; - Column D in table 9A # Copy of South African Identification Document (ID); and/ or - Column E in table 9A # Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act. Note: The CIPC (Companies and Intellectual Property Commission) registration documents will also be used as evidence to confirm compliance to the Preferential procurement requirements as part of the evaluation process. Points allocation: Points will be allocated for bidders that meets the requirements as indicated in table 9A in section 4.6. | <provide unique reference to locate (80/20) system substantiating evidence in the bid response – Annex A, section 5.7> |
|  | Specific Goals: | 10,0 |  |  |
| 2) | The promotion of Local Products in line with the PPP. In line with the promotion of Local Products SITA will allocate Preference Points to Bidders whose products contain Local Content and production for Electrical and Telecom cables. | 10,0 | Evidence: Bidder must complete, sign and submit the Local Content Requirements as indicated in Annex D. Points allocation: 0 points = Zero % Local Content; 10 points = 90 % or greater Local Content. | <provide unique reference to locate (80/20) system substantiating evidence in the bid response – Annex A, section 5.11> |
|  | Total Point Allocation: | 20,0 |  |  |

Table 8: Preference Goal Requirements for (90/10) system (Specific Goals)

| Preference Goal Requirement # | Preferential Goal Requirements | Preferential Goal Requirements for (90/10) system |  |  |
| --- | --- | --- | --- | --- |
|  | Preferential Goal Requirements allocated for this tender | Number of points allocated (90/10) system (To be completed by the organ of state) | Substantiating evidence and evidence reference to be completed by bidder. Evaluation per requirement: Each requirement indicated in the table below must be completed and points will be allocated based on the evidence required below for the (90/10) system | Evidence reference for the (80/20) system |
|  | B-BBEE Requirements |  |  |  |
| 1) | B-BBEE Requirements: Promotion of Transformational Objectives. | 5,0 | Evidence: The Bidder must provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for: - Columns A, B, C and D in table 9B # Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act: - B-BBEE certificate (from a SANAS Accredited Agency/thedtic); # or # Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only; - Column D in table 9B # Copy of South African Identification Document (ID); and/ or - Column E in table 9B # Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act. Note: The CIPC (Companies and Intellectual Property Commission) registration documents will also be used as evidence to confirm compliance to the Preferential procurement requirements as part of the evaluation process. Points allocation: Points will be allocated for bidders that meets the requirements as indicated in table 9B in section 4.6. | <provide unique reference to locate (90/10) system substantiating evidence in the bid response – Annex A, section 5.11> |
|  | Specific Goals: | 5,0 |  |  |
| 2) | The promotion of Local Products in line with the PPP. In line with the promotion of Local Products SITA will allocate Preference Points to Bidders whose products contain Local Content and production for Electrical and Telecom cables. | 5,0 | Evidence: Bidder must complete, sign and submit the Local Content Requirements as indicated in Annex D. Points allocation: 0 points = Zero % Local Content; 5 points = 90 % or greater Local Content. | <provide unique reference to locate (90/10) system substantiating evidence in the bid response – Annex A, section 5.11> |
|  | Total Point Allocation: | 10,0 |  |  |

Table 9A: B-BBEE Points as part of the Preference Goal requirements (Preferential Goal Requirements for (80/20) system)

Note: Bidder to select the section for points they wish to claim (Mark as Y=Yes) in the table below.

|  |  |  |  | Ownership of at least 51% of People who are: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Reference # | Contributor Level as defined in the Broad-Based Black Economic Empowerment Act | Local Entity | EME/QSEs | Woman Owned | Youth Owned | Owned by People living with disabilities | Score | Bidder to select the section for points they wish to claim (Mark as Y= Yes) |
|  | (A) | (B) | (C) | (D) | (E) | (F) | (G) |  |
| 1 | Level 1 | 0 | 2 | 4 | 3 | 1 | 10 |  |
| 2 | Level 1 | 0 | 2 | 4 | 3 | 0 | 9 |  |
| 3 | Level 1 | 0 | 2 | 4 | 0 | 0 | 6 |  |
| 4 | Level 2 and 3 | 0 | 1 | 2 | 1 | 1 | 5 |  |
| 5 | Level 2 and 3 | 0 | 1 | 2 | 1 | 0 | 4 |  |
| 6 | Level 2 and 3 | 0 | 1 | 2 | 0 | 0 | 3 |  |
| 7 | Level 4 and 5 | 0 | 0.,5 | 1 | 0,5 | 0,5 | 2,5 |  |
| 8 | Level 4 and 5 | 0 | 0,5 | 1 | 0.5 | 0 | 2 |  |
| 9 | Level 4 and 5 | 0 | 0,5 | 1 | 0 | 0 | 1.5 |  |
| 10 | Level 6 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 11 | Level 7 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 12 | Level 8 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 13 | Non-Contributor | 0 | 0 | 0 | 0 | 0 | 0 |  |
| Total Maximum Score Allocation: |  |  | 10 |  |  |  |  |  |
| G= A+B+C+D+E+F |  |  |  |  |  |  |  |  |

Table 9B: B-BBEE Points as part of the Preference Goal requirements (Preferential Goal Requirements for (90/10) system)

Note: Bidder to select the section for points they wish to claim (Mark as Y=Yes) in the table below.

|  |  |  |  | Ownership |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Reference # | Contributor Level as defined in the Broad-Based Black Economic Empowerment Act | EME/QSEs | Black Owned | Black Woman Owned | Youth Owned | Owned by People living with disabilities | Score | Bidder to select the section for points they wish to claim |  |
|  |  |  |  | (BO) | (BWO) |  |  |  | (Mark as Y= Yes) |  |
|  |  |  |  | (51% or more) | (More than 30%) |  |  |  |  |  |
|  |  |  | (A) | (B) | (C) | (D) | (E) | (F) |  |  |
|  | 1 | Level 1 | 0,75 | 1,5 | 1,25 | 1 | 0,5 | 5 |  |  |
|  | 2 | Level 1 | 0,75 | 1,5 | 1,25 | 1 | 0 | 4,5 |  |  |
|  | 3 | Level 1 | 0,75 | 1,5 | 1,25 | 0 | 0 | 3,5 |  |  |
|  | 4 | Level 1 | 0,75 | 1,5 | 0 | 0 | 0 | 2,25 |  |  |
|  | 5 | Level 2 and 3 | 0,5 | 1 | 0,5 | 0,25 | 0,25 | 2.5 |  |  |
|  | 6 | Level 2 and 3 | 0,5 | 1 | 0,5 | 0,25 | 0 | 2,25 |  |  |
|  | 7 | Level 2 and 3 | 0,5 | 1 | 0,5 | 0 | 0 | 2 |  |  |
|  | 8 | Level 2 and 3 | 0,5 | 1 | 0 | 0 | 0 | 1,5 |  |  |
|  | 9 | Level 4 and 5 | 0,25 | 0,5 | 0,25 | 0,125 | 0,125 | 1,25 |  |  |
|  | 10 | Level 4 and 5 | 0,25 | 0,5 | 0,25 | 0,125 | 0 | 1.125 |  |  |
|  | 11 | Level 4 and 5 | 0,25 | 0,5 | 0,25 | 0 | 0 | 1 |  |  |
|  | 12 | Level 4 and 5 | 0,25 | 0,5 | 0 | 0 | 0 | 0.75 |  |  |
|  | 13 | Level 6 | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | 14 | Level 7 | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | 15 | Level 8 | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | 16 | Non-Contributor | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | Total Maximum Score Allocation: |  | 5 |  |  |  |  |  |  |  |
|  | F= A+B+C+D+E |  |  |  |  |  |  |  |  |  |  |

Bidder substantiating evidence

# Technical Mandatory Requirement Evidence

## Bidder Certification / Affiliation Requirements

Attach a copy of valid letter from the Department of Labour as evidence that the bidder is registered as an Electrical Contractor here.

NOTE (1):

SITA reserves the right to verify information provided.

## Bidder Experience and Capability Requirements

Complete table below, noting that:

5.2.1	The bidder must have executed at least two (2) projects for the Installation of Primary Indoor Medium Voltage Switchgear and Infrastructure at a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Industrial Plant, Power Utility, Municipality or similar High Availability Environments to at least two (2) customers/projects in the past ten (10) years

5.2.2	The Bidder must provide all of the following information when completing table 10:

  - Company name; and

  - Reference Person Name, Tel and/or email; and

  - Project Scope of Work; and

  - Project Start and End-date.

    - Project end-date must be current or not older than ten (10) years from date this bid is advertised. Scope of work must be related.

Table 10: References

| # No | # Company Name | # Contact person, telephone and/or e-mail address | # Project Scope of Work | # Project start and end date |
| --- | --- | --- | --- | --- |
| # 1 | # <Company name> | # <Person Name> # <Tel> # or # <email> | < Provide scope details was executed> | # Start Date: # End Date: |
| # 2 | # <Company name> | # <Person Name> # <Tel> # or # <email> | < Provide scope details was executed> | # Start Date: # End Date: |

NOTE (1):

The Bidder must provide all of the following information when completing table 10.

NOTE (2):

Failure to comply fully to the requirements as indicated above will result in disqualification.

NOTE (3):

SITA reserves the right to verify information provided.

## CIDB Registration Requirements

The Bidder must complete and sign ANNEX B as evidence that the Bidder is registered with the CIDB with a minimum rating or higher of 7EB or 7EP and attach it here.

## Key Personnel Qualification

Attach to ANNEX A copy of a valid Registration Certificate indicating that the Project Manager has been registered as professional for a minimum five (5) years post professional registration.

The professional registration be either two (2) of the following:

- ECSA, Professional Engineer (Pr Eng), or

- ECSA, Professional Certificated Engineer Technician, or

- ECSA, Professional Engineering Technologist, or

- ECSA, Professional Engineering Technician, or

- PMI, Project Management Professional (PMP), or

- SACPCMP, Professional Construction Project Managers.

NOTE (1):

SITA reserves the right to verify the information provided.

NOTE (2):

SITA reserves the right to verify the consent from the registered person.

NOTE (3):

The Bidder must also provide registered person contact details by completing table 11.

- Attach a copy of the Professional registration certificate here and contact details of the professional registered person:

Table 11: Registered Person Contact Details

| No | Contact person, telephone and/or e-mail address |
| --- | --- |
| 1 | <Person Name> <Tel> or <email> |

## Installation Electrician Requirement

Attach to ANNEX A copy of valid Trade Test Certificate and Wireman’s License indicating that the Installation Electrician is qualified with five (5) years of experience post registrations.

NOTE (1):

SITA reserves the right to verify the information provided.

NOTE (2):

SITA reserves the right to confirm consent of submission from the Installation Electrician.

NOTE (3):

The Bidder must also provide registered person contact details by completing table 12.

Table 12: Installation Electrician Contact Details

| No | Contact person, telephone and/or e-mail address |
| --- | --- |
| 1 | <Person Name> <Tel> or <email> |

## Medium Voltage Technicians Certification Requirement

Attach to ANNEX A copy of valid Certification for each technician indicating that the person is qualified with ten (10) years of experience or a longer post certification.

- ORHVS-Authorised Certificate

- MV Cable Jointing & Terminating Certificate

NOTE (1):

SITA reserves the right to verify the information provided.

NOTE (2):

SITA reserves the right to confirm consent of submission from the Medium Voltage Technician.

NOTE (3):

The Bidder must also provide registered person contact details by completing table 13.

Table 13: Medium Voltage Technicians Contact Details

| # No | # Technicians Experience | # Contact person, telephone and/or e-mail address |
| --- | --- | --- |
| # 1 | # ORHVS-Authorised Person | # <Person Name> # <Tel> # or # <email> |
| # 2 | # MV Cable Jointing & Terminating Person | # <Person Name> # <Tel> # or # <email> |

## Equipment Data Sheets

Attach the following completed and signed Data Sheet here listed in Annex C:

(a)	SITA 11kV Main Board - Switchgear Datasheet_ General Requirements

(b)	SITA Centurion 11kV Main Board - Switchgear Datasheet - Incomer Panel Requirements

(c)	SITA Centurion 11kV Main Board - Switchgear Datasheet - Transformer Feeder Panel Requirements

(d)	SITA 11kV Main Board Switchgear Datasheet - PFC Feeder Panel Requirements

(e)	SITA 11kV Main Board Switchgear Datasheet – Battery Tripping Unit Requirements

(f)	SITA Beta 11kV Main Board Switchgear Datasheet - Incomer Panel Requirements

(g)	SITA Beta 11kV Main Board Switchgear Datasheet - Transformer Feeder Panel

NOTE (1):

SITA reserves the right to verify the information provided.

NOTE (2):

Failure to complete the Data Sheet fully will result in disqualification.

## IEC62271-200 Type Test Certification

Attach a copy of IEC62271-200 Type Test Internal Arc Certification for Primary Distribution Switchgear  here.

## Equipment General Arrangement Drawings

Attach copies of Equipment General Arrangement drawings of the following Single Line Diagram 1001547-0000-DRG-EE-0001 here.

- SITA Centurion 11kV Main Board - Switchgear - Incomer Panel

- SITA Centurion 11kV Main Board - Switchgear - Transformer Feeder Panel

- SITA 11kV Main Board Switchgear - PFC Feeder Panel

- SITA 11kV Main Board Switchgear - Battery Tripping Unit

## Special Conditions of Contract

The Bidder must accept ALL the Special Conditions of Contract by completing and signing the declaration of Acceptance in Declaration of compliance and acceptance under the Special Conditions (Section 4.4.2).

Note (1):

Failure to accept ALL the Special Conditions of Contract will result in disqualification.

# Preference Points Preferential Goals Evidence

The Bidder must:

The Bidder must provide the following Preference Goal Requirements evidence and attach it here:

          - B-BBEE Requirements:

# Promotion of Transformational Objectives

          - Bidder to select the section for points they wish to claim (Mark as Y=Yes) in  table 8  in section 4.6, dependant on which preference system the Bidder selects in line with section 4.6; and

          - Provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for as set out in table 7  in section 4.6 and attach it here:

    - Columns A, B, C and D in table 8

Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act:

- B-BBEE certificate (from a SANAS Accredited Agency);

or

- Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only;

and/ or

    - Column D in table 8:

Copy of South African Identification Document (ID):

and/ or

    - Column E in table 8:

Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act.

Note(3):

The CIPC (Companies and Intellectual Property Commission) registration documents will also be used as evidence to confirm compliance to the Preferential procurement requirements as part of the evaluation process.

          - The promotion of Local Products in line with the PPP.

In line with the promotion of Local Products SITA will allocate Preference Points to Bidders whose products contain Local Content and production for Electrical and Telecom cables.

          - Bidder to select the section for points they wish to claim (Mark as Y=Yes) in table 8 in section 4.6, dependant on which preference system the Bidder selects in line with section 4.6; and

          - Provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for as set out in table 7  in section 4.6 and attach it here:

# Evidence:
Bidder must complete, sign and submit the Local Content Requirements as indicated in Annex D.

# (3)	Indicate their commitment to claim points for each of the preference points by signing at par 4.5 in the Invitation to Bid document.

NOTE (1):

Failure on the part of a bidder to comply to paragraphs (1) and (2) and (3) above, will be interpreted to mean that preference points are not claimed.

CIDB Registration Requirement

The Bidder needs to complete and sign ANNEX B to confirm that the Bidder, is registered with the Construction Industry Development Board (CIDB) with a minimum rating or higher of 7EB, or 7EP.

      - The Bidder needs to indicate the CIDB rating by ticking next to the relevant CIDB rating in the table below:

| Service and Support (Milestones) | CIDB Rating | Bidder to Indicate the Bidder’s rating here |
| --- | --- | --- |
| CIDB Rating | 7EB |  |
|  | 7EP |  |
|  | Higher |  |

      - The Bidder needs to provide the Bidder’s CRS number in the space in the table below:

| Requirement | Bidder’s CRS Number |
| --- | --- |
| Bidder CRS number relating to the minimum rating of 7EB |  |
| Bidder CRS number relating to the minimum rating of 7EP |  |
| Bidder’s CRS number relating to the higher rating of EB or EP |  |

      - The Bidder confirms and will ensure compliance to the CIDB Basic Guide General Conditions of Contract for Construction Works (GCC 2004) as referred to in Annex E for the Bid Specification Scope of work for the duration of the contract.

NOTE 1:

SITA reserves the right to verify the information.

I, the Supplier (Full names) …………………………………………………. Representing (company name) …………………………………………………………….. hereby confirm that the Bidder is registered with Construction Industry Development Board (CIDB) and understand that it will form part of the contract and is legally binding.

Thus, done and signed at ……………………………………. On this………day of……………….20….

__________________

Signature

Designation:

Technical Information

# Technical Information

## Project Specifications

  - eSDHS-01288 - SITA Medium Voltage Switchgear Specification

  - eSDHS-01289 - SITA Power Factor Correction Specification

  - eSDHS-01290 - SITA Battery Tripping Units Specification

## Project Data Sheets

  - 01 - SITA 11kV Main Board - Switchgear Datasheet_ General Requirements

  - 02 - SITA Centurion 11kV Main Board - Switchgear Datasheet - Incomer Panel Requirements

  - 03 - SITA Centurion 11kV Main Board - Switchgear Datasheet - Transformer Feeder Panel Requirements

  - 04 - SITA 11kV Main Board Switchgear Datasheet - PFC Feeder Panel Requirements

  - 05 - SITA 11kV Main Board Switchgear Datasheet – Battery Tripping Unit Requirements

  - 06 - SITA Beta 11kV Main Board Switchgear Datasheet - Incomer Panel Requirements

  - 07 - SITA Beta 11kV Main Board Switchgear Datasheet - Transformer Feeder Panel Requirements

## Project Drawings

  - 1001547-0000-DRG-EE-0001- SITA Centurion: Proposed New 11kv Single Line Diagram

  - 1001668-0000-DRG-EL-0001- SITA Beta: Proposed New 11kv Single Line Diagram

LOCAL CONTENT REQUIREMENTS

# Local Content Requirements:

7.1	The bidder must confirm compliance to the Mandatory Local Content requirements.

7.2	The following documents are attached to guide guidance in completing the Local Content requirements:

- Document 01:	Guidance Document for the Calculation of Local Content.

- Document 02:	South African National Standard:  Local goods, services and work –

Measurement and verification of local content.

7.3	The Bidder must complete, sign and submit the following documents at bid closure:

- Document 03:	SBD 6.2 Declaration Certificate for Local Production and content for

Designated Sectors.

- Document 04:	Annexure C: Local Content Declaration.

7.4 The following Annexures should not be submitted by the bidder, however be kept by the by the bidder and be provide the documents upon request.

- Document 05: 	Annexure D: Imported Content Declaration.

- Document 06: 	Annexure E: Local Content Declaration.

NOTE: Failure to complete, sign and submit the documents as requested in section 7.3 above at bid closing will result in disqualification.

CIDB BASIC GUIDE GENERAL CONDITIONS OF CONTRACT FOR CONSTRUCTION WORKS (GCC 2004)

Refer to Attached document.