[image: image1.png]&M

AR = LNR

¢ in Research and Developmen:




REQUEST FOR QUOTATION FORM FOR GOODS

AND SERVICES

AGRICULTURAL RESEARCH COUNCIL (ARC)

1. You are kindly requested to submit a written quotation ‪‪‪ RFQ-013088 to Agricultural 


Research Council as per below or attached specification.

	Description

	SPECIFICATION FOR UPGRADING OF TRACTOR LAB DYNAMOMETER WATER COOLING PUMP SYSTEM

The water pump cooling system for the tractor lab dynamometer need to be upgraded.

The following specifications is required:

•
Electrical motor and pump combination unit 

•
Pump flow required: 300 litre/min @ 2.5 Bar (18m³/h @ 25 m)

•
3-phase electrical motor (±2.2kW)

•
All Electrical cable from isolators to pumps must be newly installed

•
Pump inlet diameter is 50 mm and outlet is 40 mm

•
Installation and commission included, Use current installation as standard

•
Manufacturing of base plate to fit pump unit

•
All steel work must be Hot Dip Galvanized (Excluding pump and motor)

•
Fit new isolator switches

•
Empty and clean water tank

•
Replace suction filter in water tank (3mm galvanized net mesh) (1.2 X 2 meter)
· Replace water inlet pipe (50mm galv bend & 50mm X 0.5 meter galv straight pipe)
•
Fill up water tank and add 40 litres of anti – rust chemical (same as for car radiator) (2 X 20 litre containers)

Furthermore the pump must be fitted on-site to the existing pipe system.

Two (2) pump units to be installed, one for the cooling tower and one for the dynamometer.

Electrical work must be COC certified.



	Closing date :17 June 2022 at 16:00

	KINDLY ENSURE THAT YOUR COMPANY IS REGISTERED ON CENTRALISED SUPPLIER DATABASE IF NOT ,KINDLY REGISTER ON THIS WEBSITE www.csd.gov.za


2.
The above specified goods/services should be delivered/rendered to: 


Name of Institute
: ARC-IAE

Address

: 141 Creswell Road 





: Weavind Park




: Pretoria 
The particulars of the guarantee that will apply to the goods quoted for,


with particular regard to the period and extent of the warranty must be 


clearly stated. Where services are required, service providers must submit


documentation pertaining the relevant experience.

4.
Your written quotation should be sent to:







Lungile Kubheka






E Mail: KubhekaL@arc.agric.za

5.
All price quotations that have a rand value of R30,000-00 to R50 000 000.00


including VAT, will be evaluated by applying the 80/20 principle as


prescribed by the Preferential Procurement Policy Framework Act 5 of


2000 and its Regulations. The lowest acceptable price will score


80 points, the 20 BBBEE points will be allocated as follows:

	B-BBEE Status

Level of

Contributor
	80/20

	1
	20

	2
	18

	3
	14

	4
	12

	5
	8

	6
	6

	7
	4

	8
	2

	Non-compliant

Contributor
	0


6.
Standard conditions: 

6.1
The validity of the quotations must be indicated.

6.2
Prices quoted should be in South African Rand and inclusive of VAT costs 


such as delivery, insurance, taxes, etc.

6.3
No price adjustments or amendment of the delivery particulars contained 


in paragraph 2 will be considered by the ARC.

6.4
The supplier accepts full responsibility for the proper execution and


fulfilment of the goods/services quoted for.

6.5
ARC reserves the right to accept or reject any special terms and 


conditions that may qualify the goods/services to be provided. 

6.6
Quotes should be submitted on an official letterhead and duly signed

6.7
Goods and services should be supplied/rendered upon receipt of a 


purchase order from the ARC

6.8
The General Conditions of Contract issued by National Treasury are


applicable. 

6.9
The ARC supply chain management code of conduct is applicable.

6.10
SBD Forms must be signed and returned together with the quotation,, failure to comply will result to disqualification of your quotation.

6.11
Your quotation must indicate the delivery date.

6.12
The ARC reserve the right to do due diligence on the quotations.

6.13
The ARC reserve the right to benchmark prices quoted.
Compulsory requirements

· Valid tax PIN number from SARS.

· Central Supplier Database report (Current and updated CSD report) showing a tax compliant status for the duration of the bidding process.

· Complete and sign the Standard Bidding Documents (SBD forms)

Thank you in anticipation

Supply Chain Management: ARC



Page 2 of 3

