STATE INFORMATION TECHNOLOGY AGENCY (SOC) LTD

Registration number 1999/001899/30

BID SPECIFICATION

| RFB REF. NO: | RFB 2590-2022 |
| --- | --- |
| DESCRIPTION | PROVIDE PREVENTATIVE AND CORRECTIVE INFRASTRUCTURE MAINTENANCE TO THE SOUTH AFRICAN POLICE SERVICE SWITCHING CENTRES AND NODAL POINT SITES FOR A PERIOD OF THREE (3) YEARS |
| PUBLICATION DATE: | 22 JUNE 2022 |
| VENDOR BRIEFING SESSION | Compulsory Briefing Session will be held as follows: Date: 28 June 2022 Time: 10:00 Place: Microsoft Teams NOTE: THE COMPULSORY BRIEFING SESSION WILL BE DONE VIRTUALLY. KINDLY RSVP (shalati.mabunda@sita.co.za) BEFORE THE 27 JUNE 2022 AT 12H00 PM VIA EMAIL FOR THE LINK |
| CLOSING DATE FOR QUESTIONS / QUERIES | 05 JULY 2022 |
| RFB CLOSING DETAILS | DATE: 14 JULY 2022 TIME: 11:00 am (SOUTH AFRICAN TIME) |
| PUBLIC OPENING OF RFB RESPONSES | N/A |
| RFB VALIDITY PERIOD | 120 DAYS FROM THE CLOSING DATE |

PROSPECTIVE BIDDERS MUST REGISTER ON NATIONAL TREASURY’S CENTRAL SUPPLIER DATABASE PRIOR TO SUBMITTING BIDS.

Contents

ANNEX A:	INTRODUCTION	3

1.	PURPOSE AND BACKGROUND	3

1.1.	PURPOSE	3

1.2.	BACKGROUND	3

2.	SCOPE OF BID	3

2.1.	SCOPE OF WORK	3

2.2.	DELIVERY ADDRESS	3

2.3.	CUSTOMER INFRASTRUCTURE AND ENVIRONMENT REQUIREMENTS	3

3.	REQUIREMENTS	4

3.1.	PRODUCT/ SERVICE / SOLUTION REQUIREMENTS	4

4.	BID EVALUATION STAGES	4

ANNEX A.1:	ADMINISTRATIVE PRE-QUALIFICATION	5

5.	ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS	5

5.1.	ADMINISTRATIVE PRE-QUALIFICATION VERIFICATION	5

5.2.	ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS	5

6.	TECHNICAL MANDATORY	6

6.1.	INSTRUCTION AND EVALUATION CRITERIA	6

6.2.	TECHNICAL MANDATORY REQUIREMENTS	6

6.3.	DECLARATION OF COMPLIANCE	9

ANNEX A.2:	SPECIAL CONDITIONS OF CONTRACT (SCC)	10

7.	SPECIAL CONDITIONS OF CONTRACT	10

7.1.	INSTRUCTION	10

7.2.	SPECIAL CONDITIONS OF CONTRACT	10

7.3.	DECLARATION OF COMPLIANCE	35

ANNEX A.3:	COSTING AND PRICING	36

8.	COSTING AND PRICING	36

8.1.	COSTING AND PRICING EVALUATION	36

8.2.	COSTING AND PRICING CONDITIONS	36

8.3.	BID PRICING SCHEDULE	37

8.4.	DECLARATION OF ACCEPTANCE	37

ANNEX A.4:	Addresses and Equipment Inventory Schedule	38

9.	Technical Schedules	38

9.1.	SAPS SITE NAMES	38

9.2.	EQUIPMENT INVENTORY SCHEDULE PER SITE	39

ANNEX A.5:	Terms and definitions	62

10.	ABBREVIATIONS	62

ANNEX B:	BIDDER SUBSTANTIATING EVIDENCE	63

11.0	MANDATORY REQUIREMENT EVIDENCE	63

11.1	BIDDER CERTIFICATION / AFFILIATION REQUIREMENTS	63

11.2	BIDDER EXPERIENCE AND CAPABILITY REQUIREMENTS	63

ANNEX C: ADDENDUM 1	64

INTRODUCTION

# PURPOSE AND BACKGROUND

## PURPOSE

The purpose of this RFB is to invite Bidders (hereinafter referred to as “bidders”) to submit bids to “Provide Preventative and Corrective infrastructure maintenance to the South African Police Service Switching Centres and Nodal point sites for a period of three (3) years”

## BACKGROUND

Electronic Communication between SAPS service outlets is achieved by means of the SAPS wide area network (WAN) comprising of approximately 25 major telecommunication Switching Centres and approximately 66 Nodal (secondary) telecommunication centres throughout South Africa.

A typical Switching Centre is equipped with an electric diesel power generator, interruptible power supply unit, HVAC unit, fire suppression system and an environmental monitoring and physical access control system to ensure high availability and security of the telecommunication switching equipment that are housed inside the Switching Centre.

To ensure that the SAPS Switching Centres and Nodal point sites maintain its high availability they require a comprehensive preventative maintenance to be performed at regular intervals.

# SCOPE OF BID

## SCOPE OF WORK

- To provide Preventative Maintenance at regular intervals to the SAPS infrastructure equipment.

- To provide Corrective Maintenance to repair, replace, fix or adjust significant equipment and defects and failures, including the required replacement of significant units, parts, modules and components on an ad-hoc callout basis.

## DELIVERY ADDRESS

Annex A.4 section 9.1 SAPS SITE NAMES

## CUSTOMER INFRASTRUCTURE AND ENVIRONMENT REQUIREMENTS

The equipment to be maintained are –

- Heating, ventilation and air-conditioning (HVAC) subsystem;

- Diesel powered Electric Generators and related electric cables, electric switch gear;

- Uninterruptable Power Supply subsystem (including batteries);

- CCTV systems;

- Access Control systems;

- Fire suppression systems;

- Telecommunication racks and cabinets;

- Environmental monitoring system;

- Electrical distribution boards;

- Container;

Refer to Annex A.4 section 9.2 for complete listing of equipment’s per SAPS Switching Centres, Nodal point sites.

REQUIREMENTS

## PRODUCT/ SERVICE / SOLUTION REQUIREMENTS

To maintain high availability of the SAPS Switching Centres, Nodal point sites by means of:

  - Preventative scheduled maintenance procedures to ensure the stability and reliability of the SAPS infrastructure equipment.

  - Corrective maintenance procedures to restore/replace any critical failed components

# BID EVALUATION STAGES

- The bid evaluation process consists of several stages that are applicable according to the nature of the bid as defined in the table below.

- The bidder must qualify for each stage to be eligible to proceed to the next stage of the evaluation.

| Stage | Description | Applicable for this bid YES/NO |
| --- | --- | --- |
| Stage 1 | Administrative pre-qualification verification | YES |
| Stage 3A | Technical Mandatory requirement evaluation | YES |
| Stage 4 | Special Conditions of Contract verification | YES |
| Stage 5 | Price / B-BBEE evaluation | YES |

ADMINISTRATIVE PRE-QUALIFICATION

# ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS

## ADMINISTRATIVE PRE-QUALIFICATION VERIFICATION

- The bidder must comply with ALL of the bid pre-qualification requirements in order for the bid to be accepted for evaluation.

If the Bidder failed to comply with any of the administrative pre-qualification requirements, or if SITA is unable to verify whether the pre-qualification requirements are met, then SITA reserves the right to-

  - Reject the bid and not evaluate it, or

  - Accept the bid for evaluation, on condition that the Bidder must submit within 7 (seven) days any supplementary information to achieve full compliance, provided that the supplementary information is administrative and not substantive in nature.

## ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS

- Submission of bid response: The bidder has submitted a bid response documentation pack –

  - that was delivered at the correct physical or postal address and within the stipulated date and time as specified in the “Invitation to Bid” cover page, and;

  - in the correct format as one original document, one copy and two copies on memory stick / USB.

Attendance of briefing session: Compulsory Virtual Briefing session is required. The bidder has to sign the briefing session attendance register using the same information (bidder company name, bidder representative person name and contact details) as submitted in the bidder’s response document. The attendance of the briefing session is compulsory.

- Registered Supplier. The bidder is, in terms of National Treasury Instruction Note 4A of 2016/17, registered as a Supplier on National Treasury Central Supplier Database (CSD).

# TECHNICAL MANDATORY

## INSTRUCTION AND EVALUATION CRITERIA

- The bidder must comply with ALL the requirements as per section 6.2 below by providing substantiating evidence in the form of documentation or information, failing which it will be regarded as “NOT COMPLY”.

- The bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response. During evaluation, SITA reserves the right to treat substantiation evidence that cannot be located in the bid response as “NOT COMPLY”.

- The bidder must complete the declaration of compliance as per section 6.3 below by marking with an “X” either “COMPLY”, or “NOT COMPLY” with ALL of the technical mandatory requirements, failing which it will be regarded as “NOT COMPLY”.

- The bidder must comply with ALL the TECHNICAL MANDATORY REQUIREMENTS in order for the bid to proceed to the next stage of the evaluation.

- No URL references or links will be accepted as evidence.

## TECHNICAL MANDATORY REQUIREMENTS

| TECHNICAL MANDATORY REQUIREMENTS | Substantiating evidence of compliance (used to evaluate bid) | Evidence reference (to be completed by bidder) |
| --- | --- | --- |
| - CERTIFICATION: ELECTRICAL CONTRACTOR The Bidder must be registered with the Department of Labour as an Electrical contractor. | Attach to Annex B a copy of a valid documentation (Certificate, letter, or membership card) from the Department of Labour to prove that the bidder is registered as an Electrical Contractor. Note: SITA reserves the right to verify information provided. | <provide unique reference to locate substantiating evidence in the bid response – see Annex B, section 11.1> |
| - PREVIOUS EXPERIENCE AND CAPABILITIES – ELECTRICAL AND MECHANICAL SUPPORT AND MAINTENANCE The Bidder must have executed specialized electrical and mechanical maintenance and support contracts to at least one (1) customer within a High Availability Environment during the past ten (10) years. Environments such as these are considered High Availability Environments but not limited to these environments as long as they are similar in nature: Hospital: Emergency standby power generators, UPS backup systems, Air-conditioning (HVAC) systems, Security access control and CCTV system, Fire prevention and detection system, Environmental monitoring systems; or Airport: Emergency standby power generators, UPS backup systems, Air-conditioning (HVAC) systems, Security access control and CCTV system, Fire prevention and detection system, Environmental monitoring systems; or Bank Data centre: Emergency standby power generators, UPS backup systems, Air-conditioning (HVAC) systems, Security access control and CCTV system, Fire prevention and detection system, Environmental monitoring systems; or Data centers or Switching centers: Emergency standby power generators, UPS backup systems, Air-conditioning (HVAC) systems, Security access control and CCTV system, Fire prevention and detection system, Environmental monitoring systems; or Mine Data centers: Emergency standby power generators, UPS backup systems, Air-conditioning (HVAC) systems, Security access control and CCTV system, Fire prevention and detection system, Environmental monitoring systems; or Municipal Data centers: Emergency standby power generators, UPS backup systems, Air-conditioning (HVAC) systems, Security access control and CCTV system, Fire prevention and detection system, Environmental monitoring systems. | Provide in Annex B reference details for a customer to whom the specialized electrical and mechanical maintenance and support contracts within a similar High Availability Environment was delivered in the past ten (10) years. Note (1): The High availability Environments listed are not limited to these environments as long as the environment is a High Availability Environment which is similar in nature. Note (2): SITA reserves the right to verify information provided. | <provide unique reference to locate substantiating evidence in the bid response – see Annex B, section 11.2> |
| - PRODUCT / SERVICE FUNCTIONAL REQUIREMENT The bidder must confirm compliance to the Service requirements for the bid. | The bidder must confirm compliance to the Service requirements for the bid by completing Annex C: Addendum 1. | <provide unique reference to locate substantiating evidence in the bid response – see Annex B, section 11.3 and Annex C: Addendum 1> |

## DECLARATION OF COMPLIANCE

|  | Comply | Not Comply |
| --- | --- | --- |
| The bidder declares by indicating with an “X” in either the “COMPLY” or “NOT COMPLY” column that – - The bid complies with each and every TECHNICAL MANDATORY REQUIREMENT as specified in SECTION 6.2 above; AND - Each and every requirement specification is substantiated by evidence as proof of compliance. |  |  |

SPECIAL CONDITIONS OF CONTRACT (SCC)

# SPECIAL CONDITIONS OF CONTRACT

## INSTRUCTION

- The successful supplier will be bound by Government Procurement: General Conditions of Contract (GCC) as well as this Special Conditions of Contract (SCC), which will form part of the signed contract with the successful Supplier. However, SITA reserves the right to include or waive the condition in the signed contract.

- SITA reserves the right to –

  - Negotiate the conditions, or

  - Automatically disqualify a bidder for not accepting these conditions.

  - Award to multiple bidders.

- In the event that the bidder qualifies the proposal with own conditions, and does not specifically withdraw such own conditions when called upon to do so, SITA will invoke the rights reserved in accordance with subsection 7.1(2) above.

- The bidder must complete the declaration of acceptance as per section 7.3 below by marking with an “X” either “ACCEPT ALL” or “DO NOT ACCEPT ALL”, failing which the declaration will be regarded as “DO NOT ACCEPT ALL” and the bid will be disqualified.

## SPECIAL CONDITIONS OF CONTRACT

- CONTRACTING CONDITIONS

  - Formal Contract. The Supplier must enter into a formal written Contract (Agreement) with SITA .

  - Right of Award. SITA reserves the right to award the contract for required goods or services to multiple Suppliers.

  - Right to Audit. SITA reserves the right, before entering into a contract, to conduct or commission an external service provider to conduct a financial audit or probity to ascertain whether a qualifying bidder has the financial wherewithal or technical capability to provide the goods and services as required by this tender.

- STATEMENT OF WORK

- PREVENTATIVE MAINTENANCE:

    - Preventive maintenance comprises of a program of activities, performed periodically, on site. This includes checks, searching for abnormalities, abnormality corrections, adjustments, tests, measurements, internal and external cleaning, surveys, as well as the analysis and replacement / repair of units, parts, modules, components, and spare parts to ensure optimal performance, effective performance, and performance according to the Original Equipment Manufacturer’s specifications.

    - Note: If any component fails due to lack preventative maintenance, then the cost of repair must be for the account of the bidder.

    - Provide upgrades and replacement of equipment as per customer requests;

    - Provide service management services, including request management, incident management, problem management, configuration management and service performance management;

    - Provide free in-post training to responsible SAPS and SITA service personnel during scheduled maintenance visits.

    - Provide maintenance administration service, including maintenance planning, records management, spares and consumable inventory management and equipment warranty management.

- Corrective Maintenance Requirements:

    - Corrective Maintenance is carried out to repair, replace, fix or adjust significant equipment and defects and failures, including the required replacement of significant units, parts, modules and components

    - Corrective Maintenance refers to the repair of any breakages and replacement of all consumables and infrastructure as follows but not limited to:

    - UPS batteries

    - PC boards

    - Power supplies

    - Hubble type connectors

    - Lights

    - Radio tower aircraft warning lights

    - Generator mechanical breakages

    - UPS power modules

    - Gas refill

    - Lightning, damage resulting from ordinary use and power spikes (Act of God)

    - Theft

    - The calls for Corrective Maintenance will be logged via a call or when proactively notified.

    - NOTE: Corrective maintenance service agreement on the listed infrastructure equipment as per Pricing Schedule Spreadsheet.

    - Corrective Maintenance is required for a period of 36 months.

- Support and Maintenance Requirements:

    - After the award to the successful bidder he or she must establish back to back agreements with suppliers to ensure any spare parts are available as per maintenance schedule for any SAPS Switching Centre and Nodal point sites equipment that is used by SAPS.

    - The bidder must be capable to provide the related services in all nine (9) provinces.

- PART REPLACEMENT

  - The bidder must provide pricing for the replacement of the equipment as per Annex A.3  8.3 Bid Pricing Schedule. This is classified as Corrective Maintenance.

- DELIVERY ADDRESS

The supplier must deliver the required products or services at as indicated in Annex A.4 section 9.1 SAPS SITE NAMES

- DELIVERY SCHEDULE

  - The full Preventative and Corrective maintenance solution must be implemented within seven (7) days after receipt of an official Purchase Order from SITA.

- SERVICES AND PERFORMANCE METRICS

  - Service providers must adhere strictly to OEM requirements:

  - 1 Hour Maximum Time To Respond (MaxTTResp) will be required.

  - 4 Hour Maximum Time To Repair (MaxTTRep) will be required on all infrastructure.

- MAINTENANCE SCHEDULE

  - Air Conditioning Units

The bidder must provide the following air-conditioning service as per each of the OEM specifications services:

    - The bidder must check service date, recorded run hours, temperature set point and recorded room temperature on a monthly basis.

    - The bidder must check for humidity set point, recorded room humidity and visible alarms Y/N and state alarm types on a monthly basis.

    - The bidder must clean filter, Rinse Humidifier bottle, Check water supply leaks and Check drains for blockages.

    - The bidder must check the condensate drain on steam distributor, check discharge pressure and suction pressure C1 & C2 KPA, check coil fins for blockages and check fan vibration/belt tension and bearing noise.

    - The bidder must check the terminals and wiring check for condenser coil cleanliness, check condenser fan, Evap. Fan Amps L1/L2/L3, Compressor No. 1 & 2 Amps L1/L2/L3 and Humidifier Amps L1/L2/L3.

    - The bidder must ensure in cases where there is an air-conditioner installed in the UPS battery room that it is fully operational and serviced on a monthly basis.

    - The bidder must ensure that the maintenance schedule is followed as non-compliance could invalidate the equipment’s warranty.

The bidder must do the following:

- Isolate unit and check for loose electrical connections

- Check Vacuum circuit board and tighten connections

- Test and check for leaks

- Clean outside condenser coil

- Inspect condition and check operation of condenser fan

- Inspect and test safety pressure switches

- Check and clean evaporator coil (inside)

- Check humidifier. If contaminated, replace evaporator bottle assembly

- Clean filters, if dust - impregnated, replace

- Clean supply fan

- Inspect condensing fan bearings

- Check condensing fan blade for cracks

- Inspect evaporator fan bearings

- Clean drip tray and drain pump (if installed)

- Clean drain pipe to ensure water runs freely

- Check unit for signs of rust – clean and paint necessary

- Straighten fins on coil with fin comb to assist air flow

- Check and Replace all covers and screws

- Restart unit and check that refrigerant is charged

- Clean unit and Re-commission unit

Full Air-conditioning, Direct Expansion Units:

- Do visual and audible check for abnormalities, oil or water leaks, malfunction, etc.

- Check abnormal temperature or vibration on bearings.

- Record details of equipment installed and condition of same.

- Check alarm history on Controller and record on field report.

- Rectify alarm conditions and record. The alarm history shall not be reset.

- Observe any abnormal noise and vibration and rectify.

- Check and adjust temperature settings as necessary

- Record damages / malfunctions.

- Make Recommendations. Issue field report.

- Check / reset differential pressure switches if fitted.

- Air Supply & Condenser Fan(s) – Check for free running. Clean and lubricate.

- Compressors – Check and Run

- Filter Drier – Check temperatures entering / leaving. Replace if necessary. Confirm that the existing filter dryer is of correct capacity for the unit fitted to. Replace if necessary.

- Supply Air – Check for water carry over.

- Condensate Tray and Drain – Check and clean.

- Controls – Check function / alarm history / settings and record data.

- Control – replace controller batteries where required.

- Grilles / Diffusers – Check for damage and blockages as well as corrosion. Fix or replace as necessary.

- Check that condensate water drain in the Pan / Chassis of the unit is clean and free of any obstructions. And that the unit is mounted to a slight angle to facilitate easy drainage.

- Check all belts and belt drives. Adjust as required.

- Check and inspect fan drive and holding down bolts.

- Check functioning of fire dampers on each floor, simulate fire conditions.

- Check operation of expansion valve.

- Check refrigeration system sight glasses for moisture and refrigerant levels.

- Cleaning of all ventilation door, ceiling, wall grilles and diffusers on an ongoing basis.

- Ensure casing is properly sealed.

- Seal around window unit with white silicone if required (if applicable).

- Air Filter(s) – Check condition and / or change / wash if necessary.

- Test for refrigerant leaks.

- Refrigerant – Check LP and HP Pressure. In the event that the pressures are out of specified limits, the bidder shall investigate the root cause and fix.

- Condensing / Evaporating pressures – check, compare to manufacturer requirements and record both the value measured and the manufacturer specified operating value.

- Check High- and Low-Pressure Switches for operation. Reset if necessary.

- Air Heaters – Function test. Replace damaged, warped or burnt-out elements.

- Heater Safety Stat – check function. Reset if tripped.

- Check thermostat functions. Calibrate / repair / replace as required. Check that the thermostat bulb is correctly located in front of the Evaporator coil. And replace if required.

- Treat for rust as required by wire brushing the affected area to expose bare metal, and touch up with an aerosol-type under-coat and two coats of colour-matched finishing coat of aerosol paint. Report major corrosion on unit to client and make recommendation (e.g. galvanized materials to be used).

- When treating for rust the unit must be removed from the vandal cages, in the event that the vandal cages are rusting, clean the rust off with sand paper and wire brush. Paint with cold galvanizing paint and repaint with a silver aluminium paint to ensure protection.

- Check Air-conditioner Control Unit thresholds (max 28 Degrees Celsius, min 18 Degrees Celsius, temp settings)

- Switch the air conditioner off at the circuit breaker. Switch back on and check if the unit restarts automatically at the previous temperature setting. If the unit does not restart automatically, reprogram for automatic restart at previous temperature.

- Record running amps and compare to name plate data.

- Check and record compressor full load operating amperages

- Check insulation on chilled piping for signs of deterioration. Repair/ replace as required.

- Simulate alarms and test the air conditioner environmental alarms with the NOC.

- Ensure that all electrical connections and wiring is secure. Use proper tools.

- Check contactors for burned/ pitted contacts. Rectify as required.

- Check for burnt and discoloured wiring and rectify.

- Brush clean evaporator coils.

- Spray clean evaporator and condenser coil

- Record refrigerant type used.

- Check for coil damage / air obstructions. Straighten coil fins using 'Fin-Comb' tool where required, and clean surfaces of the Condenser and Evaporator coils using a portable air-blower tool. Where 'dry' air-blower cleaning action is not effective make use of water and suitable solvent.

- The bidder must be capable of maintaining down-flow, up-flow, cassette split and chiller plant Air-Conditioning systems; as well as any other make of HVAC units that is used

  - Generators

The bidder must provide the following generator services as per each of the OEM specifications:

    - The bidder must change Engine Oil and Replace Oil Filter. Use manufacturer specified oil respectively.

    - The bidder must check PTO Clutch Adjustment on a quarterly basis. Lubricate PTO Clutch Levers and Linkage if required.

    - The bidder must service the generator’s battery; check Manual Belt Tensioner and Belt Wear.

    - The bidder must clean the Crankcase Vent Tube on a quarterly basis.

    - The bidder must check and repair if necessary the Air Intake Hoses, Connections.

    - The bidder must check and replace the Air filter.

    - The bidder must replace the Fuel Filter Element.

    - The bidder must check the Automatic Belt Tensioner and Belt Wear.

    - The bidder must check the Cooling System and Coolant Solution; analyse and add as require.  Pressure Test Cooling System.

    - The bidder must check the Crankshaft Vibration Dampers. Replace crankshaft damper at 4500 hours or 60 months, whichever occurs first.

    - The bidder must flush the Cooling System.

    - The bidder must check and Adjust Engine Valve Clearance.

    - The bidder must replace the primary air cleaner element when restriction indicator shows a vacuum of 625 mm (25 in.) H2O.

    - The bidder must use COOL-GARD or equivalent and the flushing interval must be done.

    - The bidder must check for water in the generator’s diesel supply tank, this must be performed by means of “water paste”, or by drawing a small quantity of fuel up a pipe for inspection.

    - The bidder must on a monthly basis perform a visual check for any obvious problems, loose parts, leaks etc. on the Generator, the following will specifically be checked:

    - bidder must test the Thermostats.

    - Fuel system for any signs of leaks or damage.

    - The pre-heater for operational status.

    - The oil level at the dipstick.

    - Check water level in radiator.

    - Fuel level should be at least one third full.

    - The Alarm Panel and Controls for normal and error - free conditions.

    - The Battery charging current and voltage for between 1 – 2 amps at 24 volts.

    - Battery cables and connections for continuity and absence of corrosion.

    - A general check will be made for any unsafe or hazardous conditions.

    - Check for any leakages on exhaust and for any liquid on the floor.

    - Check the pressure on all the gauges.

    - Keep a log of the start and finish readings on the hour meter for audit and warrantee purposes.

    - Test the generator’s performance against that of the manufacturer’s specified performance. Adjust and repair where required. (Full details shall be noted in the service pack of what the initial setting was, and what the adjusted setting is).

    - The fuel filters shall be replaced. The replacement date shall be indicated on the filter casing (where casings are part of the filter element).

    - Drain the water sediment (Water Trap) from the fuel filter.

    - Replace all air filters. The replacement date shall be indicated on the filter casing.

    - Change the Oil and Oil Filters. The replacement date shall be indicated on the filter casing.

    - Drain and flush the coolant system and renew the coolant mixture and refill to required operational level. The bidder shall confirm the position of the water supply beforehand.

    - Replace the water caps on the radiators / heat exchangers.

    - Check Alternator connections and tighten if necessary.

    - Check and set tappet clearances.

    - Check and set the start-up fuel mixture.

    - Check automatic belt tensioner (where applicable) and ensure proper operation.

    - Pressures test the cooling system.

    - Test / simulate alarms on protection devices and confirm that the generator(s) stops during these alarm conditions (overheating, low oil pressure, low coolant level, emergency stop).

    - Test / simulate alarms on the Reverse Power Flow Protection System devices and confirm that the generators are protected against reverse power flow under synchronized conditions.

    - Check Diesel Level and record.

    - Check General Condition.

    - Check Drive Belts (where applicable).

    - Check for leaks and repair (water, oil, and others).

    - Replace all rubber hoses with new.

    - Replace all rubber couplings (between pump and motor) on all the pumps with new.

    - Replace all rubber couplings on the heat exchangers with new.

    - Check battery levels, battery terminals, and battery condition. If the battery is older than 12 months, replace.

    - Check operation of Heaters, Battery Trickle Charger and Control Panel. Repair / replace if required.

    - Visually inspect the entire Exhaust System and repair where required. (The bidder does not need to allow for scaffolding).

    - Pressure clean the radiator fins / cooling tower fins.

    - The spray nozzles on the cooling towers shall be inspected for proper operation and be cleaned where required.

    - Manual operated fuel pumps shall be tested for correct operation.

    - Electrical motorized fuel pumps shall be tested for correct operation.

    - Bulk tank fuel pumps and fuel level controls shall be tested for full operation.

    - Confirm the correct operation and accuracy of the cooling circuit temperature meters (where applicable).

    - Clean the entire generator system.

    - Clean below the generator system.

    - Clean the generator plant rooms.

    - Replace all faulty light lamps in the generator rooms.

    - Search for abnormalities, correct abnormalities, make required adjustments so that the plant conform to EOM specifications and operational requirements.

    - Replace the fuel tank’s diesel level indication pipe.

    - The bidder must make sure the generator is on automatic mode on arrival and ensure it is on automatic mode and operational when leaving the site.

    - The bidder must provide runtime specification for generator as per manufacturer’s requirement. Start generator and run generator as per manufacturer’s requirement on a monthly basis.

    - The bidder must simulate power failure by switching off the mains auxiliary switches and let the standby generator start up automatically and let it run for at least 30 minutes on a monthly basis.

    - The bidder must be capable of maintaining any other type and make of generator or power generating technology infrastructure that is used by SAPS.

    - Generators fitted on trailers, maintenance must be provided to the lights, brakes, tyres, and rust on the trailers must be checked and treated on a six-monthly basis to ensure reliability and availability thereof.

    - Once the generator service is completed, the bidder shall:

- After ensuring that all UPS batteries are in a good condition, and that the UPSs have no active Alarms, conduct an Off-load test run on the generator.

- Should the Off-load generator test proof to be successful, conduct a Grid Failure and run the generator plant for 60 minutes. Where the site is fed from a Medium Voltage supply connection, the generator maintenance bidder shall provide a certified high voltage electrician (11 kV and higher) with full protective clothing to conduct the electrical switching for the power failure simulation to test the generators. The associated cost for this MV switching is deemed part of the quoted cost.

- Check the fuel level, battery voltage, oil pressure and engine temperature. If any of these are outside of the acceptable parameters, terminate the test and repair.

- Check turbochargers for excessive noise. Check for cooling phase being activated when shutting down. The generator cool down cycle shall be set to minimum 7 minutes.

- Ensure there are no leaks (fuel, water and oil) or other visible damage.

- Ensure that the plant is in Auto Mode before leaving site.

- The bidder shall perform checks, search for abnormalities, correct abnormalities, make required adjustments so that the plant conform to OEM specifications and operational requirements, and cleaning to ensure that the entire standby generator system shall perform and operate optimally, efficient, and safely.

  - UNINTERRUPTIBLE POWER SUPPLY (UPS)

The bidder must provide the following (UPS) Uninterruptible Power Supply services as per each of the OEM specifications:

    - The bidder must record System input: Voltage.  S1 /Rectifier & S2/Bypass, Current. S1/Rectifier & S2/Bypass, Frequency, Power factor and Power (kW, kVA, kvars) on a monthly basis.

    - The bidder must record System Output: Voltage, Current, Frequency, Power factor, KW Record   Dc: Dc Voltage, Rectifier current, Charger current on a monthly basis.

    - The bidder must listen for strange noises (Fans, Input and Output transformers), Ensure that no alarms are activated, Check the filters on the front door, Check for dust inside the UPS unit, Ensure Static Bypass supply available, Ensure Total Bypass supply available, Ensure Battery backup available, Check all UPS circuits switched on, on a monthly basis.

    - Service provider must ensure that the electronic control and alarm cards are dust free. The bidder   must clean the outside of the cabinet with a damp cloth, do not use cleaning solvents such as mentholated spirits, white spirits or benzene as these will damage the paint finish.

    - The bidder must listen for strange noises (Fans, Input and Output transformers, Ensure Total Bypass supply available, Ensure Static Bypass supply available, Ensure Battery backup available, Measure and note battery bank voltage, 2.25V per cell for vented cells and 2.27V for sealed cells. A 2% tolerance is acceptable for both types of batteries at 20°C.

    - Check general appearance and cleanliness of the battery room. Inspect the batteries for any defects, for e.g. cracks on a monthly basis.

    - Sealed Batteries: Please note cell voltages may differ on cells by 0.12V for the first six months

    - Check that there are no earth fault currents; this must be done on a monthly basis.

    - For separate UPS rooms, the bidder must record room temperature and status of room on a monthly basis.

    - The bidder must on a monthly basis verify that the equipment is within specifications, perform a visual Inspection and ensure that all system components are clean and functioning as they should be. Any problems or warnings related to the UPS must be recorded and a report must be provided to SITA within the same month.

    - The bidder must assess and verify the proper airflow from fans on the UPS on a monthly basis.

    - The bidder must where applicable, check and review the UPS event log for any alarms and record such events for evidence on a monthly basis.

    - The bidder must check all power terminals of equipment under load on a monthly basis.

    - The bidder must perform a discharge test on the UPS on a monthly basis.

    - The bidder must verify proper switch-over of equipment to battery operation, check the individual battery voltages under float and where possible under mains fail conditions on a monthly basis.

    - The bidder must perform Environmental system Inspection: Conduct an inspection of all capacitor banks for damage.  Ensure that all internal control and power wiring is properly seated and free of damage. Where applicable ensure appropriate torque of all internal power connections. Clean UPS and batteries on a monthly basis.

    - The bidder must ensure that on the six-monthly preventive maintenance service visits, that the respective authorized representative from the OEM is present at the SAPS Switching Centres.

    - The bidder must be capable of maintaining any other make of UPS infrastructure that may be used.

    - The bidder must ensure that the following actions will be performed on all UPS’s on a monthly basis:

    - Do a visual test for battery leakages and interconnecting cables fastened.

    - Test battery power by switching the power off and evaluate power distribution to equipment.

    - Once the Diesel Generator is on load, the UPS must be checked to ensure that the UPS batteries return to 100% capacity within ten minutes. Should they continue to discharge, then the incoming mains power must be turned back on, and the test aborted.

    - Test and record power reading switch power back on and ensure all equipment has no alarms.

    - The battery condition can only be determined under discharge conditions. If tested while the UPS is online, the test result will simply be the UPS charger output. The following is suggested:

    - Each UPS units’ batteries will be tested once per year. Connect a dummy load to the UPS units and test the performance of the batteries installed on each UPS. The dummy load must have a rating of minimum 10 kW 3-phase. The bidder shall provide a detailed report of the UPS battery performance

  - CCTV

The bidder must provide the following CCTV services as per each of the OEM specifications:

  - The bidder must ensure execution of the following on a monthly basis:

- Test all camera links to software.

- Test remote access software

- DVR playback examinations are to be conducted to ensure the correct functioning of the system.

- Test recordings.

- Replace faulty lights in all rooms.

- Focus all cameras.

- Reposition all cameras as required.

- Cleaning of lenses on all cameras.

- Interrogation of system logs to determine anomalies

  - The bidder must be capable to service, test and maintain any type of CCTV equipment that may be used by SAPS.

  - Access Control System

The bidder must provide the following Access Control System services as per each of the OEM specifications:

  - The bidder must ensure execution of the following on a monthly basis:

- Inspection of magnetic door locks for functionality and security.

- Cleaning of all biometric readers.

- Integrity testing of biometric readers and card readers.

- Interrogation of system logs to determine anomalies.

  - The bidder must be capable to service, test and maintain any make of access control system that may be used by SAPS.

  - Fire Protection / Prevention System

The bidder must provide the following Fire Protection/Prevention System services as per each of the OEM specifications:

  - The bidder must ensure execution of the following every 3 months

- All smoke detectors will be tested at each inspection.

- All alarm sounders will be tested to ensure correct operation.

- The fire alarm panel will be checked and all functions tested.

- The power supply and batteries will be tested.

- Break glass points and air conditioning units shut down will be checked and all functions tested.

- Gas lock-off and status units will be tested to ensure correct operating sequence.

- Auto / Manual functions will be tested to check correct operation.

- Double knock sequence of events will be tested.

- Check that system functioning correctly on double knock

- Evacuation Sounders operation on double knock activation will be tested to check correct operation.

- FM200 gas cylinder release solenoid will be checked and tested.

- Pressure gauges on gas cylinders checked and gas control status units checked and tested to ensure functioning correctly.

- Gas pressure will be checked

- The VESDA fire monitoring   systems filters will be cleaned and re-calibrated.

- Mains to control panel. (check that "Power fault" appears on alarm panel in the event of a mains fail)

- The Fire system must be tested fully every 12 Months, compliance certificate must be provided.

  - The bidder must be capable of maintaining any other make or model of fire prevention system that is used.

  - Cabinets

The bidder must provide the following Cabinets services as per each of the OEM specifications:

- The bidder must on a monthly basis; check the functionality of the built-in power distribution units installed inside the cabinets.

- The bidder must on a monthly basis; check the functionality of the built-in extractor fans and replace faulty fans.

  - Centralized Building and Environmental Management System

The bidder must provide the following Centralized Building and Environmental system Management System services as per OEM specifications:

- The bidder must on a monthly basis; check the functionality of all components of the Centralized Building and Environmental system management system.

- The bidder must be capable of maintaining any other make or model of Centralized Building and Environmental system management system that is used by SAPS.

- The bidder must check and test the Environmental system monitoring system inclusive of all sensors and replace/calibrate if necessary. The bidder must also provide a log report to SITA for all alarms generated over the period on a monthly basis.

- The service provided must provide a test confirmation report to the NOC confirm that they have received the tested alarms.

  - Servicing of Electrical Distribution Boards

The bidder must provide the following Electrical Distribution Board services:

- Ensure all earth cables are securely connected inside the distribution board.

- Report any obvious missing earths within the distribution board or within two meters from the distribution board.

- Remove the cover on the distribution board to ensure that no cabling has become damaged and that there’s no exposed copper at terminal connections.

- Report any burnt or discoloured wiring inside the distribution board.

- Clear any dust built up on the equipment.

- Clean all components inside distribution boards with electrical cleaning agent (use electrical contact cleaner aerosol; use insulated brushes to remove thick dust).

- Measure respective voltages and record values (especially between Neutral and Earth).

- Ensure all distribution boards are fitted with front panel circuit breaker opening blanks.

- Ensure distribution board covers are closing properly and fastening properly. Replace missing nuts and/or missing/broken closing mechanisms.

- Ensure that all circuits are labelled and noted on the legend card or distribution board.

- Ensure that all circuits going to the Hubble connectors providing power to the cabinets are labelled and noted on the legend card or distribution board.

- Ensure that the distribution board labelling is present and indicate the service and conforms to SANS10142 requirements.

- Ensure that the distribution board is fed as indicated by the existing/new label.

- Inspect distribution board: paintwork, seal, mounting, rust, and water ingress.

- Touch-up paintwork; fix seal; mounting; rust etc. of distribution boards.

- Torque all electrical and earth connections in distribution boards.

- The bidder must scan the electrical connections inside the distribution board by means of an Infra-Red scanner while the distribution boar is on load. The coloured thermal images must be placed in the As Built Pack.

- The bidder must scan each Switchgear unit or Switchgear Cluster inside the distribution board while the distribution boar is on load by means of an Infra-Red scanner. The coloured thermal images of each Switchgear unit or Switchgear Cluster must be placed in the As Built Pack.

- The bidder must issue a Certificate of Compliance as per SANS10142 for the work done on the distribution board and to certify that the relevant electrical distribution board conform to the SANS requirements.

  - Room Maintenance Requirements

The bidder must ensure that all lights are fully functional in the room. Blown lamps must be replaced by the bidder.

- The bidder must meticulously clean the entire room (including walls, doors and floor) upon completion of any service or major works.

- The bidder must repaint the floor to match the existing floor colour, with epoxy floor paint. The bidder must paint demarcation areas on the floor as well, to meet the requirements of the Occupation Health and Safety Act.

- SUB-CONTRACTING

  - Where work is sub contracted to a specialist third party bidder, the Bidder must supervise the work continuously to ensure acceptable quality and to ensure that no risk exist to SITA and ensure no service interruptions to SITA or its clients. The Support Bidder remain fully responsible for the sub bidder’s actions or omission of actions. Penalties or claims for damages caused by the sub-bidder shall be applied to the Support Bidder in full.

- HUMAN RESOURCES

  - The Bidder must ensure the skill sets of its staff. Personnel must be well trained with adequate knowledge and experience, be in possession of the relevant trade certificate, and equipped with all necessary tools and testing facilities to ensure correct and professional operation on all equipment and works to comply with in section 6.2 special conditions of contract: (18) maintenance schedule.

  - The Bidder must be responsible for its staff and they must be equipped with adequate individual safety equipment and personal protective equipment when executing the task.

- CHANGE CONTROL

  - Due to the mission critical SAPS infrastructure that must be available 24x7x365 days, all services or repairs to any SAPS infrastructure equipment that could have an negative impact on service delivery will first have to be approved by the SAPS Change Control committee.

  - After written approval is received from SITA the service provider may proceed with the required work.

- LOSSES

  - The bidder shall be held responsible for any losses caused to SAPS due to the bidder’s or his sub bidder’s actions or absence thereof. Damages shall be recovered from outstanding money’s owed to the bidder. Where outstanding moneys are not sufficient to cover the full loss experienced by SITA, the bidder shall be invoiced for the outstanding moneys.

  - Losses to SAPS shall be determined and be assigned to the maintenance bidder where the balance of probability is more than 50% that the failure or incident was caused by the maintenance bidder’s actions or absence of action.

  - Examples of losses caused to SAPS that shall be recovered from the Contract, could include:

- Fire suppression system triggered by the actions of the bidder and subsequent a fruitless discharge of gas is resulted.

- Work is being performed by the bidder inside the SAPS IT environment and intentionally or unintentionally Network cabling are damaged which causes Network Traffic loss.

- Damage to property during the execution of work.

  - The bidder must have the required insurance cover in place within two weeks from contract commencement and of sufficient value to cover these types of incidences. SITA shall not interact with the maintenance bidder’s underwriter and shall deduct moneys directly as indicated above.

- PENALTIES

  - Should the maintenance bidder not adhere to the SLA time frame specified to Respond (MaxTTResp) to an incident, the penalty to the maintenance bidder shall be equal to 10% of the full value of the Scheduled Maintenance cost for that month for the relevant site (labour and equipment).

  - Should the maintenance bidder not adhere to the SLA time frame specified to Repair (MaxTTRep) of an incident, the penalty to the maintenance bidder shall be equal to 15% of the full value of the Scheduled Maintenance cost for that month for the relevant site (labour and equipment).

  - Should the maintenance bidder not adhere to the SLA time frame specified to Refill (MaxTTResp) of an incident, the penalty to the maintenance bidder shall be equal to 15% of the full value of the Scheduled Maintenance cost for that month for the relevant site (labour and equipment).

  - The penalty for late submission of a RCAs or RFO document shall be equal to 10% of the full value of the Scheduled Maintenance cost for that month for the relevant site (labour and equipment).

  - The above penalties shall be applied at SITA’s discretion, following the breach of a Service Level Agreement. The bidder shall have the opportunity to provide a report, within seven calendar days following the incident or SITA’s notice of penalty, indicating why the bidder deem the penalty not to be applied. SITA shall take this into consideration, but SITA’s decision shall be final and shall deduct penalty values from the monthly invoices for the relevant site(s).

  - Penalties for not adhering to the specified SLA timelines shall be calculated on a sliding scale, and be as follow:

  - Second time not adhering to, for the same site in a three-month period: two times the initial penalty.

  - Third time not adhering to, for the same site in a three-month period: four times the initial penalty.

  - Fourth time not adhering to, for the same site in a three-month period: six times the initial penalty.

  - Fifth and more times time not adhering to, for the same site in a three-month period: ten times the initial penalty.

- DELIVERY TIME-FRAMES AFTER BID AWARD

  - Corrective maintenance and Preventative solution must be implemented within seven (7) days   after receipt of an official purchase order.

- SCOPE OF WORK CHANGES

  - SITA reserves the right to add or remove any SAPS sites from contract on notification done three (3) months in advance.

- SERVICE HISTORY AND INVENTORY SERVICES

  - The service provider must at the end of the contract hand over to SITA the complete maintenance history data set. This will include a complete inventory of all assets and associated service history of all inventory items, engineering drawings and changes thereto, and the condition of each inventory item with regards to its life cycle stage.

- ROUTE CAUSE ANALYSIS AND REASON FOR OUTAGE REPORTS

  - The Reason for Outage (RFO) for SAPS infrastructure failures shall be issued within 12 hours of the failure, by the maintenance bidder.

  - A detailed engineering Root Cause Analysis (RCA) shall be issued within 36 hours of the SAPS infrastructure failure. The following minimum points shall be addressed in the RCA:

- Background leading to the failure

- Engineering reason for failure, which is supported by the Original Equipment Manufacturer?

- If a SLA failure, why the SLA has been breached

- Moneys that shall be credited by the maintenance bidder to SITA as penalty for failure

- How similar failures shall be prevented for this site and other sites under the maintenance bidder’s responsibility

- Time required for permanent repairs

- How the restored system (and other similar systems) shall be tested to make sure similar failures shall not occur.

- Upon SITA’s prior approval, and nature of the component failure, the 36-hour SLA may be extended by SITA to cater for detailed analysis.

  - Technically poor and sub-standard RCAs shall not be accepted and shall be referred back to the maintenance bidder, with the 36hour SLA still intact.

  - Technically acceptable RCAs requiring further explanation shall be referred back to the maintenance bidder, after which another 12-hour window shall be allowed for elaboration on the requested areas.

- FINANCIALS – INVOICES AND JOB CARDS

  - The service provider will be expected at the end of the month to provide two (2) separate invoices (i.e. Preventative and Corrective ):

  - One invoice for the contractual scheduled preventative maintenance work carried out (This one Invoice must have the monthly signed Job cards for all site signed by the supplier and the SITA or SAPS person verifying that the scheduled preventative work was done).

  - All Corrective Maintenance requests from SITA will be based on a work instruction after approval of submitted quote for the corrective maintenance work. Hourly tariff rates to start once bidder is on site.

  - Depending on requests multiple invoices for the Corrective work carried out (The Invoices must have the signed Job cards signed by the supplier and the SITA or SAPS person verifying that the corrective work was done).

  - Should SITA not be satisfied with the quality of the work performed by the bidder, Preventative and or  Corrective work, SITA has the right to reject the work. The Bidder must then redo the work to SITA’s satisfaction at his own cost.

- SUPPLIER PERFORMANCE REPORTING

  - Quarterly meetings to be scheduled between SITA/Client and service provider and also ADHOC meetings from both sided.

  - A monthly report must be submitted to SITA on the first business day of the following month, with the following information:

  - Status of equipment as per maintenance schedule

    - Problems, solutions and risks.

    - Where any downtime occurred the following must be shown:

    - Reason for Outage

    - Date of Outage

    - Time of Outage

    - Total repair time

  - Any irregularities or faults encountered with regards to any component that is a part of the Switching Centre and Nodal point sites must be reported to the responsible SITA representative.

  - A formal report must be submitted to the SITA representative after every service, maintenance or repair; including the relevant job sign-off sheets signed by SITA and the service provider.

  - The service provider must provide a detailed schedule that will be used per site for inspections and maintenance, as well as the processes that will be followed to perform the above-mentioned tasks.

- CERTIFICATION, EXPERTISE AND QUALIFICATION

  - The Supplier represents that,

    - it has the necessary expertise, skill, qualifications and ability to undertake the work required in terms of the Statement of Work or Service Definition and;

    - it is committed to provide the Products or Services; and

    - perform all obligations detailed herein without any interruption to the Customer.

    - at the time of the contracting the intended personnel who will carry out the maintenance have the required qualifications for the following:

    - Electrical (generator, UPS and power distribution boards)

    - HVAC systems

    - Fire detection and prevention system

    - Access control system

    - CCTV system

    - Centralized building and environmental system management system.

    - The Supplier must provide the service in a good and workmanlike manner and in accordance with the practices and high professional standards used in well-managed operations performing services similar to the Services;

    - The Supplier must perform the Services in the most cost-effective manner consistent with the level of quality and performance as defined in Statement of Work or Service Definition;

    - Original Equipment Manufacturer (OEM) or Original Software Manufacturer (OSM) work. The Supplier must ensure that work or service is performed by a person who is certified by Original Equipment Manufacturer or Original Software Manufacturer.

- ELECTRICAL WORK

  - The Bidder must ensure that Electrical Work is performed as prescribed by the Occupation Health and Safety Act (Act 85 of 1993 as amended), Electrical Regulations 2009, including,

  - The person performing the electrical work  is registered at the Department of Labour as an Electrical Bidder;

  - The standard of work conforms to SABS SANS 10142-1: The code of practice for wiring of premises; and

  - Any Electrical installation or alteration is certified after completion of work by means of a Certificate of Compliance.

- SERVICE HISTORY

  - The bidder must insure that the processes and/or procedures and/or systems are in place to track work performed and ensure that the following components:

  - Electrical (generator, UPS and power distribution boards)

  - HVAC systems

  - Fire detection and prevention system

  - Access control system

  - CCTV system

  - Centralized building and environmental system management system receives the specified periodic services, this information must be readily available to SITA at no extra charge.

- HEATING, VENTILATION AND AIR CONDITIONING (HVAC) WORK.

  - The Bidder must ensure the HVAC work is performed as prescribed by the Occupation Health and Safety Act (Act 85 of 1993 as amended), Pressure Equipment Regulations, including,

  - The installation, repair, maintenance or modification to HVAC equipment is performed by a Refrigerant Gas Practitioner in accordance with Pressure Equipment Regulation.

- LOGISTICAL CONDITIONS

  - The service provider shall have a 24/7/365 Technical Call Centre.

  - This Call Centre shall have multiple telecommunication lines and shall have a 100% telecommunication uptime and 100% Information Technology uptime. This Call Centre shall be equipped with backup power sources and shall have a 100% power uptime. The bidder shall have a disaster recovery site to which Call Centre operations can be routed, should the primary Call Centre encounter a disaster. The disaster recovery site shall be operational and functional and be able to manage 25% of the operations within 15 minutes, 50% of the operations within 30 minutes, and able to manage full strength within 60 minutes.

  - The staff manning the bidder’s Call Centre shall have a technical background and understand the Data Centre Environmental system. This Call Centre shall supervise the actions of the technicians on the call out and ensure that the most suitable technical, safe, and economical action is taken to resolve the incident with no risk to SITA and so as to prevent a failure in the SAPS Infrastructure.

  - In the event that SITA’s email system is down, the above correspondence shall revert to telephonic correspondence with telephonic updates.

  - The service provider shall have a proper incident management process in place to ensure that the best possible levels of service quality and availability are maintained.

  - The Maintenance Bidder shall have an External Escalation Matrix in place within one week of contract award to manage external escalations against his Call Centre. The Maintenance Bidder shall also have an Internal Escalation Matrix in place within one week of contract award to indicate to SITA how internal escalations within the Call Centre shall run.

  - Proper problem management needs to be implemented by the bidder to eliminate recurring incidents, and to minimize the impact of incidents that cannot be prevented.

  - Configuration management needs to be implemented to ensure the infrastructure equipment performance, and operational information can be measured throughout its life.

- SKILLS TRANSFER AND TRAINING

  - The Bidder must ensure that the SITA/SAPS technical staff receives the required informal training to ensure the safe operation of the new equipment.

- REGULATORY, QUALITY AND STANDARDS

  - The Supplier must for the duration of the contract ensure compliance with ISO/IEC General Quality Standards, ISO27001, and Protection of Personal Information Act (POPIA).

  - The Supplier must for the duration of the contract ensure compliance with General Quality Standards, ISO 9001

  - The Supplier must for the duration of the contract ensure compliance with SANS standards (SANS 10222-2)

  - Occupational Health and Safety Act, inclusive of the Regulations contained within this Act, with specific reference to the Lead Regulations, Environmental Regulations, Driven Machinery Regulations, Electrical Machinery Regulations, Electrical Installation Regulations and SANS 10142, and Pressure Equipment Regulations.

  - Registered with Department of Labour as Installation Electrician to oversee changes where changes or extensions are made to the electrical installation and to issue a Certificate of Compliance as prescribed by the Occupational Health and Safety Act.

  - Registered as a SAQCC Gas registered refrigerant gas practitioner for the installation, repair or modification and/or maintenance of a refrigeration system

  - National Key Points Act 1980 as amended.

  - Environmental Conservation Act 1989 as amended.

  - SAPS site access and security policy.

  - SAPS Change Control Policy.

  - Any approved new site equipment installations and enhancements of Infrastructure must be quality assured and comply with all applicable SABS standards as well as municipality standards.

  - The safety of SAPS personnel and visitors to SAPS premises must be placed first, at all times and great care must be taken not to damage any infrastructure or equipment.

- PERSONNEL SECURITY CLEARANCE

  - The Supplier personnel who are required to work with GOVERNMENT CLASSIFIED information or access government RESTRICTED areas must be a South African Citizen and at the expense of the Supplier be security vetted (pre-employment screening, criminal record screening and credit screening).

  - The bidder shall be responsible for his own personal security, staff security, and security escort when executing Corrective Maintenance duties. This security cost is deemed part of and included in the contractual rates for full corrective maintenance.

  - The bidder personnel who enter into SAPS restricted areas must adhere to SAPS security standards that are applicable.

  - The Supplier must ensure that the security clearances of all personnel involved in the Contract remains valid for the period of the contract.

  - The Supplier must provide proof of security vetting.

- CONFIDENTIALITY AND NON-DISCLOSURE CONDITIONS

  - The Supplier, including its management and staff, must before commencement of the Contract, sign a non-disclosure agreement regarding Confidential Information.

  - Confidential Information means any information or data, irrespective of the form or medium in which it may be stored, which is not in the public domain and which becomes available or accessible to a Party as a consequence of this Contract, including information or data which is prohibited from disclosure by virtue of:

    - the Promotion of Access to Information Act, 2000 (Act no. 2 of 2000);

    - being clearly marked "Confidential" and which is provided by one Party to another Party in terms of this Contract;

    - being information or data, which one Party provides to another Party or to which a Party has access because of Services provided in terms of this Contract and in which a Party would have a reasonable expectation of confidentiality;

    - being information provided by one Party to another Party in the course of contractual or other negotiations, which could reasonably be expected to prejudice the right of the non-disclosing Party;

    - being information, the disclosure of which could reasonably be expected to endanger a life or physical security of a person;

    - being technical, scientific, commercial, financial and market-related information, know-how and trade secrets of a Party;

    - being financial, commercial, scientific or technical information, other than trade secrets, of a Party, the disclosure of which would be likely to cause harm to the commercial or financial interests of a non-disclosing Party; and

    - being information supplied by a Party in confidence, the disclosure of which could reasonably be expected either to put the Party at a disadvantage in contractual or other negotiations or to prejudice the Party in commercial competition; or

    - information the disclosure of which would be likely to prejudice or impair the safety and security of a building, structure or system, including, but not limited to, a computer or communication system; a means of transport; or any other property; or a person; methods, systems, plans or procedures for the protection of an individual in accordance with a witness protection scheme; the safety of the public or any part of the public; or the security of property; information the disclosure of which could reasonably be expected to cause prejudice to the defence of the Republic; security of the Republic; or international relations of the Republic; or plans, designs, drawings, functional and technical requirements and specifications of a Party, but must not include information which has been made automatically available, in terms of the Promotion of Access to Information Act, 2000; and information which a Party has a statutory or common law duty to disclose or in respect of which there is no reasonable expectation of privacy or confidentiality;

  - Notwithstanding the provisions of this Contract, no Party is entitled to disclose Confidential Information, except where required to do so in terms of a law, without the prior written consent of any other Party having an interest in the disclosure;

  - Where a Party discloses Confidential Information which materially damages or could materially damage another Party, the disclosing Party must submit all facts related to the disclosure in writing to the other Party, who must submit information related to such actual or potential material damage to be resolved as a dispute;

  - Parties may not, except to the extent that a Party is legally required to make a public statement, make any public statement or issue a press release which could affect another Party, without first submitting a written copy of the proposed public statement or press release to the other Party and obtaining the other Party's prior written approval for such public statement or press release, which consent must not unreasonably be withheld.

- GUARANTEE AND WARRANTIES

The Supplier warrants that:

  - In case infrastructure equipment needs to be replaced all relevant guarantees and warranties must be honoured by the service provider.  At expiry of the two-year contract, the service provider will transfer the warranty/guarantee to SAPS.

  - The warranty of goods supplied under this contract remains valid for twelve (12) months after the goods, or any portion thereof as the case may be, have been delivered to and accepted at the final destination indicated in the contract, or for eighteen (18) months after the date of shipment from the port or place of loading in the source country, whichever period concludes earlier;

  - as at Commencement Date, it has the rights, title and interest in and to the Product or Services to deliver such Product or Services in terms of the Contract and that such rights are free from any encumbrances whatsoever;

  - the Product is in good working order, free from Defects in material and workmanship, and substantially conforms to the Specifications, for the duration of the Warranty period;

  - during the Warranty period any defective item or part component of the Product be repaired or replaced within 3 (three) days after receiving a written notice from SITA;

  - the Products is maintained during its Warranty Period at no expense to SITA;

  - the Product possesses all material functions and features required for SITA’s Operational Requirements;

  - the Product remains connected or Service is continued during the term of the Contract;

  - all third-party warranties that the Supplier receives in connection with the Products including the corresponding software and the benefits of all such warranties are ceded to SITA without reducing or limiting the Supplier’s obligations under the Contract;

  - no actions, suits, or proceedings, pending or threatened against it or any of its third-party suppliers or sub-contractors that have a material adverse effect on the Supplier’s ability to fulfil its obligations under the Contract exist;

  - SITA is notified immediately if it becomes aware of any action, suit, or proceeding, pending or threatened to have a material adverse effect on the Supplier’s ability to fulfil the obligations under the Contract;

  - any Product sold to SITA after the Commencement Date of the Contract remains free from any lien, pledge, encumbrance or security interest;

  - SITA’s use of the Product and Manuals supplied in connection with the Contract does not infringe any Intellectual Property Rights of any third party;

  - the information disclosed to SITA does not contain any trade secrets of any third party, unless disclosure is permitted by such third party;

  - it is financially capable of fulfilling all requirements of the Contract and that the Supplier is a validly organized entity that has the authority to enter into the Contract;

  - it is not prohibited by any loan, contract, financing arrangement, trade covenant, or similar restriction from entering into the Contract;

  - the prices, charges and fees to SITA as contained in the Contract are at least as favourable as those offered by the Supplier to any of its other customers that are of the same or similar standing and situation as SITA; and

  - any misrepresentation by the Supplier amounts to a breach of Contract.

- INTELLECTUAL PROPERTY RIGHTS

  - SITA retains all Intellectual Property Rights in and to SITA's Intellectual Property. As of the Effective Date, the Supplier is granted a non-exclusive license, for the continued duration of this Contract, to perform any lawful act including the right to use, copy, maintain, modify, enhance and create derivative works of SITA's Intellectual Property for the sole purpose of providing the Products or Services to SITA pursuant to this Contract; provided that the Supplier must not be permitted to use SITA's Intellectual Property for the benefit of any entities other than SITA without the written consent of SITA, which consent may be withheld in SITA's sole and absolute discretion. Except as otherwise requested or approved by SITA, which approval is in SITA's sole and absolute discretion, the Supplier must cease all use of SITA's Intellectual Property, at of the earliest of:

    - termination or expiration date of this Contract;

    - the date of completion of the Services; and

    - the date of rendering of the last of the Deliverables.

  - If so required by SITA, the Supplier must certify in writing to SITA that it has either returned all SITA Intellectual Property to SITA or destroyed or deleted all other SITA Intellectual Property in its possession or under its control.

  - SITA, at all times, owns all Intellectual Property Rights in and to all Bespoke Intellectual Property.

  - Save for the license granted in terms of this Contract, the Supplier retains all Intellectual Property Rights in and to the Supplier’s pre-existing Intellectual Property that is used or supplied in connection with the Products or Services.

  - Provide SITA with the compliant safety file.

- GENERAL

  - The supplier will be bound by Government Procurement: General Conditions of Contract.

  - (GCC) as well as this Special Conditions of Contract (SCC), which will form part of the signed contract with the Supplier. However, SITA reserves the right to include or waive the condition in the signed contract.

  - SITA reserves the right to:

    - Negotiate the conditions, or

    - Automatically disqualify a bidder for not accepting these conditions.

    - Right to Audit: SITA reserves the right, before entering into a contract, to conduct or commission an external service provider to conduct probity to ascertain whether a qualifying bidder has the technical capability to provide the goods and services as required by this tender.

  - “The parties in this Agreement agree that the offer price of all the equipment shall be at the wholesale price or below wholesale price as agreed with the OEM. Should, at any time during the existence of the agreement that the offered price which is higher than the wholesale price or as agreed with the OEM, SITA client shall be entitled to such wholesale price with the exclusion of the mark-up which the reseller may have charged”.

NOTE: These conditions will form part of the contract obligations and suppliers are expected to comply in order for SITA to conclude an agreement with the potential suppliers. Failure to comply during finalisation of a contract may result to disqualification.

- COUNTER CONDITIONS

Bidders’ attention is drawn to the fact that amendments to any of the Bid Conditions or setting of counter conditions by bidders may result in the invalidation of such bids.

- FRONTING

  - The SITA supports the spirit of Broad Based Black Economic Empowerment and recognizes that real empowerment can only be achieved through individuals and businesses conducting themselves in accordance with the Constitution and in an honest, fair, equitable, transparent and legally compliant manner. Against this background the SITA any form of fronting.

  - The SITA, in ensuring that bidders conduct themselves in an honest manner will, as part of the bid evaluation processes, conduct or initiate the necessary enquiries/investigations to determine the accuracy of the representation made in bid documents. Should any of the fronting indicators as contained in the Guidelines on Complex Structures and Transactions and Fronting, issued by the Department of Trade and Industry, be established during such enquiry/investigation, the onus will be on the bidder / contractor to prove that fronting does not exist. Failure to do so within a period of 14 days from date of notification may invalidate the bid / contract and may also result in the restriction of the bidder/contractor to conduct business with the public sector for a period not exceeding ten (10) years, in addition to any other remedies SITA may have against the bidder/contractor concerned.

- PRODUCT ADHERANCE / MODEL CHANGE

  - In the event where a bidder offers a product/service against an item and the item is subsequently awarded to the bidder, it is required of the contractor to continue to supply the model awarded throughout the contract period.

  - In the event that the product/service is discontinued, SITA Contract Management must be notified of such an occurrence and an official amendment will be issued.

  - In the case where equipment has been discontinued and or replaced with a new product/service, the contractors are required to submit letters from manufacturer/suppliers stating the changes.

  - Furthermore, contractors are to take note that the price of the new product/service should not differ from the current bid price of the original model.

  - The new product/service must adhere to the minimum specification for the item category.

  - Contractors are not to deliver new products/services prior to approval of model changes by the SITA.

- BUSINESS CONTINUITY AND DISASTER RECOVERY PLANS

- The bidder confirms that they have written business continuity and disaster recovery plans that define the roles, responsibilities and procedures necessary to ensure that the required services under this bid specification is in place and will be maintained continuously in the event of a disruption to the bidder’s operations, regardless of the cause of the disruption.

- TARGETED PROCUREMENT/TRANSFORMATION

SITA/SAPS, in terms of the PPPFA Regulation 2017 section 9(1), has an obligation to advance designated groups which includes black SMMEs (i.e. Exempted Micro Enterprises (EME) and Qualifying Small Enterprises (QSE)) for the supply of certain ICT goods or services where feasible to subcontract for a contract above R30m, an organ of state must apply subcontracting to advance designated groups.

- The bidder is required to subcontract a minimum of 30% of the value of the contract to an EME or QSE which is at least 51% owned by black people, or to EMEs and/or QSEs which are at least 51% owned by black women or youth.

- SUPPLIER DUE DILIGENCE

SITA reserves the right to conduct supplier due diligence prior to final award or at any time during the Contract period and this may include pre-announced/ non-announced site visits. During the due diligence process the information submitted by the bidder will be verified and any misrepresentation thereof may disqualify the bid or Contract in whole or parts thereof.

## DECLARATION OF COMPLIANCE

|  | ACCEPT ALL | DO NOT ACCEPT ALL |
| --- | --- | --- |
| - The bidder declares to ACCEPT ALL the Special Condition of Contract as specified in section 7.2 above by indicating with an “X” in the “ACCEPT ALL” column, OR - The bidder declares to NOT ACCEPT ALL the Special Conditions of Contract as specified in section 7.2 above by - - Indicating with an “X” in the “DO NOT ACCEPT ALL” column, and; - Provide reason and proposal for each of the conditions that is not accepted. |  |  |
| Comments by bidder: Provide reason and proposal for each of the conditions not accepted as per the format: Condition Reference: Reason: Proposal: |  |  |

COSTING AND PRICING

# COSTING AND PRICING

## COSTING AND PRICING EVALUATION

- In terms of Preferential Procurement Policy Framework Act (PPPFA), the following preference point system is applicable to all Bids:

  - the 80/20 system (80 Price, 20 B-BBEE) for requirements with a Rand value of up to R50 000 000 (all applicable taxes included); or

  - the 90/10 system (90 Price and 10 B-BBEE) for requirements with a Rand value above R50 000 000 (all applicable taxes included).

- This bid will be evaluated using the preferential point system of 90/10, subject to the following conditions –

  - If the lowest acceptable bid price is up to and including R50 000 000 (all applicable taxes included) then the 80/20 preferential point system will apply to all acceptable bids; or

  - If the lowest acceptable bid price is above R50 000 000 (all applicable taxes included) then the 90/10 preferential point system will apply to all acceptable bids;

- The bidder must complete the declaration of acceptance as per section 8.4 below by marking with an “X” either “ACCEPT ALL”, or “DO NOT ACCEPT ALL”, failing which the declaration will be regarded as “DO NOT ACCEPT ALL” and the bid will be disqualified.

- Bidder will be bound by the following general costing and pricing conditions and SITA reserves the right to negotiate the conditions or automatically disqualify the bidder for not accepting these conditions. These conditions will form part of the Contract between SITA and the bidder. However, SITA reserves the right to include or waive the condition in the Contract.

## COSTING AND PRICING CONDITIONS

- SOUTH AFRICAN PRICING. The total price must be VAT inclusive and be quoted in South African Rand (ZAR).

- TOTAL PRICE

  - All quoted prices are the total price for the entire scope of required services and deliverables to be provided by the bidder.

  - The cost of delivery, labour, S&T, overtime, etc. must be included in this bid.

  - All additional costs must be clearly specified.

- BID EXCHANGE RATE CONDITIONS. The bidders must use the exchange rate provided below to enable SITA to compare the prices provided by using the same exchange rate:

| Foreign currency | South African Rand (ZAR) exchange rate |
| --- | --- |
| 1 US Dollar | R15, 18 |
| 1 Euro | R17,20 |
| 1 Pound | R20,69 |

## BID PRICING SCHEDULE

Note: Bidders will complete the bid pricing schedule in the Excel spreadsheet format provided and include this as part of the submission documents.

SITA reserves the right to negotiate pricing with the successful bidder prior to the award as well as envisaged quantities.

## DECLARATION OF ACCEPTANCE

|  | ACCEPT ALL | DO NOT ACCEPT ALL |
| --- | --- | --- |
| - The bidder declares to ACCEPT ALL the Costing and Pricing conditions as specified in section 8.2 above by indicating with an “X” in the “ACCEPT ALL” column, or - The bidder declares to NOT ACCEPT ALL the Costing and Pricing Conditions as specified in section 8.2 above by - - Indicating with an “X” in the “DO NOT ACCEPT ALL” column, and; - Provide reason and proposal for each of the condition not accepted. |  |  |
| Comments by bidder: Provide the condition reference, the reasons for not accepting the condition. |  |  |

Addresses and Equipment Inventory Schedule

# Technical Schedules

## SAPS SITE NAMES

| No | Site Name (SAPS Switching Centres sites) |
| --- | --- |
| 1 | East London Switching Centre |
| 2 | Mthatha Switching Centre |
| 3 | Port Elizabeth Switching Centre |
| 4 | Bloemfontein Switching Centre |
| 5 | Welkom Switching Centre |
| 6 | Brixton Switching Centre |
| 7 | Germiston Switching Centre |
| 8 | Krugersdorp Switching Centre |
| 9 | Vereeniging Switching Centre |
| 10 | Durban Switching Centre |
| 11 | Empangeni Switching Centre |
| 12 | Hilton Switching Centre |
| 13 | Newcastle Switching Centre |
| 14 | Port Shepstone Switching Centre |
| 15 | Modimolle Switching Centre |
| 16 | Polokwane Switching Centre |
| 17 | Middelburg Switching Centre |
| 18 | Nelspruit Switching Centre |
| 19 | Kimberley Switching Centre |
| 20 | Upington Switching Centre |
| 21 | Potchefstroom Switching Centre |
| 22 | Rustenburg Switching Centre |
| 23 | Maitland Switching Centre |
| 24 | George Switching Centre |
| 25 | Worcester Switching Centre |
| No | Site Name (SAPS Nodal point sites) |
| 1 | Jeffereysbay bldg. Eastern Cape |
| 2 | Zwelitsha bldg. Eastern Cape |
| 3 | Benoni 10111 bldg. East Rand Gauteng |
| 4 | Honeydew bldg. Roodepoort Gauteng |
| 5 | Lyttelton SAPS bldg. Centurion Gauteng |
| 6 | Boschkop bldg. Bronkhorstspruit Gauteng |
| 7 | Tulbach bldg. Pretoria Gauteng |
| 8 | Dube bldg. Pretoria Gauteng |
| 9 | Erasmuskloof bldg. Pretoria Gauteng |
| 10 | Garsfontein bldg. Pretoria Gauteng |
| 11 | JHB Provincial bldg. Johannesburg Gauteng |
| 12 | Mamelodi bldg. Pretoria Gauteng |
| 13 | Midrand 10111 bldg. Midrand Gauteng |
| 14 | Mobile JOCC 1 trailer Johannesburg South |
| 15 | Mobile JOCC 2 trailer Johannesburg South |
| 16 | Newlands bldg. Menlyn Pretoria Gauteng |
| 17 | Pretoria Radio Tech bldg. Pretoria Gauteng |
| 18 | Wagthuis bldg. Pretoria Gauteng |
| 19 | PTA Hawks bldg. Pretoria Gauteng |
| 20 | NAT JOCC bldg. Snake Valley Centurion Gauteng |
| 21 | Persequor Park bldg. Pretoria Gauteng |
| 22 | Silverton Logistics bldg. Silverton Pretoria Gauteng |
| 23 | KZN JOCC bldg. Durban KwaZulu-Natal |
| 24 | Richardsbaai SAPS bldg. KwaZulu-Natal |
| 25 | Servamus bldg. Durban KwaZulu-Natal |
| 26 | Duiwelskloof container. Limpopo |
| 27 | Polokwane 10111 bldg. Polokwane |
| 28 | Seshego container. Polokwane |
| 29 | Middelburg Radio Tech bldg. Mpumalanga |
| 30 | Middelburg SAPS bldg. Mpumalanga |
| 31 | Middelburg 10111 bldg. Mpumalanga |
| 32 | Witrivier 10111 bldg. Mpumalanga |
| 33 | Nelspruit Radio Tech Mpumalanga |
| 34 | Mobile JOCC 5 trailer Eastern Cape |
| 35 | East London 10111 bldg. Eastern Cape |
| 36 | Port Elizabeth 10111 bldg. Eastern Cape |
| 37 | Plattekloof bldg. Cape Town |
| 38 | WC JOCC bldg. Cape Town |
| 39 | Viljoensdrif container Free State |
| 40 | Namakgale container |
| 41 | Laersdrift container |
| 42 | Brixton 10111 SAPS new |
| 43 | Maitland container |
| 44 | Matlala container |
| 45 | Encobo container |
| 46 | Mobile JOCC 4 trailer |
| 47 | Hlogotlou container |
| 48 | Nelspruit JOCC |
| 49 | Port Elizabeth JOCC |
| 50 | Mahikeng 10111 name change |
| 51 | Bloemfontein JOCC |
| 52 | Mfuleni |
| 53 | George Radio Technical |
| 54 | Jeppe DoP |
| 55 | Johannesburg Central SAPS |
| 56 | Roos Senekal SAPS |
| 57 | Welkom 10111 new |
| 58 | Selosesha 10111 new |
| 59 | Phuthaditjhaba 10111 new |
| 60 | Park Road DOCC new |
| 61 | Trompsburg DOCC new |
| 62 | Thabong DOCC new |
| 63 | Zamdela DOCC |
| 64 | Bethelem DOCC new |

## EQUIPMENT INVENTORY SCHEDULE PER SITE

| SAPS SWITCHING CENTERS | QTY |
| --- | --- |
| (1) East London Switching Centre |  |
| Air-conditioner Alliance under ceiling units | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 650KVA Volvo | 2 |
| UPS 600 KVA TESCOM | 2 |
| (2) Mthatha Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 350KVA | 1 |
| UPS 80KVA Gamatronic | 1 |
| (3) Port Elizabeth Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 650KVA Volvo | 2 |
| UPS 600 KVA TESCOM | 2 |
| (4) Bloemfontein Switching Centre | 2 |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 250KVA - Perkins | 1 |
| UPS 80 KVA Gamatronic | 1 |
| (5) Welkom Switching Centre |  |
| Air-conditioner 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 250KVA - Perkins | 1 |
| UPS 80 KVA Gamatronic | 1 |
| (6) Brixton Switching Centre |  |
| Air-conditioner 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 350KVA John Deere | 1 |
| UPS 100 KVA Socomec | 2 |
| (7) Germiston Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 4 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 350KVA John Deere | 1 |
| UPS 100 KVA Socomec | 2 |
| (8) Krugersdorp Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 350KVA John Deere | 1 |
| UPS 100 KVA Sokomec | 2 |
| (9) Vereeniging Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 500 KVA John Deere | 1 |
| UPS 100 KVA Socomec | 2 |
| (10) Durban Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 4 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 500KVA - Perkins | 1 |
| UPS 100 KVA – Gamatronics | 2 |
| (11) Empangeni Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 4 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 500KVA - John Deere | 1 |
| UPS 100 KVA Eaton | 2 |
| (12) Hilton Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 500KVA - John Deere | 1 |
| UPS 100 KVA Eaton | 2 |
| (13) Newcastle Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 33000 BTU | 1 |
| Air-conditioner 80000BTU Uniflair down blower | 2 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 400KVA - John Deere | 1 |
| UPS 120 KVA - Delta | 1 |
| (14) Port Shepstone Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 400KVA John Deere | 1 |
| UPS 100 KVA Gamatronics | 1 |
| (15) Modimolle Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 400KVA John Deere | 1 |
| UPS 100 KVA Delta | 1 |
| (16) Polokwane Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 400KVA John Deere | 1 |
| UPS 80KVA Eaton | 2 |
| (17) Middelburg Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 4 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 400KVA John Deere | 1 |
| UPS 100KVA Socomec | 2 |
| (18) Nelspruit Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 400KVA John Deere | 1 |
| UPS 100KVA Gamatronic | 1 |
| (19) Kimberley Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 350KVA John Deere | 1 |
| UPS 100KVA - Eaton | 1 |
| (20) Upington Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 4 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 250KVA John Deere | 1 |
| UPS 80KVA EATON | 2 |
| (21) Potchefstroom Switching Centre |  |
| Air-conditioner 18000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 400KVA John Deere | 1 |
| UPS 100KVA Eaton | 1 |
| (22) Rustenburg Switching Centre |  |
| Air-conditioner 1x LG 24000 BTU Split unit 1x York 24000 BTU wall type unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 400KVA John Deere | 1 |
| UPS 80KVA Eaton | 2 |
| (23) Maitland Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 4 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 350KVA - Perkins | 1 |
| UPS 100 KVA Gamatronics | 1 |
| (24) George Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 3 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 350KVA - Perkins | 1 |
| UPS 100 KVA – Eaton | 2 |
| (25) Worcester Switching Centre |  |
| Air-conditioner LG 24000 BTU Split unit | 2 |
| Air-conditioner 80000BTU Uniflair down blower | 4 |
| Environmental system BUSICOR | 1 |
| Fire system FM 200/Technoswitch | 1 |
| CCTV Geovision | 1 |
| Biometrics Sagem access control | 3 |
| Generator 350KVA - John Deere | 1 |
| UPS 100 KVA Gamatronic | 1 |

| SAPS NODAL POINTS | QTY |
| --- | --- |
| (1) Jeffereysbay bldg. Eastern Cape |  |
| Generator 250KVA Volvo | 1 |
| (2) Zwelitsha bldg. Eastern Cape |  |
| Generator 600KVA John Deere | 1 |
| UPS 10KVA | 1 |
| (3) Benoni 10111 bldg. East Rand Gauteng |  |
| Generator 400KVA Perkins | 1 |
| Fire system FM 200/Technoswitch | 1 |
| UPS 80KVA APC Galaxy | 1 |
| Air-conditioner 18000 BTU LG Split unit | 2 |
| (4) Honeydew bldg. Roodepoort Gauteng |  |
| Generator 250KVA Volvo | 1 |
| UPS 80KVA APC Galaxy | 2 |
| Air-Con 18000 BTU Carrier wall units | 3 |
| (5) Lyttelton SAPS bldg. Pretoria Gauteng |  |
| Air-conditioner 18000BTU Samsung Split unit | 1 |
| UPS 5KVA APC | 1 |
| Generator 500KVA Cummings | 1 |
| (6) Boschkop bldg. Bronkhorstspruit Gauteng |  |
| Generator 20 KVA Volvo | 1 |
| UPS 10 KVA APC | 1 |
| Air-conditioner 18000 BTU Carrier Split unit | 1 |
| (7) Tulbach bldg. Pretoria Gauteng |  |
| Air-conditioner 80000BTU Airdale down blower | 2 |
| Air-conditioner 12000 BTU LG Split unit | 15 |
| Fire system FM 200/Technoswitch | 1 |
| Generator 550KVA Mitsubishi | 6 |
| Generator 350KVA Volvo | 2 |
| Biometric System Sagem access control | 20 |
| UPS 100KVA APC | 2 |
| (8) Dube bldg. North West |  |
| Generator 10KVA KAIAO | 1 |
| (9) Erasmuskloof bldg. Pretoria Gauteng |  |
| Air-conditioner 35000BTU LG Split unit | 3 |
| Generator 600KVA Volvo and Perkins | 2 |
| UPS 100KVA Gamatronics | 1 |
| (10) Garsfontein bldg. Pretoria Gauteng |  |
| Generator 250KVA John Deere | 1 |
| (11) JHB Provincial bldg. Gauteng |  |
| Generator 600KVA Perkins | 1 |
| (12) Mamelodi bldg. Pretoria Gauteng |  |
| Generator 350KVA Volvo | 1 |
| (13) Midrand 10111 bldg. Gauteng |  |
| Air-conditioner 80000BTU Uniflair down blower | 4 |
| Air-conditioner 24000BTU Samsung Split unit | 2 |
| UPS 40KVA Meissner | 2 |
| UPS 250KVA APC | 4 |
| Generator 800 KVA Mitsubishi | 2 |
| (14) Mobile JOCC 1 trailer JHB |  |
| Air-conditioner 12000BTU LG Split unit | 1 |
| Generator 5KVA Panda | 1 |
| UPS 5KVA APC | 1 |
| (15) Mobile JOCC 2 trailer JHB |  |
| Air-conditioner 12000BTU Carrier Split unit | 1 |
| Generator 5KVA Panda | 1 |
| UPS 5KVA APC | 1 |
| (16) Newlands bldg. Menlyn Gauteng |  |
| Air-conditioner 18000BTU Carrier Split unit | 2 |
| Generator 300KVA Perkins | 2 |
| (17) Pretoria Radio Tech bldg. Gauteng |  |
| Air-conditioner 18000BTU LG Split unit | 4 |
| Generator 150KVA Rolls Royce | 1 |
| (18) Wagthuis bldg. Pretoria Gauteng |  |
| Air-conditioner 80000BTU Airdale down blower | 3 |
| Air-conditioner 50000BTU Samsung Split unit | 3 |
| UPS 120KVA APC | 2 |
| Fire system FM200/ Technoswitch | 1 |
| Biometrics Verdi access control system | 1 |
| (19) PTA Hawks bldg. Pretoria Gauteng |  |
| UPS 100KVA APC | 1 |
| Air-conditioner 1x Carrier 18000 BTU 1x York 24000 BTU | 2 |
| Generator 200KVA John Deere | 1 |
| (20) NAT JOCC bldg. Snake Valley Centurion Gauteng |  |
| Air-conditioner 24000BTU Carrier Split unit | 10 |
| Air-conditioner 18000BTU Carrier Split unit | 2 |
| Generator 350KVA Mindu | 1 |
| UPS 60KVA APC | 1 |
| (21) Persequor Park bldg. Pretoria Gauteng |  |
| Air-conditioner 18000BTU LG Split unit | 3 |
| Air-conditioner 18000BTU Carrier | 2 |
| Generator 500KVA - Perkins | 1 |
| UPS 100KVA - APC | 1 |
| (22) Silverton Logistics bldg. Pretoria Gauteng |  |
| Fire system FM 200/Technoswitch | 1 |
| Air-conditioner 80000BTU Airdale down blower | 1 |
| Air-conditioner 18000BTU LG Split unit | 2 |
| Generator 1600KVA Perkins | 1 |
| Security Verdi access control system | 1 |
| UPS 20KVA – APC | 5 |
| (23) KZN JOCC bldg. KwaZulu-Natal |  |
| Air-conditioner 12000BTU LG Split unit | 1 |
| (24) Richardsbaai SAPS bldg. KwaZulu-Natal |  |
| Generator 350KVA John Deere | 1 |
| (25) Servamus bldg. Durban KwaZulu-Natal |  |
| Air-conditioner 18000BTU Samsung Split unit | 1 |
| Biometric Sagem access control | 1 |
| Generator 1000KVA - MTU | 1 |
| UPS Gamatronic UPS (Not commissioned) | 3 |
| (26) Duiwelskloof container. Limpopo |  |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator Serviced by another SP |  |
| UPS 10KVA - Gamatronics | 1 |
| (27) Polokwane 10111 bldg. Limpopo |  |
| Air-conditioner 18000BTU Jetair Split unit | 2 |
| (28) Seshego container. Limpopo |  |
| Air-conditioner 18000BTU Jetair Split unit | 2 |
| Generator Serviced by another SP | 1 |
| UPS 10KVA – Gamatronics | 1 |
| (29) Middelburg Radio Tech bldg. Mpumalanga |  |
| Generator 10KVA - KAIAO | 1 |
| (30) Middelburg SAPS bldg. Mpumalanga |  |
| Generator 500KVA - Perkins | 1 |
| UPS 80KVA - APC | 2 |
| (31) Middelburg 10111 bldg. Mpumalanga |  |
| Generator 60KVA – John Deere | 1 |
| (32) Witrivier 10111 bldg. Mpumalanga |  |
| Generator 60KVA - Volvo | 1 |
| (33) Nelspruit Radio Tech. Mpumalanga |  |
| Generator Not connected | 1 |
| (34) Mobile JOCC 5 trailer |  |
| Air-conditioner 12000BTU Samsung Split unit | 1 |
| Generator 5KVA PANDA | 1 |
| UPS 5KVA APC | 1 |
| (35) East London 10111 bldg. Eastern Cape |  |
| Generator 250KVA Scania | 1 |
| (36) Port Elizabeth 10111 bldg. Eastern Cape |  |
| Generator 800KVA Perkins | 2 |
| UPS 600 KVA TESCOM | 1 |
| CCTV 32ch Hikvision DVR system | 1 |
| (37) Plattekloof bldg. Cape Town |  |
| UPS 400KVA APC | 2 |
| (38) WC JOCC bldg. Cape Town |  |
| Air-conditioner 24000BTU LG Split unit | 42 |
| Air-conditioner 80000BTU Uniflair down blower | 6 |
| Generator 500KVA John Deere | 1 |
| Biometric Sagem access control | 6 |
| UPS 450KVA APC | 2 |
| (39) Viljoensdrif container Free State |  |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 25KVA - Volvo | 1 |
| UPS 10KVA - Gamatronics | 1 |
| (40) Namakgale container Limpopo |  |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 25KVA - Volvo | 1 |
| UPS 10KVA - Gamatronics | 1 |
| (41) Laersdrift container Mpumalanga |  |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 25KVA - Volvo | 1 |
| UPS 10KVA - Gamatronics | 1 |
| (42) Brixton 10111 Gauteng |  |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 25KVA - Volvo | 1 |
| UPS 10KVA - Gamatronics | 1 |
| (43) Maitland container W-Cape |  |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 25KVA - Volvo | 1 |
| UPS 10KVA - Gamatronics | 1 |
| (44) Matlala container Limpopo |  |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 25KVA - Volvo | 1 |
| UPS 10KVA - Gamatronics | 1 |
| (45) Encobo container Eastern Cape |  |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 25KVA - Volvo | 1 |
| UPS 10KVA - Gamatronics | 1 |
| (46) Mobile JOCC 4 trailer |  |
| Air-conditioner 12000BTU Samsung Split unit | 1 |
| Generator 5KVA PANDA | 1 |
| UPS 5KVA APC | 1 |
| (47) Hlogotlou container Limpopo |  |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 25KVA - Volvo | 1 |
| UPS 10KVA - Gamatronics | 1 |
| (48) Nelspruit JOCC Mpumalanga |  |
| Air-conditioner 12000BTU Samsung Split unit | 1 |
| Generator 5KVA PANDA | 1 |
| UPS 5KVA APC | 1 |
| (49) Port Elizabeth JOCC Eastern Cape |  |
| Air-conditioner 12000BTU Samsung Split unit | 1 |
| Generator 5KVA PANDA | 1 |
| UPS 5KVA APC | 1 |
| Air-conditioner 12000BTU Samsung Split unit | 1 |
| (50) Mahikeng SAPS North West |  |
| UPS 80KVA APC Serviced by another SP | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 100KVA John Deere Serviced by another SP | 1 |
| Biometric Sagem access control | 1 |
| (51) Bloemfontein JOCC Free State |  |
| Air-conditioner 12000BTU Samsung Split unit | 1 |
| Generator 5KVA PANDA | 1 |
| UPS 5KVA APC | 1 |
| (52) Mfuleni SAPS W-Cape |  |
| UPS 100KVA APC Serviced by another SP | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 200KVA John Deere Serviced by another SP | 1 |
| Biometric Sagem access control | 1 |
| (53) George Radio Technical W-Cape |  |
| Air-conditioner 18000BTU LG Split unit | 4 |
| Generator 150KVA Rolls Royce Serviced by another SP | 1 |
| UPS 100KVA APC | 1 |
| Biometric Sagem access control | 1 |
| (54) Jeppe DoP JHB Gauteng |  |
| UPS 100KVA APC Serviced by another SP | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 150KVA John Deere Serviced by another SP | 1 |
| Biometric Sagem access control | 1 |
| (55) Johannesburg Central SAPS Gauteng |  |
| UPS 100KVA APC Serviced by another SP | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 200KVA John Deere Serviced by another SP | 1 |
| Biometric Sagem access control | 1 |
| (56) Roossenekal SAPS Mpumalanga |  |
| UPS 80KVA APC | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 100KVA John Deere | 1 |
| Biometric Sagem access control | 1 |
| (57) Welkom 10111 new |  |
| UPS 100KVA APC Serviced by another SP | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 200KVA John Deere Serviced by another SP | 1 |
| Biometric Sagem access control | 1 |
| (58) Selosesha 10111 new |  |
| UPS 80KVA APC | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 100KVA John Deere | 1 |
| Biometric Sagem access control | 1 |
| (59) Phuthaditjhaba 10111 new |  |
| UPS 80KVA APC | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 100KVA John Deere | 1 |
| Biometric Sagem access control | 1 |
| (60) Park Road DOCC new |  |
| UPS 80KVA APC | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 100KVA John Deere | 1 |
| Biometric Sagem access control | 1 |
| (61) Trompsburg DOCC new |  |
| UPS 80KVA APC | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 100KVA John Deere | 1 |
| Biometric Sagem access control | 1 |
| (62) Thabong DOCC new |  |
| UPS 80KVA APC | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 100KVA John Deere | 1 |
| Biometric Sagem access control | 1 |
| (63) Zamdela DOCC |  |
| UPS 80KVA APC | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 100KVA John Deere | 1 |
| Biometric Sagem access control | 1 |
| (64) Bethelem DOCC new |  |
| UPS 80KVA APC | 1 |
| Air-conditioner 18000BTU Samsung Split unit | 2 |
| Generator 100KVA John Deere | 1 |
| Biometric Sagem access control | 1 |

Terms and definitions

# ABBREVIATIONS

A		Amp

CAD		Computer Aided Design

CD		Compact Disc

CIDB		Construction Industry Development Board

Excl		Excluding

Hz		Hertz

ICT		Information and Communication Technology

Incl		Including

ISO		International Organization for Standardization

kVA		Kilo Volt Ampere

kVAr		Kilo Volt Ampere reactive

kW		Kilo Watt

OEM		Original Equipment   Manufacturer

PPPFA	Preferential Procurement Policy Framework Act

Rpm		Revolutions per Minute

SABS		South African Bureau of Standards

SANS		South African National Standards

SITA		State Information Technology Agency

SLA		Service Level Agreement

UPS		Uninterruptable Power Supply

USB		Universal Serial Bus

V		Volt

SAPS            South African Police Service

PPPFA         Preferential Procurement Policy Framework Act

BIDDER SUBSTANTIATING EVIDENCE

# 11.0	MANDATORY REQUIREMENT EVIDENCE

## BIDDER CERTIFICATION / AFFILIATION REQUIREMENTS

Attach a copy of a valid documentation (Certificate, letter, or membership card) from the Department of Labour as proof that the bidder is registered as an Electrical Contractor here.

## BIDDER EXPERIENCE AND CAPABILITY REQUIREMENTS

Complete table below, noting that:

  - Bidder must provide reference details from at least one (1) customer to whom specialized electrical and mechanical maintenance and support contracts within a High Availability Environment  was delivered, and

  - Project end-date must be current or not older than ten (10) years from date this bid is advertised,

  - Scope of work must be related.

Table 1: References

| No | Company name | Reference Person Name, Tel and/or email | Project Scope of work | Project Start and End-date |
| --- | --- | --- | --- | --- |
| 1 | <Company name> | <Person Name> <Tel> <email> | <Provide details of the project scope for specialized electrical and mechanical maintenance and support contracts within a High Availability Environment was delivered in the past ten (10) years> | Start Date: End Date: |

## 11.3 PRODUCT / SERVICE FUNCTIONAL REQUIREMENT

The bidder must confirm that they comply with the Service Requirements for Preventative and Corrective infrastructure maintenance to the South African Police Service Switching Centres and Nodal point sites by completing Annex C: Addendum 1 and attach it here.

- ANNEX C: ADDENDUM 1

NB:  The bidder must confirm that they comply with the following Technical Mandatory  Functional Requirements  as indicated below as this will be legal contractual binding:

| PREVENTATIVE SERVICE REQUIREMENT: | - Preventive maintenance comprises of a program of activities, performed periodically, on site. This includes checks, searching for abnormalities, abnormality corrections, adjustments, tests, measurements, internal and external cleaning, surveys, as well as the analysis and replacement / repair of units, parts, modules, components, and spare parts to ensure optimal performance, effective performance, and performance according to the Original Equipment Manufacturer’s specifications. |
| --- | --- |
|  | - Note: If any component fails due to lack preventative maintenance, then the cost of repair must be for the account of the bidder. |
|  | - Provide upgrades and replacement of equipment as per customer requests; |
|  | - Provide service management services, including request management, incident management, problem management, configuration management and service performance management; |
|  | - Provide free in-post training to responsible SAPS and SITA service personnel during scheduled maintenance visits. |
|  | - Provide maintenance administration service, including maintenance planning, records management, spares and consumable inventory management and equipment warranty management. |
|  | - Preventive maintenance comprises of a program of activities, performed periodically, on site. This includes checks, searching for abnormalities, abnormality corrections, adjustments, tests, measurements, internal and external cleaning, surveys, as well as the analysis and replacement / repair of units, parts, modules, components, and spare parts to ensure optimal performance, effective performance, and performance according to the Original Equipment Manufacturer’s specifications. |
| CORRECTIVE SERVICE REQUIREMENTS: | - Corrective Maintenance is carried out to repair, replace, fix or adjust significant equipment and defects and failures, including the required replacement of significant units, parts, modules and components |
|  | - Corrective Maintenance refers to the repair of any breakages and replacement of all consumables and infrastructure as follows but not limited to: |
|  | - UPS batteries |
|  | - PC boards |
|  | - Power supplies |
|  | - Hubble type connectors |
|  | - Lights |
|  | - Radio tower aircraft warning lights |
|  | - Generator mechanical breakages |
|  | - UPS power modules |
|  | - Gas refill |
|  | - Lightning, damage resulting from ordinary use and power spikes (Act of God) |
|  | - Theft |
|  | - The calls for Corrective Maintenance will be logged via a call or when proactively notified. |
|  | - NOTE: Corrective maintenance service agreement on the listed infrastructure equipment as per Pricing Schedule Spreadsheet. |
|  | - Corrective Maintenance is required for a period of 36 months. |

I, the bidder (Full names)………………………………………………………….representing (company name)…………………………………………………………….. Hereby confirm that I comply with the above Technical Mandatory Requirements and understand that it will form part of the contract and is legally binding.

Thus done and signed at …………………………………….. On this………day of……………..….20….

……………………………….

Signature

Designation: