# Part 3: Scope of Work

| Document reference | Tutuka Power Station Ash Disposal Facility Volume Increase Civil Works Project – Employer’s Works Information. | No of pages |
| --- | --- | --- |
|  | This cover page | 2 |
| C3.1 | Employer’s Works Information – Ash Disposal Facility Civil Work Project | 174 |
|  | Total number of pages | 176 |

# C3.1: Employer’s works Information

Table of Contents

C3.1: Employer’s works Information	3

1.	Description of the works	7

1.1	Executive Overview	7

1.2	Employer’s Objectives and Purpose of the works	8

1.3	Scope of the works	8

1.3.1	Civil Site Services	11

1.3.2	Dams and Ancillary Works	12

1.3.3	Desilting of the Existing Settling Dam	14

1.3.4	Decommissioning and rehabilitation of the existing Settling Dam	14

1.3.5	Decommissioning and rehabilitation of the existing Clean Dam (South)	15

1.3.6	Overall Site Rehabilitation Works	16

1.4	Interpretation and Terminology	17

1.4.1	List of Definitions	17

1.4.2	List of Abbreviations	18

2.	Management and Start Up	20

2.1	Management Meetings	20

2.2	Documentation Control	22

2.2.1	Documentation Management	22

2.2.2	Drawings Format and Layout	23

2.2.3	Plant Identification	23

2.2.4	Configuration change control	24

2.3	Health and Safety Risk Management	24

2.5	Quality Assurance Requirements	31

2.5.1	General	31

2.5.2	Quality Management Documents Requirements	31

2.5.3	Operational Documents	32

2.5.4	Inspections and Tests	33

2.5.5	Quality Responsibility	34

2.5.6	Non Conformances and Defects	34

2.5.7	Quality Reporting	35

2.5.8	Preservation, shipping and transportation	35

2.6	Programming Constraints	36

2.6.1	General	36

2.6.2	Computerised Planning	36

2.6.3	Planning and Scheduling Levels	37

2.6.4	Planning Programmes	38

2.7	Contractor’s Management, Supervision and Key People	41

2.8	Invoicing and Payment	41

2.9	Insurance Provided by the Employer	43

2.10	Contract Change Management	43

2.11	Provision of Bonds and Guarantees	43

2.12	Records of Defined Cost, Payments & Assessments of Compensation Events to be kept by the Contractor	44

2.13	Training Workshops and Technology Transfer	44

3.	Engineering and the Contractor’s design	45

3.1	Employer’s Design	45

3.1.1	Existing Civil Infrastructure and Areas	45

3.1.2	Civil and Structural Detailed Design Technical Deliverables	45

3.2	Contractor’s Scope of Works	46

3.2.1	Low Pressure Services	46

3.3	Procedure for Submission and Acceptance of Contractor’s design	46

3.3.1	Design Review Procedure	47

3.3.2	Project Engineering Change Procedure	47

3.3.3	Process for Submission of Documents	47

3.3.4	Time Required for Acceptance of Designs	48

3.4	Other Requirements of the Contractor’s design	48

3.4.1	Technical Risk Assessments	48

3.5	Use of Contractor’s design	49

3.6	Design of Equipment	49

3.7	Equipment required to be included in the Works	50

3.8	As-built Drawings, Operating Manuals and Maintenance Schedules	50

3.8.1	Drawing Requirements	51

3.8.2	Data Books	52

4.	Procurement	53

4.1	B-BBEE and Preferencing Scheme	53

4.2	Supplier Development Localisation and Industrialisation (SDL&I)	53

4.3	Subcontracting	56

4.3.1	Preferred Subcontractors	56

4.3.2	Subcontract Documentation, and Assessment of Subcontract Tenders	56

4.3.3	Limitations on Subcontracting	57

4.4	Plant and Materials	57

4.4.1	Quality	57

4.4.2	Plant & Materials provided “free issue” by the Employer	59

4.5	Tests and Inspections before Delivery	61

5.	Construction	63

5.1	Temporary Works, Site Services & Construction Constraints	63

5.1.1	Employer’s Site entry and security control, permits, and Site regulations	63

5.1.2	People restrictions on Site; hours of work, conduct and records	64

5.1.3	Health and safety facilities on Site	64

5.1.4	Environmental controls, fauna & flora, dealing with objects of historical interest	64

5.1.5	Title to materials from demolition and excavation	65

5.1.6	Cooperating With and Obtaining Acceptance of Others	65

5.1.7	Publicity and Progress Photographs	65

5.1.8	Contractor’s Equipment	65

5.1.9	Equipment provided by the Employer	66

5.1.10	Site services and Facilities	66

5.1.11	Facilities provided by the Contractor	68

5.1.12	Survey control and Setting Out of the Works	70

5.1.13	Control of Noise, Dust, Water and Waste	72

5.1.14	Sequences of Construction or Installation	73

5.1.15	Giving Notice of Work to be covered up	75

5.1.16	Hook ups to Existing Works	75

5.2	Completion, Testing, Commissioning and Correction of Defects	75

5.2.1	Work to be done by the Completion Date	75

5.2.2	Use of the Works before Completion has been certified	76

5.2.3	Materials Facilities and Samples for Tests and Inspections	76

5.2.4	Commissioning	76

5.2.5	Start-Up Procedures required to put the Works into Operation	76

5.2.6	Take Over Procedures	77

5.2.7	Access given by the Employer for correction of Defects	77

5.2.8	Performance Tests after Completion	77

5.2.9	Training and Technology Transfer	77

5.2.10	Operational Maintenance after Completion	79

6.	List of Reference Procedures, Standards and Specifications	80

6.1	General	80

6.2	Civil engineering and structural works	82

6.2.1	Variations to the Standardised Specification	83

7.	List of Drawings	172

7.1	Drawings Issued by the Employer	172

7.1.1	Civil and Structural	172

7.2	Documents Issued by the Employer	175

# Description of the works

## Executive Overview

Tutuka Power Station is a six-unit coal fired power plant that produces a total of 3654 MW of electricity. The first unit was connected to the national grid in 1985 and the last unit was connected in 1990. Tutuka Power Station has been in operation for a period of 40 years, and it disposes of burnt boiler Ash in a dry format by means of conveyors and spreaders at the Ash Disposal Facility (ADF).

The Power Station is facing a problem of depleting ashing space. The Employer plans on extending the existing Ash Disposal Facility (ADF) as well as the construction of a new Pollution Control Dam (PCD), Rehabilitated Runoff Dam (RRD) along with the accompanying site services consisting of roads, clean and dirty water channels at the Tutuka Power Station. Only the site services and construction of the dams forms part of this contract, the ADF expansion will be done as a separate contract.

This contract includes the supply, delivery, transportation, handling, storage, construction/installation, commissioning, testing, adjustment, handover in complete working order and upholding during the Defects Liability Period of all Civil works to be incorporated as part of the development of the ADF complex as described below.

The works consist of:

Site Services

- Construction of Dirty Water Runoff Channels from the top of the dump to the dams

- Construction of Rehabilitated Water Runoff Channels from the top of the dump to the dams

- Construction of Clean Water Runoff Channels from the top of the dump to the dams

- The construction of permanent and temporary access roads.

- The construction of permanent and temporary fencing.

Dams

- The construction of the Silt Trap for the Pollution Control Dam

- The construction of the Pollution Control Dam.

- The construction of the Silt Trap for the Rehabilitated Runoff Dam

- The construction of the Rehabilitated Runoff Dam.

Overall Site Rehabilitation Works

- Rehabilitation of all work areas.

Take-Out Options:

- Construction of Dirty Water Runoff Channels from the eastern side of the dump to the dams.

- Construction of dirty stormwater culverts from the eastern side of the dump.

- Construction of permanent access roads on the eastern side of the dump.

- De-silting of the Settling Dam

- Decommissioning and rehabilitation of the existing Settling Dam

- Decommissioning and rehabilitation of the existing Clean Dam South

## Employer’s Objectives and Purpose of the works

The objective of the project is to implement water management infrastructure to support the ashing operations at Tutuka Power Station such that ashing takes place in an environmentally compliant manner. All works shall comply to the gazetted government regulation Government Notice (GN) 704 and the Environmental Management Plan (EMP).

## Scope of the works

The scope of works for the Tutuka Ash higher project can be summarised within the following infrastructure aspects:

The Contractor is referred to the NEC3 ECC C4 Site Information document. It is imperative to note that the site contains existing dams holding ash contaminated water, which cannot be discharged externally (without appropriate treatment) and must be managed entirely within the existing basins. The Employer's Designer has established a management philosophy to address the volume of contaminated water on site. This philosophy encompasses specific temporary works (such as seepage wells, coffer dams, etc) and a carefully prescribed sequencing of construction activities to ensure environmental compliance and safety.

The Contractor is obliged to strictly comply to these stipulated water management requirements; however, the Contractor is welcome to introduce improvements or alternative solutions that can improve the handling of contaminated water. All water management options shall be fully accounted for in the pricing submitted for the contract. Proposed improvements will be evaluated and approved by the Employer's Designer to ensure compliance with overall project objectives and regulatory standards. It is the Contractor's responsibility to implement effective measures for the containment and management of contaminated water throughout the project duration and to ensure that all activities are carried out in a manner that minimizes environmental impact while ensuring site safety.

- Prescribed Temporary Works and Dealing with Water on Site:

- Construction of temporary coffer dam downstream of the Settling Dam.

- Construction of a seepage well downstream of the Settling Dam coffer dam (inclusive of temporary pumping system).

- Construction of a seepage well in the RRD footprint (inclusive of temporary pumping system).

- Continuous water management as detailed in the prescribed sequence of construction for the dams section 5.1.14 during entire construction period for the dams. Provisions should be made to manage considerable water depth in the excavated basins.

Please refer to Section C4 Site information and drawing 0.61/96781-2 (Stormwater Management) for more details on dealing with water on site.

- Site services:

  - Clean, rehabilitated runoff and dirty water channels.  Site clearance, restricted excavations and construction of reinforced concrete channels.

  - Construction of clean, rehabilitated runoff and dirty stormwater culverts.  Restricted excavations, base preparation works, installation of culvert conduits, and backfilling works. Some pipe culverts will be installed using the Pipe-Jacking methodology (under an operational conveyor).

  - Construction/Installation of Inlet and Outlet structures for channels, culverts and pipes.

  - Horizontal drilling of stormwater drainage pipe from planned from the northeast of the ash dump to the south.

  - Permanent and temporary access roads.

  - Permanent and temporary fencing.

- New clean water diversion earth berms either side of dirty water channel No. 4.

- New clean water channel No. 1, from the overland conveyors up to tie into the existing clean water channel southeast of culvert No. 5.

- New clean water channel No. 2, including culvert No. 2.

- New clean water channel No. 3, including pipe culvert No. 12 under the extendible conveyor.

- New concrete dirty water channel No. 1 from overland conveyors to tie into dirty water channel No. 5 including culverts No. 1, 3, 7 and 5.

- New ash-lined dirty water channel No. 2, including pipe culvert No. 04 under the extendible conveyor. Channel to be concrete lined on exit of pipe culvert No.4 to tie into dirty water channel No. 1

- New concrete dirty water channel No. 3, from eastern services battery limit to culvert No. 4, including culvert No. 9.

- New concrete dirty water channel No. 4, from culvert No. 09 to and including culvert No. 8.

- New concrete dirty water channel No. 5 to tie into PCD Silt Trap

- New rehab water channel No. 1, from the top of the ADF through and including culverts No. 10 and, past culvert No.1, 7, 6 & 8, up to the new RRD silt traps, including culvert No’s 6 & 11.

- New concrete rehab water channel No. 2, from eastern services battery limit to tie into the new rehab channel No. 1.

- New fence around the ash dump and dams complex.

- New dual-compartment pollution control dam (PCD) and silt traps.

- New rehab runoff dam (RRD) and silt traps.

- New access road No. 1, from culvert No. 3 to culvert No. 5, tying into the existing Access road at culvert No. 5,

- New access road No. 2 crossing over culvert No. 1

- New access road No. 3 from the eastern services battery limit

- Dams (Pollution Control Dam and Rehabilitated Runoff Dam, according to prescribed sequencing as described in section 5.1.14):

  - Selective and bulk excavation

  - Excavation of subsoil drainage area

  - Construction of temporary coffer dam downstream of settling dam

  - Site clearance and topsoil stripping.

  - Construction of a seepage well downstream of the Settling Dam coffer dam (inclusive of temporary pumping system).

  - Construction of a seepage well in the RRD footprint (inclusive of temporary pumping system).

  - Continuous water management during entire construction period for the dams. As part of the continuous water management requirements, construction shall be in accordance to the prescriptive construction sequencing outlined in Section 5.1.14.

  - Construction of reinforced concrete silt traps reinforced concrete feeder pipes and reinforced concrete inlet structure to each compartment of the dams.

  - Basin bulk excavations for the dams.

  - Restricted excavations for drainage systems and division wall foundation works (including installation of waste rock pioneer layer).

  - Construction of reinforced concrete division wall for the PCD.

  - Construction of earth embankment walls including access ramps for both the PCD and RRD.

  - Installation of subsoil, leak detection and perimeter drainage systems.

  - Basin preparation works. This may entail stabilisation of basin material in unsuitable areas if encountered.

  - Construction of water-tight reinforced concrete floor system.

  - Concrete lining of embankments.

  - Construction of spillways, outlet channel and energy dissipation structures.

  - Construction of reinforced concrete and brickwork pump station.

- Overall site rehabilitation works

The following section may be removed without triggering any contractual claims. The Employer reserves the right to exclude activities listed under the "Take-Out" option, and such exclusions shall not result in any contractual consequences. As a result, the Contractor shall not raise any claims regarding the omission of the stated “Take-Out” option activities.

Take Out Option Activities:

- De-silting of the existing Settling Dam

- New concrete dirty water channel No. 6, from the northeast of the ADF to be terminated at the battery limit to culvert No 13, including culvert No. 13 & 14.

- New access road No. 5 to be terminated at the eastern services battery limit including access road section over culvert No’s 13 & 14.

- Decommissioning and rehabilitation of the existing Settling Dam.

- Decommissioning and rehabilitation of the existing Clean Dam (South).

### Civil Site Services

Refer to Section 2 Site Services Drawings in drawing pack and drawing register

- Clearing and 100mm topsoil removal for all site services infrastructure; channels, access roads and fencing, where applicable.

- Erection of a new high security fence as specified on construction drawings to extend around the works area.

- Excavation and construction of concrete Dirty Water, Rehabilitated Runoff and Clean Water channels for proposed phase as detailed and specified on construction drawings. Channels are mainly 150mm thick fibre reinforced concrete V and trapezoidal shaped channels constructed on G5 material (sourced from commercial sources) compacted as specified on construction drawings.

- Excavation and construction of access roads as detailed on construction drawings. Road layer works consist of a 150mm gravel wearing course (As per TRH14, imported from commercial sources) on two 150mm G5 (SANS, TRH14) (sourced from excavations on site or from commercial sources, if required) layers compacted as specified on construction drawings. All fill material to roadbed levels to be sourced from excavations on site.

- Erection of guard rails along roads as specified on construction drawings.

- Excavation and installation of culvert crossings as detailed on construction drawings for dirty, rehabilitated runoff and clean water channels. Precast concrete portal culverts to be laid on 300mm thick insitu cast concrete bases constructed on 150mm G5 (SANS, TRH14) layer compacted as specified on construction drawings. Culvert installations to include reinforced concrete headwalls as detailed.

- Inlet and outlet structures for channels and pipes.

- Pipe-jacked connecting between channels.

- Horizontal drilling of drainage pipe as shown on Drawing 0.61/96774/1.

- Permanent and temporary access roads.

- Permanent and temporary fencing.

- Preparation works for topsoil and subsoil stockpile areas for proposed works. These areas are to be in line with the Environmental Management Plan (EMP) requirements. Stockpile areas are indicated on Site Services General Arrangement drawings and the Contractor is to plan and design for these areas (including access roads and temporary crossings).

- Rock fill from excavations on site or commercially sourced to be installed in areas of deep soil saturation, where applicable.

- Prepare stockpile area for dump-rock from existing embankments and channels to be used for dams’ construction.

### Dams and Ancillary Works

Refer to Section 3 Dams Drawings in drawing pack and drawing register

The dams shall be constructed according to the prescriptive sequencing outlined in Section 5.1.14. Specific work activities are as follows:

- Site clearance and topsoil stripping of the footprint. A large portion is underwater or located within the riparian zone. The material is likely to be soft and saturated and not usable for construction. The material is to be stockpiled as indicated on construction drawings. Deeper excavations (embankment wall box-cut, division wall foundation strip and silt trap) are likely to be in soft material that will need to be stockpiled for possible use of fill material during the rehabilitation of the settling dam.

- Construction of reinforced concrete silt traps, concrete feeder pipes and reinforced concrete inlet structure to each compartment of the dams. Silt traps are reinforced concrete dual compartment structures fitted with mechanical sluice gates.

- Basin bulk excavations for the dams - Deeper excavations are expected to competent material in some areas, over and above the indicated excavations, and will also be to stockpile. Side wall collapses may be expected and strutting of material and wet works is likely to be required. Basin preparation will be done, and a compacted waste rock layer will need to be installed as per specifications, especially for load bearing structures (e.g. division wall and sump structure). The dam basin will mostly be founded on soft to semi stiff material and will require to be reworked to achieve the required specifications before placement of the blinding layer.

- Restricted excavations for drainage systems and division wall foundation works.

- Construction of reinforced concrete division wall for the PCD. The wall shall be founded on a 1m thick pioneer layer of waste rock overlain by a 600mm thick G5 material (from commercial sources) earth mattress compacted as specified on the construction drawings. The wall shall be constructed in panels with 20mm expansion joints between the panels.  Joint details for the wall panels are indicated on the construction drawings.

- Earth embankment walls will include access ramps for both compartments of the PCD and RRD.

- The cut-off trenches will follow the outside perimeter of the dam wall and function as an interception drain. The structure would therefore include a main drain line and a curtain drain that leads into the main drain line. The geotextiles used needs to be sufficient to avoid blinding and allow permeation of excess water.

- The entire basin will have a herringbone drain line consisting of a perforated drainage pipeline within a commercial, graded filter medium. The entire drain line is to be wrapped in a geotextile. Main drain lines will be dual lines that is interlinked every 50m to allow for some redundancy.

- All the drain lines that collect contaminated water will report to the main collection sump.

- Two solid HDPE pipelines is to be installed, running along the division wall and allowing flow from the upstream dam walls to bypass the dams through constructed intakes.

- Construction of water-tight reinforced concrete floor system. The floor of the dams is constructed of 150mm reinforced concrete panels cast on a concrete blinding layer that is cast on a 150mm base preparation layer compacted to specification.  If the insitu base material is not suitable it shall be replaced with a 150mm G7 material (from on-site excavations or commercial sources, where applicable) layer compacted to specification. Joints of the floor panels shall be sealed with a rearguard, joint filler and joint sealant as specified on the drawings.

- The embankments shall be lined with a 600mm thick transition gravelly semi-filter layer (with A4 bidim overlaying it), 200mm thick cushion/filter material and a 150mm reinforced concrete slab.

- Construction of spillways, outlet channel and energy dissipation structure. Spillways and the outlet channel shall be constructed of 200mm thick mesh reinforced concrete.

- Reinforced concrete outlet structures shall be constructed on the southern end of both the PCD and the RRD. Intake sumps shall house steel abstraction pipes that terminate in the Pump Station which forms part of the same structure. Brickwork superstructures will be constructed on top of the concrete outlet structures.

- Preparation works for de-silted material stockpile areas in proximity of the existing settlement dam, taking into account adequate work and access space to all construction activities.

- Stockpile of rock from existing channels and embankments to be decommissioned to be used during construction.

- Rock fill from stockpiles, excavations on site or commercially sourced to be installed in areas of deep soil saturation, where applicable.

- Prepare stockpile area for dump rock from existing embankments and channels to be used for dams’ construction.

- Remainder of unused stockpiled material to be utilised for rehabilitation of the settling dam.

### Desilting of the Existing Settling Dam

De-silting of the existing Settling Dam. The dam shall be de-silted to an average depth of 3m over the entire footprint. An ultimate volume capacity of 150ML is required for the Settling Dam to allow management of water bodies for all the dams. The removed material shall be stockpiled adjacent to the Settling Dam for use as coffer dam material and also as for rehabilitation material of the Settling Dam on completion of the works. The Settling Dam will be rehabilitated by backfilling it completely with suitable material to prevent any ponding of water in a storm event.

### Decommissioning and rehabilitation of the existing Settling Dam

- Decommissioning and rehabilitation of the existing Settling Dam. Note: This work is listed under the “Take-Out” option in Section 1.3.

- The decommissioning and rehabilitation process must adhere to the following objectives:

    - Safely decommission the Settling Dam.

    - Rehabilitate the footprint and surrounding areas as specified in Section 1.3.6 and specifications PSW.

    - Minimize environmental impact throughout the decommissioning and rehabilitation process.

    - Ensure compliance with all applicable regulations and standards.

- The decommissioning process will include the following key activities:

Pre-Decommissioning Assessment

    - Conduct a comprehensive site assessment to identify and document existing conditions, including hydrological, geological, and ecological factors.

    - Engage with relevant stakeholders, especially from the Employer, on the decommissioning and rehabilitation plans.

Development of Decommissioning Plan

    - Prepare a detailed decommissioning plan outlining the methodology, timelines, and resource requirements.

    - Submit the decommissioning plan for approval from the Employer.

Site Preparation

    - Establish work area boundaries and implement safety measures to restrict access during decommissioning.

    - Set up erosion and sediment control measures to protect surrounding areas.

Removal of Infrastructure

    - Safely dismantle and remove all dam infrastructure, including spillways, intake structures, and any associated equipment.

    - Ensure that all materials are disposed of or recycled in accordance with environmental regulations.

Silt Management

    - Assess and manage silt accumulation within the dams.

    - Remove silt where necessary, ensuring to follow environmental guidelines to prevent contamination.

    - If required to be disposed, silt which would be of ash origin, may be dumped on the ash dump. The Contractor should accommodate this operation.

Water Management

    - Develop a “decommissioning” water management plan to control the transfer of water from one dam to another or the release of clean water during decommissioning.

    - Ensure that any discharged water meets regulatory standards for quality before being released into the environment. If the water quality does not meet regulatory standards then it shall be transferred to the PCD.

Rehabilitation

    - Reshape/Recontour the footprint to restore natural topography and hydrology (for the Settling Dam, this activity requires filling of the footprint area to allow surface drainage away from the area).

    - Implement re-vegetation strategies using native plant species to promote biodiversity. The Contractor should develop a revegetation strategy which shall be reviewed and approved by the Employer.

    - Monitor the rehabilitation process to ensure successful establishment of vegetation and stability of the site.

Final Inspection and Reporting

    - Conduct a final inspection to ensure all decommissioning and rehabilitation activities have been completed as per the approved plan.

    - Prepare a final report documenting the decommissioning process, any issues encountered, and the outcomes of the rehabilitation efforts.

### Decommissioning and rehabilitation of the existing Clean Dam (South)

- The activities are similar to items for the existing Settling Dam (refer to Section 1.3.4) except for the rehabilitation effort as outlined below.

Rehabilitation

    - Remove the dam wall to allow free drainage from the dam footprint. The area shall be rehabilitated as specified in Section 1.3.6.

### Overall Site Rehabilitation Works

The primary goal of the overall site rehabilitation activities is to restore the site to a condition that is environmentally sustainable and aesthetically pleasing. The contractor is obliged to rehabilitate all work areas to an acceptable standard, ensuring proper planting, maintenance, and care of grass, trees, shrubs, and ground cover.

The Contractor shall perform the following works as part of the site rehabilitation:

- Soil Assessment and Improvement

    - Sample and test specific soils to determine improvement requirements.

    - Implement necessary soil improvements.

- Preparation of Areas

    - Shape and trim areas to specified contours and tolerances.

    - Prepare surfaces for grassing, including scarifying and roughening as needed.

- Topsoil Management

    - Supply and stockpile topsoil from suitable sources, ensuring it is free from contaminants.

    - Place and level topsoil on prepared surfaces.

- Planting Vegetation

    - Plant grass cuttings, sods, and hydro sown seeds according to specified rates and methods.

    - Ensure the planting of healthy trees, shrubs, and ground covers at designated locations with appropriate hole preparation.

- Watering and Maintenance:

    - Regularly water and maintain grass and plants to promote establishment.

    - Control weeds and replace any plants that fail to thrive.

- Erosion Control

    - Implement measures to prevent erosion during construction and maintain site integrity.

- Final Monitoring

    - Ensure that an acceptable grass cover (75% coverage with no bare patches exceeding 500 mm) is achieved within specified timeframes.

## Interpretation and Terminology

### List of Definitions

Terms and/or abbreviations used in this Works Information are defined as follows:

Table 1: Definitions

| Definition term | Definition Description |
| --- | --- |
| Employer | The person named as the Employer in the Appendix to Tender and the legal successors in title to this person. |
| Contractor | The person(s) named as Contractor in the Letter of Tender accepted by the Employer and the legal successors in title to this person(s). |
| Project Manager | The person appointed by the Employer to act as the Project Manager for the purposes of the Contract and named in the Appendix to Tender, or other person appointed from time to time by the Employer and notified to the Contractor as per NEC procedures. |
| Supervisor | The person appointed by the Employer to act as the Supervisor for the purposes of the Contract and named in the Appendix to Tender, or other person appointed from time to time by the Employer and notified to the Contractor as per NEC procedures. |
| Construction Manager | The person appointed by the Supervisor to act as the Construction Manager whose responsibility is to act on behalf of the Supervisor and fulfill the duties and actions that are delegated to them and is the representative of the Supervisor on site managing day to day operations and duties for the Supervisor as per the NEC. |
| Drives | Drives are all mechanical or electrical prime movers, e.g. actuators, pumps, etc. |
| Major plant | Machinery e.g. Conveyors, Feeders, etc. |
| Works Information | The document/s forming part of the contract in which are described the methods of executing the various items of work to be done, and the nature and quality of the materials to be supplied and includes technical schedules and drawings attached thereto as well as all samples and patterns. |
| Competent Person | A person who is qualified by virtue of his education, training, experience and contextual knowledge to make a determination regarding the performance of a building or part thereof in relation to a functional regulation or to undertake such duties as may be assigned to him in terms of these regulations. |
| Fire Protection System | Any fire alarm device or system or fire-extinguishing device or system, or combination thereof, that is designed and installed for detecting, controlling, or extinguishing a fire or otherwise alerting occupants, or the fire department, or both, that a fire has occurred. |

### List of Abbreviations

Table 2: Abbreviation

| Abbreviation | Meaning given to the abbreviation |
| --- | --- |
| ADF | Ash Disposal Facility |
| AP | Appointed Person |
| APP | Appointed Professional Person |
| B-BBEE | Broad Based Black Economic Empowerment |
| BMH | Bulk Materials Handling |
| BPLwD | Black People Living with Disability |
| BWO | Black Woman Owned |
| BYO | Black Youth Owned |
| C&I | Control and Instrumentation |
| CA | Contract Award |
| CoE | Centre of Excellence |
| CPA | Cost Price Adjustment |
| CPM | Critical Path Method |
| CQP | Contract Quality Plan |
| CR | Construction Regulations |
| CV | Curriculum Vitae |
| DB | Distribution Board |
| DC | Direct Current |
| DCS | Distributed Control System |
| DE | Drive End |
| DIR | Department of Internal Revenue |
| DOL | Department of Labour |
| DSO | Dam Safety Office |
| DTM | Digital Terrain Model |
| DWD | Dirty Water Dam |
| DWS | Department of Water and Sanitation |
| ECSA | Engineering Council of South Africa |
| ELLS | Electric Leak Location Survey |
| EMP | Environmental Management Plan |
| EMPr | Environmental Management Plan Report |
| EIA | Environmental Impact Assessment |
| FAT | Factory Acceptance Test |
| FMEA | Failure Mode and Effect Analysis |
| FRI | Forecast Rate of Invoice |
| FSL | Full Supply Level |
| FSS | Finance Shared Services |
| GCL | Geosynthetic Clay Liner |
| GN | Government Notice |
| HAZOP | Hazard and Operability |
| HDPE | High Density Polyethylene |
| HECU | Head End Control Unit |
| IEC | International Electrotechnical Commission |
| ISO | International Organisation for Standardisation |
| ITP | Inspection and Test Plan |
| KKS | Numbering System used at Tutuka Power Station |
| kPa | kilopascal |
| LAR | Limited Access Register |
| LCP | Local Control Panel |
| LLP | Long Line Protection |
| LOSS | Limits Of Supply and Services |
| LPS | Low Pressure Services |
| LV | Low Voltage |
| MAMSL | Metres above mean sea level |
| MCP | Main Conveyor Position |
| MS | Mild Steel |
| MTR | Motor Trip Relay |
| MV | Medium Voltage |
| NCR | Non Conformance Report |
| NEC | New Engineering Contract |
| NEMA | National Environmental Management Act |
| NFPA | National Fire Protection Association |
| NOC | Non-overtop Crest Level |
| OD | Outside Diameter |
| OEM | Original Equipment Manufacturer |
| OHSA | Occupational Health and Safety Act |
| OPCR | Outside Plant Control Room |
| OR | Operation Regulation |
| P&ID | Piping and Instrumentation Diagram |
| PCD | Pollution Control Dam |
| PDD | Project Development Department |
| PFD | Process Flow Diagram |
| PPE | Personal Protective Equipment |
| PS | Power Station |
| QA | Quality Assurance |
| QC | Quality Control |
| QCP | Quality Control Plan |
| QM | Quality Management |
| QMS | Quality Management System |
| RBO | Reliability Based Optimisation |
| RRD | (Recently) Rehabilitated Runoff Dam |
| SABS | South African bureau standards |
| SANRAL | The South African National Roads Agency Limited |
| SANS | South African National Standards |
| SAT | Site Acceptance Test |
| SBE | Small Black Enterprises |
| SCP | Standby Conveyor Position |
| SD&L | Supplier Development and Localisation |
| SHE | Safety, Health and Environment |
| SIT | Site Integration Test |
| SOC | State Owned Company |
| TH | Transfer House |
| TLB | Tractor Loader Backhoe |
| TP | Terminal Point |
| tph | Metric Tonnes per hour |
| UHMWPE | Ultra High Molecular Weight Polyethylene |
| VAT | Value Added Tax |
| VDSS | Vendor Document Submittal Schedule |
| VSD | Variable Speed Drive |
| VT | Voltage Transformer |
| WBS | Work Breakdown Structure |
| WUL | Water Use Licence |
| WULA | Water Use Licence Application |

# Management and Start Up

## Management Meetings

Meetings will be held monthly between the Project Manager and the Contractor (and any other co-opted members).  The Contractor is to be represented at each meeting by the appropriate members of the staff.

The venue for these meetings is as determined by the Project Manager.  The Project Manager writes the minutes of meetings.

Any action of the Project Manager, Supervisor, Contractor and Adjudicator implied in the minutes of meetings with contractual implications is confirmed by a separate communication given in accordance with this Works Information and NEC.

The Contractor reports the overall progress and as a minimum requirement, the following is addressed:

- Contractor’s current activity progress and planned finish dates.

- Contractor’s to report on all items listed in the NEC core clause, 31.

- Contractor’s and Project Manager’s programme agenda compared for delays and milestone targets.

- Current and projected manpower by class.

- Health, safety and quality Management.

- The progress of any other relevant activities.

- To discuss any technical or commercial issues.

- Skills Development and Localisation.

- CSI and Infrastructure Project Implementation Plan.

- Procurement progress.

- Problem areas or concerns.

Regular meetings of a general nature may be convened and chaired by the Project Manager as follows:

Table 3: Meetings Schedule

| Title and purpose | Approximate time & interval | Location | Attendance by: |
| --- | --- | --- | --- |
| Risk register and compensation events | Weekly | Venue determined by the Project Manager | Relevant appointed members of a Risk and/or Compensation event committee |
| Overall contract progress and feedback (from contract date to execution commencement) | Bi - Weekly | Venue determined by the Project Manager | Employer, Contractor, Supervisor, and Others as determined by the Project Manager |
| Planning Meetings (including integration meetings with Others) | Weekly | Venue determined by the Project Manager | Employer, Contractor, Supervisor, Planners and Others as determined by the Project Manager |
| Safety and Environmental Meetings | Fortnightly | Venue determined by the Project Manager | Employer, Contractor, Supervisor, Safety Officers and Others as determined by the Project Manager |
| Payment Assessment Meeting | Monthly – 20th of every month | Venue determined by the Project Manager | Employer, Contractor, Supervisor, Quantity Supervisors and Others as determined by the Project Manager |
| Quality and Engineering Meeting | Monthly or as determined by Project Manager | Venue determined by the Project Manager | Employer, Contractor, Supervisor Safety Officers and Others as determined by the Project Manager |

Meetings of a specialist nature may be convened as specified elsewhere in this Works Information or if not so, specified by persons and at times and locations to suit the Parties, the nature and the progress of the works. Such meetings should not prejudice the Employer in terms of cost, quality and schedule. Records of these meetings shall be submitted to the Project Manager by the person convening the meeting within five days of the meeting. People attending meetings must have authority to make decisions and execute the decision.

## Documentation Control

### Documentation Management

      - Document identification

The documentation requirements cover the various engineering stages, from the design stage through fabrication, installation, testing and commissioning and most importantly for the operating, maintenance and training stage of the project.

The Contractor is responsible for the compilation and the supply of the documentation during the various project stages and to provide the documentation programme to link with the milestone dates.  Documentation and drawings are programmed for delivery to meet the milestone dates and in accordance with the agreed VDSS supplied by the Employer.

#### Documents Submission

All documents and records must be submitted according to Technical Document and Record Management Work Instruction (240-76992014) and Gx Projects Documentation Deliverable Requirements Specification (240-65459834) and the Employer ensures that the Contractor is provided with latest revisions of all these documents. In order to portray a consistent image, it is important that all documents used within the project follow the same standards of layout, style and formatting as described in the documents above. The Contractor is required to submit documents as electronic in pdf format in a USB and hard copies and must be delivered to the Project Manager with a transmittal note.

The Contractor submits the Master Document List to the Employer on a monthly basis for tracking purposes, irrespective of whether there are updates or not. The MDL includes list of drawings and documents and contains the following minimum information for each document:

- Date of submission

- Transmittal number

- Transmittal title

- Document description

- Document number

- Document Type

- Revision number

- Document Approval Status

- Document Authorisation Status (i.e. Accepted With Comments, Not Accepted with Comments, Accepted)

#### Documentation Review and Turn-around

The Employer has a minimum 14 calendar days to review and consolidate review comments for documentation submitted by the Contractor. The Contractor also has a minimum 14 calendar days to respond and / rectify as per the comments by the Employer.

### Drawings Format and Layout

The creation, issuing and control of all Engineering Drawings will be in accordance to the latest revision of 36-943 (Engineering Drawing Office and Engineering Documentation Standard) and 36-945 and 36-946 (associated Work Instructions) to be supplied as part of the enquiry documents. Drawings issued to the Employer will be a minimum of one hardcopy and an electronic copy. All Contractors are required to submit electronic drawings in Micro Station (DGN) format, and scanned drawings in pdf format. No drawings in TIFF, AUTOCAD or any other electronic format will be accepted. Drawings issued to Eskom may not be “Right Protected” or encrypted. (240-86973501) The Employer reserves the right to use these drawings to meets it other contractual obligations.

### Plant Identification

#### Plant Coding Allocation

Coding of the design will be based on the AKZ coding system and the Employer will undertake the coding in line with its standards. The AKZ coding shall be applied during the design review stage(s) and cross referenced to all arrangement drawings, schematics, wiring diagrams, instructions and manuals and where practical to spare part equipment lists and manuals. The Contractor will be required to include allocated coding to the electronic design drawings.

#### Plant Labelling

The Contractor will also manufacture and install AKZ labels to identified plant items as per list supplied by the Employer. Labels will be manufactured and installed according to the Employer’s AKZ Plant Labelling and Equipment Descriptions Standard. The labeling standard will be supplied as part of the enquiry documents. Mention no. 240-62937990 Tutuka AKZ Plant Labelling Guideline.

### Configuration change control

Any changes to the design baselines will be formally managed according to the Eskom Project Engineering Change Procedure (240-53114026). All design reviews will be conducted according to the Design Review Procedure (240-53113685)

## Health and Safety Risk Management

    - General

- In carrying out its obligations to the Employer in terms of this contract, which obligations include, amongst others, providing the works; using Plant, Materials and Equipment; and whilst at the site for any reason, the Contractor is the “Employer” in terms of the Occupational Health and Safety Act, No. 85 of 1993, in respect of its activities and in relation to its employees, agents, Subcontractor/s and mandatories.

- The Contractor does not consider itself under the supervision or management of the Employer with regard to compliance with the Safety Health and Environmental requirements.

- Furthermore, the Contractor does not consider himself to be a subordinate or under the supervision of the Project Manager in respect of these matters.  The Contractor is responsible for the supervision of its employees, agents, Subcontractors and mandatories and takes full responsibility and accountability for ensuring that they are competent, aware of the Safety Health and Environmental requirements, whilst executing the works in accordance with the Safety Health and Environmental requirements.

- The Contractor ensures compliance with, amongst others:

- The provisions of the Occupational Health and Safety Act, No. 85 of 1993 and all applicable regulations (as amended), binding in terms thereof.

- The latest versions of standards, procedures, specifications, rules, systems of work and requirements of the Employer, copies of which will be provided to the Contractor on request. Refer to Section 6.

- The Health and Safety Plan prepared by the Contractor in accordance with the Employer’s Safety Health and Environmental Specification and requirements.

- The provisions of the National Environmental Management Act (as amended) and all regulations in force from time to time in terms of that Act, including Record of Decisions.

- The documentation referred to in paragraphs 2.3.1 (4) are collectively referred to as the Safety Health and Environmental requirements and forms a part of the contract Works Information.

- The Contractor ensures that its employees, agents, Subcontractors and mandatories comply with the provisions of the Occupational Health and Safety Act, No. 85 of 1993, and all applicable regulations binding in terms thereof as well as the Employer’s Safety Health and Environmental Specification whilst making use of plant, materials and equipment and whilst at the Site for any reason whatsoever.

- The Contractor implements a comprehensive health and safety management system, based on the ISO 45001: 2018 requirements for utilisation at the project.

- The Contractor appoints a person, qualified and competent in accordance with the safety health and environmental requirements, as the liaison with the Employer’s Project Safety, Health and Environment Manager/Officer or delegated person for all such matters as related to safety, health and the environment. The Contractor shall ensure that such a person is contactable 24 hours a day, and is registered with a registered professional council approved by the Principal Director of the Department of Labour, as per the requirements of the latest Construction Regulations, inclusive of  all exemptions and amendments pertaining thereto.

- The Contractor hereby indemnifies the Employer and holds the Employer harmless in respect of any and all loss, costs, claims, demands, liabilities, damage, penalties or expenses that may be made against the Employer and/or suffered or incurred by the Employer (as the case may be) as a result of, any failure of the Contractor, its employees, agents, Subcontractors and mandatories to comply with their obligations, and/or the failure of the Employer to procure the compliance by the Contractor, its employees, agents, Subcontractors and/or mandatories with their responsibilities and/or obligations in terms of or arising from the Occupational Health and Safety Act, No. 85 of 1993.

    - Mandatory Agreements

- The Contractor confirms that:

- In terms of sections 37(1) and 37(2) of the OHSA, the Employer is relieved of any and all of its responsibilities and liabilities pertaining to the activities performed by the Contractor (and its employees, agents, Subcontractors and mandatories) relating to the works; the use of plant, materials and equipment; and whilst at the Site for whatsoever reason.

- The Contractor confirms that, in terms of the Construction Regulations, regulation 6, it is hereby mandated as the designer and must perform all duties required of a designer.

- The Contractor confirms that he has been provided with sufficient information regarding the health and safety arrangements applicable to the works; the use of Plant, Materials and Equipment, as well as at the Site.

- In addition, the Contractor shall ensure that:

- Prior to the Contractor commencing with any operations/ activities relating to the works and/or prior to gaining access to the Site, the Contractor concludes a written mandatory agreement with the Employer in terms of section 37(2) of the OHSA and 5(1)(k) under the construction regulations. The aforementioned agreement constitutes a record of the written arrangements and procedures between the Contractor and Employer regarding health and safety.

- As far as is reasonably practicable, the safety and absence of risks to health in connection with the production, processing, use, handling, storage or transport of articles or substances is maintained.

- As far as is reasonably practicable, all hazards pertaining to the health and safety of persons and harm to the environment that are attached to any work which is performed, any article or substance which is produced, processed, used, handled, stored or transported and any plant or machinery which is used in its business, is clearly identified and, as far as is reasonably practicable, further establishes what precautionary measures should be taken with respect to such work, article, substance, plant or machinery in order to protect the health and safety of persons and or harm to the environment, and provides the necessary means to apply such precautionary measures.

- Such information, instructions, training and supervision as may be necessary to ensure, as far as is reasonably practicable, the health and safety at work of its employees, agents, Subcontractors and mandatories is provided.

- As far as is reasonably practicable, no employee, agent, Subcontractor and mandatory performs any work or produces, processes, uses, handles, stores or transports any article or substance or operates any plant or machinery, unless the precautionary measures contemplated in paragraph 2.3.3, or any other precautionary measures which may be prescribed have been taken.

- Such measures as may be necessary in the interest of health and safety and the environment are enforced.

- Work is performed and that plant, materials  or equipment is used under the direct supervision of a person trained to understand the hazards associated with it and who has the authority to ensure that precautionary measures required by the Employer are implemented.

- All employees are informed of the scope of their authority as contemplated in OHSA.

    - Health and Safety Obligations

- In addition to the mandatory agreements, the Contractor:

- Ensures that all statutory appointments (as required in terms of the Occupational Health and Safety Act, No. 85 of 1993 and all applicable regulations binding in terms thereof, as amended) and other appointments required in terms of the Employer’s Safety Health and Environmental Specification, are in place and that all appointees are cognisant of their duties and responsibilities in terms of such appointments.

- Ensures that such appointees execute their duties and responsibilities as required by such an appointment.

- Ensures that all personnel brought by itself onto site (including employees of Contractors and Subcontractors) are suitably qualified and trained for the performance of the task, duties and functions, which will be allocated to them.

- Immediately reports any occupational or other injuries, near miss events, property damage, environmental related incidents as well as any potential threat to the health and safety of individuals at the works or on the site, as soon as he becomes aware thereof, to the Project Manager.

- Complies with the Employer’s Environmental, Occupational Health & Safety Incident Management Procedure - 32-95, relating to the reporting and investigation of incidents.  The classification of incidents contained in such document are considered final and must be applied by the Contractor relating to any incidents/ injuries relating to its employees, agents, Contractors, Subcontractors and mandatories whilst on Site.

- Conducts a risk assessment regarding the utilisation of PPE and thereafter ensure that PPE of good quality is issued (at its own cost) to its employees, agents, Contractors, Subcontractors and mandatories prior to such individuals accessing the site, alternatively performing activities related to the works at the site, as specified in the Eskom PPE Specification.

- Notwithstanding the overall responsibility of the Contractor to ensure compliance with the provisions of the Occupational Health and Safety Act, No. 85 of 1993 and all applicable regulations (as amended), the regulations binding in terms thereof and the Safety Health and Environmental requirements, the Contractor ensures, amongst others:

- Ensures that all statutory appointments (as required in terms of the OHSA and regulations binding in terms thereof) and other appointments required in terms of the SHE Requirements, are in place and that all appointees are cognisant of their duties and responsibilities in terms of such appointments.

- Must ensure that such appointees execute their duties and responsibilities as required by such an appointment.

- Ensures that all personnel brought by itself onto Site (including employees of Contractors and Subcontractors) are suitably qualified and trained for the performance of the task, duties and functions, which will be allocated to them.

- Must immediately report to the Project Manager any occupational injuries, near miss events, property damage, environmental related incidents as well as any potential threat to the health and safety of individuals at the works or on the Site, as soon as it becomes aware thereof.

- Complies with the Employer’s procedure 32-95 “relating to the Reporting and Investigation of Incidents.  The classification of incidents contained in such document are considered final and must be applied by the Contractor relating to any incidents/ injuries relating to its employees, agents, Contractors, Subcontractors and mandatories whilst on Site and or conducting business in relation to the scope of the contract.

- Conduct a risk assessment regarding the utilisation of PPE and thereafter ensure that PPE of good quality is issued (at its own cost) to its employees, agents, Contractors, Subcontractors and mandatories prior to such individuals accessing the Site, alternatively performing activities related to the works at the Site as specified in the Eskom PPE Specification.

    - Radiographic Examinations

- If radiographic tests are carried out in the plant, the danger area must be evacuated with the exception only of authorised radiographic workers, and thereafter barricaded. Compliance is according to Regulatory, Eskom’s Safety Health and Environmental Specification.

- The relevant warning signs at the lockout gates are bolt secured and not by wire or any other means, which could be removed while radiographic tests are in progress. The area is barricaded and access is restricted until the radiographic process is complete. The radiographic technicians ensure that all the lockout gates are opened on completion of the tests.

    - Fire Protection

- The Contractor complies with the requirements of the Employer’s Safety Health and Environmental Specification, pertaining to fire protection. The Contractor ensures that adequate firefighting apparatus is provided at all his work sites, and that his staff is trained in the use of this apparatus.

- Precautions are taken to prevent any occurrence of fires or explosions while carrying out any work near flammable gas and liquid systems.

- Any tampering with the Employer’s Fire Equipment is strictly forbidden.  All exit doors, fire escape routes, walkways, stairways and stair landings are kept free of obstruction, and not be used for work or storage at any time.  Firefighting equipment remains accessible at all times.

  - Environmental Constraints and Management

- The Contractor provides an Environmental Management Plan applicable during installation and maintenance of works. The plan provides a guideline on the environmental management of the handling of the works. All waste will be handled in an environmentally friendly manner. The Contractor conforms to the “polluter pays principle”, duty of care and other NEMA principles.

- All of the Contractor’s staff complies with the Employer’s environmental requirements in accordance with the Employer’s Specific Health, Safety and Environmental Specification.

- The Contractor ensures that all environmental authorization obligations, applicable legislative requirements and Employer’s specific requirements are fulfilled. This includes all national, provincial and local environmental legislation and requirements.

- The Contractor issues on a weekly and monthly basis, Environmental Management Performance and Expenditure Reports to the Project Manager.

- The Contractor conducts their environmental management based on the ISO 14001:2015 requirements and implement their environmental management practices accordingly.

- The Contractor develops and implements as a minimum the following procedures:

    - Environmental Management Plan.

    - Waste Management Procedure.

    - Spill Management Procedure.

    - Hazardous Chemical Substances Management and Storage Procedure.

    - Water Management Procedure.

    - Stockpile and Erosion Management Procedure.

    - Clear-and-Grub Procedure.

    - Environmental Rehabilitation Procedure.

    - Erosion Control Plan during construction.

- All environmental procedures, as listed above, are site-specific and submitted to for acceptance by the Project Manager before the commencement of construction activities.

    - Waste Management

- All waste management activities, which include procurement of control measures, handling and disposal or processing of all waste forms generated on the Contractor’s site, are conducted according to Tutuka Waste Management Procedure (14RISKENV-013). All costs associated with waste management are the responsibility of the Contractor.

    - Spill Management

- The Contractor, at his cost, has available spill control measures (spill kits, drip trays, etc.), to the satisfaction of the Employer. All hazardous wastes generated from a spill are disposed of at a licensed disposal facility, at the cost of the Contractor, and safety disposal certificates are kept for record purposes.

    - Dust and Storm-water Management

- The Contractor implements dust control measures. The Contractor ensures that no ponding of storm-water occurs on the construction site and shall establish good storm-water management in accordance with the Employer’s requirements. Storm-water management measures shall comply to the gazetted government regulation GN704 and the EMP. Additionally, Contractor’s Storm water management plan shall be integrated with the Station’s plans.  The plan shall align with regulatory requirements to manage contaminated runoff from areas such as all ash footprints (including temporary coarse ash that is placed on top of the liner during construction).  The stormwater management plan shall take into account the volumes contained in the existing dams during construction as per the prescribed sequence of construction for the dams (See Section 5.1.14).

    - Environmental Rehabilitation

- The Contractor rehabilitates both its lay-down and construction site at the end of the project. The rehabilitation is done in accordance with the Gx Coal Area 1 Environmental Rehabilitation Plan - 240-100259162, as provided by the Employer. The Contractor submits to the Project Manager a rehabilitation plan and schedule at least 2 weeks before finalisation of the works for approval by the Project Manager. All rehabilitation costs are the responsibility of the Contractor.

## Quality Assurance Requirements

### General

The Contractor complies with the Employer’s Quality Requirements Standards.

- The Contractor and all Subcontractors comply with the Employer’s quality requirements including those listed in the Employers specification document, ( 240-105658000).

- Certified to ISO 9001 is a mandatory requirement for this contract. The Contractor uses the QMS for all phases of the Project. The Contractor provides evidence of a fully implemented QMS within its own organisation. The Employer may, at his sole discretion, carry out an audit on the Contractor or Subcontractor’s QMS for acceptance.

- The Contractor is required to submit construction method statements to satisfy the regulators prior to commencement of any construction activities.  The Contractors must allow sufficient time in their schedule for this activity. These method statements need to be submitted within the first month of contract award.

### Quality Management Documents Requirements

The Contractor conforms to the quality management requirements as per ISO 9001 and the Employer’s Supplier Contract Quality Requirements Specification (240-105658000).

The Contractor submits the following documents, within 30 days of the Contract Date, to the Employer for review and acceptance and prior to the commencement of the works.

#### The Contract Quality Plan (CQP)

The Contractor submits to the Project Manager within 30 days of Contract Date for review and acceptance prior to the commencement of work, a CQP which will detail the Contractor’s organisation, quality assurance and quality control procedures within that organisation specific to this project. The CQP must be aligned to, and reference ISO 10005:2005 QMS, guidelines for quality plans and in compliance with the guideline in QM 240-105658000.

The CQP will make reference to the Contractor’s QMS documents to be used in this Contract:

- The Contractor’s QMS compliance with the requirements of ISO 9001: 2015.

- Contractor’s quality manual.

- Contractor’s quality procedures.

- Contractor’s quality forms and work instructions.

- Contractor’s quality system documents referenced in this Works Information.

- Employers Works Information, drawings, specifications, standards and codes, etc.

### 2.5.2.2 Quality Control Plan or Inspection and Test Plan

As defined in the approved CQP the Contractor drafts and submits to the Project Manager for evaluation and .acceptance, prior to the commencement of any works, the requisite Inspection and Test Plan (ITP) or Quality Control Plan (QCP). The ITP/QCP shows each activity from the Works Information. The Project Manager inserts intervention points based on the risk profile of the equipment.

- The interventions points include all witness, hold, verification, surveillances and review points required by the Project Manager. The Contractor’s failure to allow the intervention points will constitute a non-conformance.

- The intervention requirements take into consideration the criticality of the Plant and Materials.

- Where intervention points have been bypassed without prior written waver from the Project Manager, result in the repeat performance of the activity in question and a Non-conformance (NC) is issued.

The Contractor supplies the Project Manager with a QCP or ITP for review and acceptance. The Contractor supplies the Project Manager with a detailed contract organogram showing the quality personnel to be used in the Contract. The Contractor provides CVs of the quality management employees who will be responsible for quality on site.

Quality Management employee’s responsibilities include but are not limited to the following:

- Implementation of the QMS

- Administration of QA/QC systems

- Verification of approval status of Subcontractor’s QCP and procedures

- On-and -offsite inspections

- Co-ordination, inspection and verification of the Employer’s intervention points

- Review of Contractor testing and inspection documents (procedures, test results)

- Reporting on quality performance

### Operational Documents

The Contractor submits as a minimum the following documents, as required by the Employer, which requirement does not constitute a compensation event, during the execution of the Works:

- Updated QCP register.

- Inspection notifications accompanied by their inspection report.

- Non-conformance and Defects registers and reports.

- Updated Site and off site inspection schedules.

- Inspection and or FAT / SAT dates.

- Inspections, completed and outstanding.

- Inspection and test reports.

- Weekly and monthly contract quality progress report.

- Data books for the completed works, before commissioning can commence (refer to the data book specification).

### Inspections and Tests

All Plant and Materials are comprehensively tested in accordance with the agreed ITP/ QCPs prior to delivery. The Employer reserves the right to appoint others to inspect all parts during manufacturing, erection and commissioning to be present at any of the tests specified. The witnessing of tests by the Supervisor or Others, and if the Supervisor chooses to waive the witnessing of any tests, it does not relieve the Contractor of his responsibilities.

Tests that are required by the Employer are carried out by the Contractor during manufacturing, erection and commissioning to prove compliance with the specification independently of any test that may have been carried out at the Contractor’s premises.

The Supervisor inspects parts of the Plant at his discretion during manufacturing stages and before shipment as per the agreed ITP/QCP;

- The Contractor is responsible for the inspection of all the work that is performed and the Supervisor only verifies that the work is conducted as per the Works Information.

- The Contractor conducts all inspections in accordance with the accepted ITP/QCP.

- The Contractor provides suitably qualified personnel to conduct on-and-offsite inspections.

- The Contractor ensures that all are inspected and approved before the Supervisor is invited for verification.

- The Contractor provides a minimum of five (7) working days’ notice for local off-site inspections, 24 hours for local on-site inspection, and 21 working days’ notice for foreign inspections.  The notice contains copies of the Contractor’s inspection reports.

### Quality Responsibility

The Contractor’s responsibilities include but are not limited to the following:

- The Contractor is accountable for the quality of the output and liable for any failures.

- Implementation of their QMS on site.

- Administration of their QA/QC systems on site.

- Verification of approval status of Subcontractor’s Quality programmes, that is, CQP’s, QCPs, NC’s, Defects and all their operational procedures and works instructions.

- On-and-offsite inspections.

- Weekly and monthly progress reporting on quality performance.

- The Contractor is responsible for defining the level of intervention of QA/QC or inspections in line with the Employers requirements.

- The Contractor is responsible for defining the level of intervention of QA/QC or inspections to be imposed on his Subcontractor, suppliers and sub-suppliers and must ensure that these are in line with the Employer’s requirements.

The Supervisor will be responsible for the following:

- Reviews of the quality submissions.

- Verification of the Contractor’s intervention points.

- Reviews the Contractor’s ITP/QCP documents (procedures, test results).

- Reviews the data book.

- Issue of Defects Certificate.

- Checks and marks off materials off site.

### Non Conformances and Defects

Where Non-Conformance (NC) notifications are issued, the Contractor acknowledges receipt within the period of reply and proposes corrective and preventive actions to the Supervisor. The corrective and preventive actions will include the implementation and completion dates. Progress on all NCs notifications issued to the Contractor must be reported to the Supervisor on weekly basis.

- The Contractor’s Quality Manager keeps a register of all NC notifications issued.

- Records of NCs notifications are kept and form part of the data book records.

- Deviations from the Contract are treated as a non-conformance.

To ensure reduction of non-conformances, the Employer will implement a penalty to the value of R20 000.00 for every NCR issued during the contract period if not closed within 14 working days.

During the contract execution phase, the Contractor will be monitored by the Supervisor for performance on quality related aspects. The monitoring will be in the form of audits and assessments.

### Quality Reporting

The Contractor submits a monthly quality report, on the last working day of the month.  The report includes but not limited to the following:

- A register of NCRs and defects.

- Updated QCP / ITP register.

- QA monthly report summary.

- Planned and completed local and foreign inspection dates.

- Completed and outstanding Inspections.

- Audit findings report.

- Risks with Mitigation plan.

### Preservation, shipping and transportation

The Contractor ensures that all Plant and Materials are preserved in an appropriate manner as described in the product specifications or in the Employer preservation, shipping and transportation procedures as applicable. The Contractor submits the preservation, shipping and transportation procedures to the Supervisor for review and acceptance. The Supervisor may choose to witness the packaging, loading and offloading of the products, depending on the equipment criticality, this will be indicated in the intervention points on the ITP/QCP.

The Contractor also ensures that all storage requirements for Plant and Materials are properly implemented to preserve the products against adverse conditions, deterioration, damages, etc. Storage and preservation procedures for the different equipment must be submitted to the Project Manager for review and acceptance. The Project Manager may request to inspect the stored Plant and Materials at any given point during the storage period of the product.

The Contractor shall comply with the quality criteria and constraints stated in this Works Information.

Plant and Materials for this contract is not shipped by the Contractor until all the documents stated in the Particular Specification have been submitted to the Supervisor.

## Programming Constraints

### General

The Contractor submits a single integrated Level 3 programme that incorporates all the work to be performed including that of his Subcontractors.  The interfaces between Subcontractors as well as the interfaces between Subcontractors and the Contractor are clearly identified. Project key dates are to be incorporated into the programme.

### Computerised Planning

Primavera is the only planning tool Eskom accepts for this project; therefore the Contractor is required to obtain this planning tool for the use of producing their programmes. The Project Manager does not intend duplicating the Contractor’s planning and scheduling, however, the Accepted Programme will be used in the Employer’s internal integrated and Master project programmes for project control purposes, updating and monitoring. The accepted programme will be in Primavera XER file. The Project Manager requires one project programme to be used and updated during the installation process, which will remain with Eskom. This ensures that any changes, deviations to the Programme can be carried out on the agreed programme and monitored. The initial programme supplied to Eskom after Contract award must be fully resource loaded.

Any changes that are required to be made to the Project/Programme i.e. scope changes, delays and the such, will be recorded through the Eskom change process and documentation, where all parties agree to the changes and sign.

The Contractor and Project Manager shall agree on the format on how the updates will be done i.e. PDF, XER, and the frequency of the updates i.e. such as on a weekly basis, or at any other time as required by the Contractor, or as instructed by the Project Manager.

The latest version of Primavera has been adopted by the Employer for all planning, progress monitoring and reporting on the Contract. The Contractor obtains this software and applies it for the planning and control of the work in line with the Work Breakdown Structure (WBS) which will be agreed upon contract award.

### Planning and Scheduling Levels

All planning and scheduling is done based on the Critical Path Method (CPM). The Contractor uses activity codes to define interfaces and to be agreed upon, between project manager and Contractor.  The Contractor’s programme must show the actual critical path clearly.

The schedule layout takes into account the approved WBS, reflecting the manner the works are to be performed as per the Contractor’s Method Statement and how activities are to be summarised, reported and monitored.

The following levels of programmes are to be used for this project for integrated project control:

- Management programme (Level 1).

- Project programme (Level 2).

- Control programme (Level 3 – Sub-system level).

- Discipline specialty programme (Level 4).

#### Management Programme (Level 1) – Project Master Programme

The management programme Level 1 is the project master programme and is used to show the overall time frames for the works.  It is a statement of project objectives recorded in graphic form.

#### Project Programme (Level 2)

A "rolled up" programme from the control level 3 programme is produced.  It will be separated by unit, plant area and by phase (engineering, procurement, construction and commissioning).

2.6.3.3 Control Programme (Level 3 – Sub-system level)

The project programme is prepared representing the significant work activities and deliverables associated with the works.

The programme includes:

- Major milestones, interface dates, access dates and key dates (for the new plant, existing plant and between Subcontractors).

- The duration of major activities and their relationship to one another.

- Identified long-lead material items.

- Responsibility assignments for accomplishing project objectives end product is a time scaled bar-chart programme developed using logic network.

This programme is separated by unit, by plant area, by phase, by WBS. The work within each plant area is broken down by engineering discipline, procurement, delivery, construction by the Contractor, start-up and commissioning. The programme is resource-loaded and it forms the basis for progress measurement, progress curves and histograms for each discipline within a plant area. .This is used for Evaluations and for the accepted programme after contract award. This will be saved and used as the original.

The Contractor submits a Level 3 Programme to the Project Manager which breaks the Works Information down to a sub-system level as per the Activity Schedules. This programme is then  aligned with the Contractor’s Method Statement. The Contractor’s Forecasted Rate of Invoicing (FRI) should also align with the resource loading on the programme.

2.6.3.4 Discipline Programme (Level 4)

The discipline specialty programme is developed and maintained by the Contractor and generated for tracking and control of various activities and deliverables for all phases of the project.  This programme is formatted as a spreadsheet or a database report utilizing the WBS breakdown.  This programme represents the day-to-day activities which are work-unit based and are summarized in the level 3 activities.

Resource information for manpower, plant, material and equipment and reflected in resource histograms is provided by the Contractor.  Staffing histograms are required to be submitted based on “equivalent personnel”.

### Planning Programmes

The Contractor develops a contract programme which will include a bar chart conforming to the project master programme dates included and sufficient detail to indicate the Contractor’s intention for executing the works. This programme covers major items relating to design, procurement, manufacture, delivery, erection, start-up and commissioning. The critical path is clearly shown.

Key milestones, access dates, interface dates and commissioning key dates are clearly identified in the contract programme, including access dates and release of terminal points that involve the Employer or Others.

The programme makes provision for site related preparation such as site establishment, safety induction and medical clearance of the entire Contractor’s staff that will be working on site.

#### Design Programme

The design programme contains a full list of documents and drawings, their submission dates and duration for review as specified by the Contractor in the VDSS. The programme also illustrates the sequence of work for the project and the submission of drawings, studies and reports.

The design programme meets the requirements of the Contractor and Others engaged on the project.  The Contractor is required to submit the programme for review by the Project Manager.

The programme should include all the design reviews to be conducted as per the Employer’s Design Review Procedure. The Contractor is responsible for conducting the following design reviews:

- Detail Design Freeze Review.

- Integrated Design Review.

- Construction Completion Review.

- Acceptance Testing Review.

#### Procurement and Manufacturing Programme

The Contractor is required to submit a procurement and manufacturing programme for review by the Project Manager which identifies as a minimum:

- Details of orders and target dates for placing subcontracts.

- Any detailed design required within the manufacturing period.

- Long-lead delivery items.

- Hold-points and witness-points for inspection and tests for acceptance and release.

- CSI roll out plan to be incorporated.

This programme is in sufficient detail to enable the work to be adequately tracked and progressed.

#### Construction Programme

The Contractor is required to submit a construction programme that is resource loaded for review by the Project Manager.  This programme includes the following criteria:

- Full details of all civil/mechanical/electrical/C&I/Low Pressure Services terminal point release requirements.

- Identify any erection or commissioning activities that may affect other construction activities.

- Identify when services are required for commissioning purposes.

This programme shall meet the requirements of the Contractor and Others engaged on the project.

The programme shall be based on the following working hours: Where applicable

- Twenty four (24) hours per day.

- Seven (7) days per week.

- Holidays included as working days.

- Pay weekends to be negotiated (if working 7 day work week).

#### Commissioning Programme

During the progress of the works, the Contractor develops a detailed commissioning programme with sufficient detail, to enable the work to be adequately progressed and tracked to meet the commissioning key dates.

Training programme to be incorporated into the commissioning programme.

The commissioning programme is detailed to sub-system level and is fully integrated with the Construction Programme.

#### Reporting and Data Requirements for Contractors Document number 240-83561037

This specification is included as an Annexure to the Works Information. This specification lists all the data and reporting that must be submitted by the Contractor on a weekly / monthly basis to the Project Manager. The purpose of this information is to implement proper project controls on this project.

#### Project Work Breakdown Structure

Activity durations should not be longer than 10 days, activities longer than 10 days should be split into sub tasks.

Table 4: Civil and Structural Work Breakdown Structure

| WORK BREAKDOWN STRUCTURE (WBS) |  |  |
| --- | --- | --- |
| 1 | PLANNING PROGRAMME |  |
| 2 | CIVIL AND STRUCTURAL |  |
|  |  | Design Activities |
|  |  | Procurement Activities |
|  |  | Manufacturing Activities |
|  |  | Delivery Activities |
|  |  | Construction Activities |
|  |  | Commissioning Activities |
| 7 | OTHER |  |
| 8 | HAND-OVER |  |

## Contractor’s Management, Supervision and Key People

The Contractor will provide the Employer and the Project Manager with an organogram showing the key people and the roles and responsibilities.

The organogram provided must show clear reporting lines between individuals, including individuals from subcontractors or joint ventures.

The Contractor provides the following key personnel as a minimum:

- Contracts Director.

- Project Manager.

- Safety, Health and Environment (SHE) Manager.

- Senior Quantity Surveyor.

- Quality (QA/QC) Manager.

- Environmental Officer.

- Construction Manager.

- Senior Surveyor.

- Bulk Earthworks Engineer/Site Agent.

- Civil Works Engineer/Site Agent.

- Planner.

## Invoicing and Payment

There are no additional requirements to the invoicing and payment clauses in Section 5 of the core clauses.

At each assessment interval, the Contractor submits to the Project Manager a forecast rate of invoicing that includes all the expected payments by the Employer to the Contractor on a month-by-month basis.

The invoices from the Contractor contain the following information:

- The registered name of the Contractor.

- The VAT registration number of the Contractor.

- The address of the Contractor.

- The Employer’s contract number.

- The VAT registration number of the Employer.

- The amount paid to date.

- The value of the invoice split into payments as per the activity schedule as indicated in the price Lists.

- Any retention monies to be deducted from the invoice.

- Any interest payable.

- Escalation formula used where applicable.

- Settlement discount.

- Proof of ownership of materials supplied.

The Contractor shall address the tax invoice to Eskom Holdings SOC Ltd and include on each invoice the following information:

All invoices in PDF format shall be emailed straight from your system to an Eskom email address (see email addresses below):

- Email addresses for invoice submission:

  - All invoices: invoicesgrpcapitalOTH@eskom.co.za

  - The Project Manager shall be copied when submitting invoices.

- All queries and follow up on invoice payments should be made by contacting the FSS Contact Centre:

  - Tel: 011 800 5060  or e-mail: fss@eskom.co.za

- For Foreign invoices, the Contractor is required to physically deliver hard copies of original documents to the Project Manager even though the Contractor has e-mailed those invoices.

- The Contractor ensures compliance with the tax Requirement for submitting invoices electronically.

- If there is Cost Price Adjustment (CPA) on your invoice, the Employer recommends that the Contractor issue a separate invoice for CPA so that if there are any issues on the CPA the rest of the invoice can be paid while resolving CPA issues.

- The base invoice number needs to be mentioned on the CPA invoice.

- Electronic invoicing does not guarantee payment but ensures visibility of all invoices and ensures that no invoices get lost. If the Goods Receipt (GR) is not done the invoice will be parked and the system will automatically send an e-mail to the Project Manager to do the goods receipt. This is also tracked by the Employer through the parked invoice report.

- The Contractor can request a parked invoice report from the Finance Shared Services (FSS) Contact Centre which can then be followed up and corrected. You are welcome to forward the details of invoices corrected to the FSS Contact Centre.

## Insurance Provided by the Employer

There are no additional requirements to the risk and insurance clause in Section 8 of the core clauses.

## Contract Change Management

There are no additional requirements to the compensation event clauses in Section 6 of the core clauses.

## Provision of Bonds and Guarantees

The form in which a bond or guarantee required by the conditions of contract (if any) is to be provided by the Contractor as given in Part 1 Agreements and Contract Data, document C1.3, Sureties.

The Employer may withhold payment of amounts due to the Contractor until the bond or guarantee required in terms of this contract has been received and accepted by the person notified to the Contractor by the Project Manager to receive and accept such bond or guarantee.  Such withholding of payment due to the Contractor does not affect the Employer’s right to termination stated in this contract.

## Records of Defined Cost, Payments & Assessments of Compensation Events to be kept by the Contractor

There are no additional requirements to the compensation event clauses in Section 6 of the core clauses.

## Training Workshops and Technology Transfer

The Contractor provides training on the Plant regarding operating, maintenance and engineering aspects. The Contractor provides training material and a separate training course for operating, maintenance and engineering personnel. For more detailed requirements on the training required refer to Section 5.2.9 of this Works Information.

# Engineering and the Contractor’s design

## Employer’s Design

Detailed designs were completed by the Employer. The Design is described in detail below and in the documents and drawings listed in Section 6 and 7.

### Existing Civil Infrastructure and Areas

The ADF complex consists of the following existing civil infrastructure, with the properties of each of the water holding facilities listed within the Integrated Water Use License (Licence number: 08/C11K/ABCFDI/1016) below :

- Existing Ash Disposal facility which has areas which has been rehabilitated and which have open ash areas (advancing face).

- Existing Ash Settling pond.

- Dirty Dam South. (Position where PCD will be constructed)

- Clean Dam South. (Position where RRD will be constructed)

- Clean Dam North.

- Dirty and clean water (unlined) stormwater conveyance infrastructure on and around the ADF.

Water management at the ADF is treated largely independent of water management of the PS terrace. The following infrastructure located on and around the PS terrace does not form part of the scope of works:

- Station North Clean Dam.

- Station Dirty Dam.

- DB Thermal Dam.

- Steinmuller Dam.

- Raw Water Reservoirs.

There is, however a current transfer of process water for dust suppression from the PS terrace to the AD, via a pipeline. According to the PS, the volume flow of water being transferred is approximately 2Ml/day.

### Civil and Structural Detailed Design Technical Deliverables

The detailed  Site services design of the civil works covers the following items, objectives and technical deliverables as described below.

Design Items:

- Geotechnical investigation and laboratory testing.

- Developing of an ADF and associated infrastructure water balance and stormwater management philosophy.

- Detailed design of the water management infrastructure such as the conveyance systems on and around the ADF.

- Detail design of the water holding infrastructure such as the PCD and RRD along with its associated silt traps, inlet and outlet works and spillways etc.

- Detailed design of the temporary and permanent roads.

- Detailed design of the perimeter fence.

Objectives of Design: The objective of the design of the continuous ashing operations at Tutuka Power Station is to design a facility that allows for the disposal of ash which is compliant with the existing environmental and water use legislation requirements.

Deliverables:

- Geotechnical Investigation Report.

- Basic Engineering Design Report.

- Detailed Engineering Design report.

- Detailed Design drawings.

A complete list of drawings for the civil and structural detailed design is included in Section 7.1.1

## Contractor’s Scope of Works

### Low Pressure Services

The Contractor must take note that the Pump Stations under his scope will interface with another contract for the installation of pumps. Details of the interface requirements will be communicated at a later stage. The Contractor should price the works as per given information in the Works Information and the drawings.

## Procedure for Submission and Acceptance of Contractor’s design

All the Designs shall be passed on to the Project Manager for review and approval prior to placement of any order or procurement of the designs.

### Design Review Procedure

Where the Contractor has design work in their scope, the Contractor is the Design Authority as defined in the Design Review Procedure (240-53113685). The Contractor is responsible for following this design procedure and conducting all the design reviews as specified in this procedure. The Contractor is responsible for conducting the following design reviews:

- Detail Design Freeze Review.

- Integrated Design Review.

- Construction Completion Review.

- Acceptance Testing Review.

### Project Engineering Change Procedure

The Contractor takes note of the Employer’s Project Engineering Change Procedure (240-53114026).  An engineering change includes any proposed change originating from engineering, Contractors, Project Management or Construction Management.

The Project Engineering Change Procedure applies to the Employer’s personnel or Contractors performing engineering or engineering related work where the quality of the engineering work performed is the direct responsibility of the Project Manager.

### Process for Submission of Documents

The Contractor submits all documents according to the accepted VDSS. The process for the submission of documents is described below:

- The Contractor submits the documents/drawings to the Project Manager.

- The Project Manager’s Document Controller registers the documents.

- The Project Manager’s Document Controller will supply the documents/drawings to all relevant parties within the Project Manager’s project team.

- The Project Manager’s team reviews the documents/drawings and will submit all comments or inputs to the Project Manager and the Project Manager submits to the Contractor for consideration.

- If the Project Manager finds major deficiencies in the submitted documents/drawings, the Contractor revises the documents/drawings and resubmits to the Project Manager.

- The Project Manager reviews the documents/drawings and if no major deficiencies are found, the Contractor organises a Design Review session.

- The Project Manager and the Contractor conduct a Design Review.

- If any fundamental errors were found in the designs or further actions are required, the Contractor record all concerns raised and revises the designs.

- The Contractor organises a Design Review session once all designs were revised according to the concerns raised by the Project Manager.

- If no fundamental errors were found in the designs during the Design Review session, the Contractor compiles the Design Review minutes or report and submits it to the Project Manager.

- The Project Manager’s Document Controller registers the report.

- The Project Manager’s team reviews the Contractor’s report/minutes. If the report/minutes are not acceptable, the Contractor revises the report/minutes and resubmits to the Project Manager.

- The Project Manager will accept the Contractor’s design once the report/minutes are accepted by the Project Manager’s team.

### Time Required for Acceptance of Designs

The Project Manager will return one copy of the drawing marked “Accepted”; “Accepted as Noted” or “Not Accepted”, as may be appropriate.  The notations “Accepted” and “Accepted as Noted” authorize the Contractor to proceed with the manufacture of the Plant covered by such drawings subject to the corrections, if any, indicated thereon.  Where prints or drawings have been “Not Accepted” or “Accepted as Noted” the Contractor makes the necessary revisions on the drawings and submit further copies for acceptance in the same procedure as for the original submission of drawings.  Every revision shows by number, date and subject in the revision block on the drawing.

## Other Requirements of the Contractor’s design

### Technical Risk Assessments

#### HAZOP Studies

- The Contractor carries out formal HAZOP Studies on all systems in their supply. These studies are done in accordance with the requirements as laid down in the Eskom HAZOP Guideline: 240-49230111.

- All recommendations are included in the Contractor’s designs. This is submitted to the Project Manager for acceptance.

#### FMEA (FAILURE MODE AND EFFECT ANALYSIS)

The Contractor carries out formal Failure Mode and Effect Analysis (FMEA) Studies on all systems in their supply. These studies are done in accordance with the requirements as laid down in the Eskom FMEA Guideline: 240-49230046.

    - System Interface

The Contractor is responsible for all system interfaces which forms part of the works. The Employer will provide the relevant information defining the system interfaces. The Contractor caters for all the identified interfaces.

## Use of Contractor’s design

All Contractor designs shall be used only and once review & approval of the designs has occurred by the Employer. The approval shall be submitted to the Project Manager in writing.

## Design of Equipment

All designs of equipment by the Contractor shall be used only and once review & approval of the designs has occurred. The review & approval shall be submitted to the Project Manager.

- The Contractor shall provide to the Project Manager and relevant Construction Management personnel the documentation for the warranties from manufacturers or suppliers of all equipment required in execution of the structures to be built within the ADF area.

- The Employer (Construction Health and Safety Agent) is obliged to ensure that proof to the effect that the designers comply with their obligations as stipulated in the Construction Regulations, section 6 is submitted during the application for a construction work permit.

- All the required documentation will be made available by relevant Construction Management personnel to the Contractor regarding the codification of equipment as well as the freight, storage and delivery requirements within the Eskom sites prior to the procurement of any equipment required for the execution of the structures to be built within the ADF area.

- The Contractor is solely responsible for providing the protection of the equipment from damage or loss due to weather, fire, theft, unexplained disappearance or similar during the execution of the works.

- The Contractor shall bear the cost of the replacement of any equipment or part thereof damaged or requiring replacement and all such costs shall be covered as per the required construction insurance taken out by Contractor for the construction of the works at the ADF area.

- The liability of the use of such equipment in the execution of the works shall remain that of the Contractor (i.e. this includes the design and transport, storage, maintenance, use of the equipment).

## Equipment required to be included in the Works

No specialised equipment is identified as being required, however if any is required, the designs shall be provided by the Contractor and reviewed as per Sections 3.3 above.

## As-built Drawings, Operating Manuals and Maintenance Schedules

- Language: All documentation, including reports, manuals, etc. is in the English language.

- Manuals:

The technical, training, operating and maintenance manuals are provided for each type of a functional unit. Technical manuals include all technical data as well as the technical data and leaflets of each individual component provided. Where generic manuals are provided, an addendum is provided indicating the applicable project specific components.

Manuals are of a good quality and cover the following as a minimum:

- Technical descriptions of the equipment and component parts.

- General arrangement drawings.

- Installation instructions with drawings or pictures.

- Operating and maintenance instructions for all components.

- Detailed parts lists (accompanied by exploded view type drawings clearly detailing the part and uniquely identifying it).

- Spare part ordering instructions.

Any special instructions pertaining to storage of spare parts or their shelf life is included in the maintenance manual. All drawings requested for component location, dismantling and re-assembly for maintenance are included in the maintenance manual. All special tools required for operating and maintenance of the equipment are presented in a form of a schedule in the operating and maintenance manual, respectively. The content of the training manual is based on the content of the technical, operating and maintenance manuals.

This section is read in conjunction with Section 2.2: Documentation Control and the VDSS.

### Drawing Requirements

The Contractor supplies reproducible drawings according to the Vendor Document Submittal Schedule (VDSS). The Contractor develops the following minimum requirements for the drawings:

#### Drawing Numbering System

The Employer supplies the proposed Project Manager drawing numbering system. The Contractor may assign his own drawing number as required to meet his document control system requirements.

#### As-Built Drawings

The Contractor’s Staff will maintain a master set of red-lined as-built drawings. The Contractor will provide drawing mark-ups as work is completed. The Project Manager and the Contractor will ensure that all appropriate information is transferred to the field record copy of drawings. The Project Manager and the Contractor will check the "as-built" for completeness and accuracy.

The following types of drawings will be updated to as-built status:

- P&IDs.

- Underground utilities drawings.

- Electrical single-line diagrams.

- Electrical schematic drawings.

- Wiring diagrams (including panel layouts and loop diagrams).

- Plant arrangements.

- Mechanical drawings.

- Civil & Structural drawings.

- Piping layouts.

- Valve and Equipment lists.

#### Operating and Maintenance Manual

The Contractor provides operating and maintenance manuals, as well as an Operating Technical Specification for the new Plant. The Contractor provides four (4) hard copies and an electronic copy.

The procedures are provided by the original equipment manufacturer detailing descriptions of operating and the maintenance work. The procedure covers the requirements for maintenance of the equipment over the design life.

#### Maintenance Schedule

The Contractor provides a maintenance strategy for the life expectancy of the new Plant with a summary schedule. The Contractor provides the life expectancy of the equipment. The Contractor lists maintenance spares (with detailed specifications) for the life expectancy of the equipment. Maintenance strategy updates to be in accordance with the Reliability Based Optimisation (RBO) standard for all disciplines (electrical, civil, mechanical, fire, C&I).

### Data Books

The Contractor shall compile Data Books progressively for all manufacturing and construction/erection inspections, operating manuals and test records and documents for every piece of plant required in producing the Works. The Contractor shall submit data books to the Supervisor and Project Manager for their review for all Plant and Materials and work undertaken with the applicable requirements and specifications at 50%, 80% and 100% completion.

# Procurement

## B-BBEE and Preferencing Scheme

The Employer requires the Contractor to maintain a Broad Based Black Economic Empowerment Recognition Level (B-BBEE Recognition Level) for the duration of the contract.

Section 1: Specific Goals

A maximum of 10/20 points may be awarded to a tenderer for the specific goal specified for the

tender. The points scored for the specific goal must be added to the points scored for price and the

total must be rounded off to the nearest two decimal places. Subject to section 2(1)(f) of the

Preferential Procurement Policy Framework Act, the contract must be awarded to the tenderer

scoring the highest points.

| B-BBEE Status Level of Contributor | Number of points (90/10 system) | Number of points (80/20 system) |
| --- | --- | --- |
| 1 | 10 | 20 |
| 2 | 9 | 18 |
| 3 | 6 | 14 |
| 4 | 5 | 12 |
| 5 | 4 | 8 |
| 6 | 3 | 6 |
| 7 | 2 | 4 |
| 8 | 1 | 2 |
| Non-compliant contributor | 0 | 0 |

NB: The following documents are required to claim preference points,

- Valid B-BBEE certificate issued by a SANAS accredited verification agency / sworn affidavit / CIPS affidavit

- Proof of ownership / shareholding (preferably CIPC documentation) inclusive of shareholding breakdown

- Certified ID copies of shareholder(s)

- Proof of Disability (where applicable)

- In a case of a trust, consortium or joint venture (including incorporated consortia and joint ventures),a consolidated B-BBEE status level verification certificate.

Tenderer failing to provide documentation for the allocation of preference points will not be disqualified, but’

- May only score point out of 90/80 for price

- Scores 0 points out of 10/20 for specific goals

## Supplier Development Localisation and Industrialisation (SDL&I)

Objective Criteria

Mandatory Subcontracting as condition of award

Subcontracting is mandatory on contracts above R30 million and is a condition for contract award.

Tenderers shall subcontract a minimum of 30% of the contract value to the following designated groups:

- an EME or QSE which is 51% owned by black people living in rural or underdeveloped area or townships.

NOTE 1: Tenderers shall submit the following mandatory returnable for Subcontracting:

- Subcontracting agreement signed by both with subcontractors’ company registration documents (CK and B-BBEE certificate or sworn affidavit) or

- Copies of sub-contracting contracts (agreements) or copies of letters from the tenderer to the sub-contractors, stating the intent to sub-contract. The Tenderer should sign both documents and the Sub-contractor(s) earmarked.

Potential scope to be subcontracted and/or outsourced:

- XXXX

- XXXX

Subcontracting, in this instance, will be treated as a condition for contract award. A supplier awarded a contract may not subcontract more than 25% of the value of the contract to any other entity that does not have an equal or higher B-BBEE status level of a contributor than the supplier concerned unless the contract is subcontracted to an EME that has the capability and ability to execute the subcontract

Local Content and Production

| Commodity | Components | Local Content Threshold |
| --- | --- | --- |
| Steel Products and Components for Construction | - Reinforcement steel (rebar) - Wire rod and Drawn wire - Joining/Connecting Components - Fasteners | 100% 100% 100% 100% |
| Plastic Pipes | High density polyethylene (HDPE) pipes | 100% |
| PPE | Reflector Vests, Jackets, Boots, Textiles, Clothing, Leather & Footwear, etc. | 100% |
| Bagged and Bulk Cement |  |  |
| Cement type | Description | Local Content Threshold |
| Cem I | Pure Portland cement with a 95-100% clinker. | 100% |
| Cem II | Portland cement containing varying additions of secondary materials, i.e., fly ash, pozzolana, slag, silica fume, or limestone | 100% |
| Cem III | Blast furnace cement, 50% OPC, 50% blast furnace slag | 100% |
| Cem IV | Pozzolanic cement, OPC and fly ash | 100% |
| Cem V | Composite cement: slag and ash cement. Blended cements with more than one blending material | 100% |
| Masonry cement | Mixture of Portland cement and plasticizing materials such as limestone to improve setting time | 100% |

NOTE 1: Mandatory for eligibility under Objective Criteria:

- (F1) - SBD 6.2 Declaration Form

- (F2) - Annexure C (Local Content Declaration-Summary Schedule

- (F3) - Annexure D-Imported Content Declaration – Supporting Schedule to Annexure C

- (F4) - Annexure E-Local Content Declaration- Supporting Schedule to Annexure C.

A tender that does not meet the minimum threshold on or before tender closing is an unacceptable tender.

Skill Development:

Skills development will be in terms of the Standard for Developing Skills through Infrastructure Contracts published by the Construction Industry Development Board (“the CIDB Skills Standard”) which the tenderer must comply with for further evaluation. Contractors are responsible for achieving the contract skills development goal and are provided with a number of methods for measuring their achievements. They may, if need be, devolve their obligations onto subcontractors.

Table below illustrates the skills development targets:

| Skills Type | Number of learners | Intake | Outcome |
| --- | --- | --- | --- |
| Engineering Technician/ Technologist (Civil) | 8 | S4 | National Diploma Civil |
| Yellow Plant Operators | 12 | N1/Grade 10 | Certificate of Competence |
| Steel Fixer | 15 | N1/Grade 10 | Steel Fixer Level 1 |
| Concrete Hand | 15 | N1/Grade 10 | Concrete Hand Level 1 |
| Shutter Hand | 15 | N1/Grade 10 | Shutter Hand Level 1 |
| Safety Officer | 10 | N6/Diploma/Degree | SACPCMP |
| Total | 75 |  |  |

Note 3: The above-mentioned Skills are a guideline. The actual skills/trade type may be negotiated. However, expenditure of 0.25% of the Acceptable Contract Amount in accordance with the CIDB CSDG is a Condition for Contract Award.

The Tenderers are free to propose any other relevant Skills Development that will be feasible and benefit the previously disadvantaged communities. This may even include Workplace Integrated Learning (WIL) from the TVET Colleges around Gert Sibande District Municipality.

Supplier Development Localization and Industrialization (SDL&I) Undertaking

The following SDL&I undertaking to form part of the enquiry:

- Enterprise or Supplier Development

The contractor will be required to propose Enterprise or Supplier Development.

Contractor to identify and incubate an SME from the designated groups, in one or more of the areas to be sub-contracted.

Assistance could be in the form of business support and equipment and/or finance. Beneficiary must be from the proximity of the Tutuka PS.

The contractor will also be expected to draft an Enterprise Development (ED) proposal within eight weeks of tender award. ED agreement must be signed with the beneficiary and sent to Eskom for review and acceptance. Progress will be monitored throughout the duration of the contract.

- Job Creation

Tenderer to indicate number of Jobs to be created and/or retained from this contract.

SDL&I Penalty and Performance Security

Eskom will apply a penalty of 2.5% of the Contract Value for failure to meet SDL&I obligations

One of the following options will apply for SDL&I performance security:

- For the duration of the contract, Eskom will retain 2.5% of every invoice (excluding VAT) as security for the fulfilment of all SDL&I Obligations. The retained amounts shall only be released to the Contractor upon fulfilment of all SDL&I obligations at the end of the contract.

- Alternatively, the Contractor shall submit a bond equivalent to 2.5% of the Contract Value and shall only be released to the Contractor upon fulfilment of all SDL&I Obligations.

Reporting and Monitoring

- The suppliers shall on a monthly/quarterly basis submit a report to Eskom in accordance with Data Collection Template on their compliance with the SDL&I obligations described above.

- Eskom shall review the SDL&I reports submitted by the suppliers within 60 (sixty) days of receipt of the reports and notify the suppliers in writing if their SDL&I obligations have not been met.

- Upon notification by Eskom that the suppliers have not met their SDL&I obligations, the suppliers shall be required to implement corrective measures to meet those SDL&I obligations before the commencement of the following report, failing which Retention clauses shall be invoked.

- Every contract shall be accompanied by the SDL&I Implementation Schedule which must be completed by the suppliers and returned to SDL&I representative for acceptance 28 days after contract award.

## Subcontracting

### Preferred Subcontractors

The Contractor makes use of any supplier for sourcing of equipment, tools and material which the Contractor will use to execute works.

2nd and 3rd Tier Companies (Sub-Contractors) should be submitted to Eskom for vetting and approval (That is, to be evaluated for LBS/BWO/SBE/BYO BPLwD classification in terms of the requirements of 32-1034).

### Subcontract Documentation, and Assessment of Subcontract Tenders

- The Contractor submits the proposed contract data for each subcontracting for acceptance to the Project Manager.

- The Contractor prepares s subcontracting document as according to the NEC Contract.

- The Contractor must inform the Project Manager when intending to subcontract some of the works from the contract scope.

- The Contractor takes note that their Subcontractors Safety Files will  be accepted by the Contractor Safety Manager before it will be handed to the GCD SHE practitioner/Officers for verification of compliance before any work commence.  Proof of acceptance by the Contractor Safety Manager needs to be in the Safety file when handed over to GCD SHE Practitioners for verification.

- The Contractor only employs qualified sub-contractors.

### Limitations on Subcontracting

The Tenderer shall submit a signed subcontract agreement letter to subcontract a minimum of 30% of contract value to one or more of the categories below:

- an EME or QSE which is at least 51% owned by black people;

- an EME or QSE which is at least 51% owned by black people who are youth;

- an EME or QSE which is at least 51% owned by black people who are women;

- an EME or QSE which is at least 51% owned by black people with disabilities;

- an EME or QSE which is 51% owned by black people living in rural or underdeveloped area or townships;

## Plant and Materials

### Quality

All Plant and Materials are either new or used. All New Plant and Materials will be free from defects. No Reconditioned Plant and/or Materials are regarded as new under any circumstances.

It will be the responsibility of the Contractor to ascertain the condition of any used equipment or materials, transport to site, corrosion protection, as well as any spares compatibility issues that may present itself in the future.

The Contractor will not use Plant or Materials which are generally recognised as being unsuitable or otherwise to be avoided for the purpose for which they are intended.

Only components of high reliability will be utilised, with a proven operating history, to enable the Plant to achieve required reliability and availability. Plant and Material design, engineering and manufacture will accord with the best modern practice applicable to high-grade products of the type to be furnished, so as to ensure the efficiency and reliability of the works and the strength and suitability of the various parts for the works.

Plant and Materials withstands ambient conditions and the variations of temperature arising under working conditions without distortion, deterioration or undue strains in any part.

All parts are made accurately, and where practicable, to standard gauges so as to facilitate replacement and repairs.  Like parts are interchangeable.

No repair of defective Plant and/or Materials will be permitted without the Project Manager’s approval and any such repair, if approved, will be carried out to the satisfaction of the Employer.

The Contractor ensures that co-ordinated and formally documented management system is in place for the assurance of quality as specified in ISO 9001, Quality management Systems – Requirements.

The Project Manager is free to specify hold and witness points during the installation and on site testing stages of the project. The Contractor issues preliminary notification of such hold and witness points by fifteen working days advance notice to the Project Manager, and confirms such hold and witness points at least seven days prior to the activity. Typical holding points are listed below:

- Design Review

- FAT

- Delivery to Site

- Erection

- SAT

- All manuals and drawings (in the specified format)

- Commissioning

In addition to maintaining appropriate inspection and test records to substantiate conformance to requirements, the following records are safely stored for a minimum period of seven years following the final completion of the works:

- Construction, layout and component approvals.

- Routine test certificates.

- Construction drawings and approvals.

After this period, the Contractor offers these records to the Employer (in writing) and obtains a disposal instruction.

Documentation regarding quality procedures is submitted within thirty days of Contract Award. The Employer will review and comment on the acceptability of these documents in a time frame as per the requirements of the contract for contractual correspondence. If controlled copies of these documents have been submitted to the Employer, then the controlled copy numbers may be quoted in the submission.

### Plant & Materials provided “free issue” by the Employer

The Employer does reserve the opportunity to negotiate with the Contractor that different plant and materials be used of another origin for whatever purpose that may become apparent at the time.

Contractor’s Procurement of Plant and Materials

- The Contractor shall supply and use suitable and sufficient construction plant, tools and equipment and materials as may be required to carry out the works efficiently.

- The following minimum construction plant is required to carry out the works efficiently:

| Item No. | Construction Plant | Minimum |
| --- | --- | --- |
| 1 | Bull dozers | 2 |
| 2 | Excavator | 4 |
| 3 | Water trucks | 4 |
| 4 | ADT's large | 4 |
| 5 | ADT's medium | 7 |
| 6 | Tipper trucks | 7 |
| 7 | Generators Large Mobile | 2 |
| 8 | TLB's | 3 |
| 9 | Smooth/Sheepfoot Rollers | 3 |
| 10 | Grader | 2 |
| 11 | Pumps | 4 |

- The Contractor at all times provides protection for all plant and materials from damage or loss due to weather, fire, theft, unexplained disappearance or similar.

- The Contractor at all times protects from damage, due to the Contractors service to provide the works, all plant and materials and equipment and all items on the site that are the property of the Employer or Others.

- The Contractor provides or manages, as part of Works everything necessary for the receiving, inspection, safe keeping and storage, issuing, handling, management and administration of all plant and materials purchased by the Contractor.

- The Contractor shall provide through the Project Manager and relevant Construction Management personnel the documentation for the warranties from suppliers of all any relevant plant and material used in the structures built within the ADF area, as well as the vendor data of the suppliers.

- The Contractor will ensure to provide all guarantees and warranties of the plant & materials used in the Works to the Project Manager and Employer when construction is completed.

- The Contractor supplies the labelling for the Plant that forms part of the works. The Contractor provides labels for the Plant according to the Tutuka label specification. The Contractor makes use of the AKZ codes and descriptions provided by the Employer.

- The labels are affixed in such a way that they are easily legible and not obstructed by the wiring or by other components.

- Clamping methods applied to the labels ensures that removal of the labels requires force.  The Project Manager will approve the proposed method of clamping prior to use.

- The Contractor supplies the Project Manager, for verification and acceptance purposes, with a label list showing the text only. The Project Manager will approve the positioning and designation of labels.

- The AKZ codes are used accordingly on documentation (e.g. drawings, manuals, equipment lists, cable schedules etc.) as a unique identification means.  References to plant are accompanied by the relevant AKZ code for that item of plant.

- Abbreviations to descriptions on the labels are generally not acceptable. Where abbreviations are unavoidable, due to the limited number of characters that can be engraved/etched on labels, the abbreviations are submitted to the Project Manager for acceptance. The Contractor makes use of the Employer’s Standard Plant Related to AKZ.  240-62937990: Tutuka AKZ Plant Labelling Guideline

- The Contractor arranges all shipments of Plant and Materials and consigns all such shipments to himself as consignee at the project shipping address, freight fully prepaid. The Contractor makes demurrage agreements and settlements with carriers for his shipments.

## Tests and Inspections before Delivery

It will be the responsibility of the Contractor to perform the required tests during construction and to coordinate documentation with the Supervisor. Test documentation generated during the commissioning phase will be filed as the work is completed. All tests and inspections are to comply with the quality management plans and requirements for the project as per Sections 2.5 and 4.4.1.

Once all Contractor construction activities are complete, the Contractor will hand over the Works to the Supervisor for testing and checkout. Completeness of the construction will be verified through a joint walk down between the Supervisor and Contractor. Any minor outstanding work items found during the construction walk down will be recorded as Defects, and dates will be established for resolution of these Defects.

Buildings with major omissions, errors, or problems found during the walk down will not be accepted for commissioning from construction. All construction documentation will be turned over to the Supervisor for review. This documentation will be reviewed for completeness, and will be included in the final safety clearance with the Project Manager.

Once the Supervisor has accepted a part of the works from construction, the responsible Project Manager will direct all pre-operational tests required to ready the subsystem for initial operation. Plant and Materials contained within the Works will undergo testing to verify that they are in good condition and ready to be put into service.

As per NEC Clause (41),  the following equipment shall not be brought to the Working Areas before they have been tested or inspected:

- Pumps for the Dirty Water Supply System to and from the Sump.

- Channel/ Sluice gates for the Silt Trap and the Sump structures.

- Adjustable weirs for the Silt Trap and Sump.

- Pipe fittings, equipment, etc. for the Dust Suppression System.

# Construction

## Temporary Works, Site Services & Construction Constraints

### Employer’s Site entry and security control, permits, and Site regulations

#### Access to Site

Access to the site is controlled and it is governed by the terms and conditions lay down by Tutuka Power Station security officials. The proposed site will be shown to the Contractor during the site meeting or clarification meeting by the Employer.

The Contractor liaises with the GCD SHE Practitioner/Officers for Safety Induction prior work to commence.  During Safety Induction, site access permits with a copy of the medical and a certified ID copy/passport (not older than three months) should be handed to the GCD SHE Practitioner/Officer for approval.

The Contractor employees will take the signed site access documents to security reception official in order to finalize their site access. The Contractor ensures that all its employees carry their site access forms with them all the time. The Contractor is subjected to alcohol testing on a daily basis. The Contractor submits his application for vehicle permit to the Project Manager. The personnel and vehicles entering and leaving the site are subjected to routine searches.

The Contractor obtains a “Gate Removal Permit” from the Project Manager before materials and equipment can be removed from site. The “Gate Removal permit” gives itemised list of materials and equipment to be removed from site.

The Contractor ensures that a tool list is available on the day of arrival and that all tools are captured on the tool list.  The tool list will be handed over to the Reception Security official that will stamp the tool list.  The tool list will be kept safe and will be used when tools needs to be remove from site.  This message should be handed over to any Subcontractor that will be working on Tutuka Power Station.

#### Site Regulations

The Contractor complies with the Site Regulations as per Employer’s Safety Health and Environmental Specification 240-166180310.

Any subject within the authority of the Project Manager may be addressed by a Site Regulation.

Before work starts on Site, a kick-off meeting is held with the Contractor and the Project Manager, to explain in detail all requirements of the Site Regulations.

The Contractor is issued with a copy of the current Site Regulations at the project kick-off meeting.

#### Permit to Work System

The Contractor allocates staff to be trained and authorised as Responsible Persons according to the Employer’s Plant Safety Regulations (36-681) and/or High Voltage Regulations.  These Responsible Persons are available on Site as and when required to take out permits to work.

In this contract the Contractor shall appoint employees to attend and be authorised as follows:

- All Construction Managers, Assistant Managers, Supervisors and Assistant Supervisors to attend PSR and be authorised as Authorised Supervisors.

- Four(4) Supervisors to be authorised in terms of the PSR as Responsible Persons; and

- Two (2) to be authorised in terms of ORHVS as Responsible Persons.

### People restrictions on Site; hours of work, conduct and records

Restrictions and hours of work may apply at Tutuka Power Station.  The Contractor keeps records of his people on Site, including those of his Subcontractors which the Project Manager or Supervisor have access to at any time. These records may be required when assessing compensation events.

### Health and safety facilities on Site

The Contractor provides a First Aid service and SHE representative to his employees and Sub-Contractors.  In the case where these prove to be inadequate, like in the event of a serious injury, the Employer’s Medical Centre and facilities will be available. Outside the Employer’s office hours, the Employer’s First Aid Services are only available for serious injuries and life threatening situations. The Employer recovers the costs incurred, in the use of the above Employer’s facilities, from the Contractor.

### Environmental controls, fauna & flora, dealing with objects of historical interest

The environmental controls shall be complaint to the following:

- IWUL number: 08/C11K/ABCFGI/1016 (File no. 16/2/7/C114/B045).

- NEAS reference: DEA/EIA/0001416/2012.

- DEA reference: 14/12/163/3/3/52.

- As per Tutuka Waste Management Procedure – 14RISKENV-013.

- National Environmental Management Act (NEMA, Act No. 107 of 1998).

- National Environmental Management Waste Act (NEMWA, Act No. 59 of 2008).

### Title to materials from demolition and excavation

As per Clause 73.2 the Contractor has no title to materials from excavation and demolition (e. g. coal).

### Cooperating With and Obtaining Acceptance of Others

Other Contractors are working in the same area as the work of this contract.  In this regard, the Contractor co-ordinates his work with the Project Manager to maintain harmonious working conditions on Site.

During the progress of the works the Contractor provides access to Others who also execute work in the same area, on an as and when required basis.

The Contractor makes his own assessment of the problems and difficulties which may be encountered for providing access to and interfacing with Others (this includes access difficulties experienced during construction or commissioning phase).

### Publicity and Progress Photographs

The taking of photographs at Tutuka Power Station including the Project works is restricted and subject to the approval by the Project Manager.

For the purpose of the Progress Reporting Requirements, the Project Manager may prohibit the taking of such photographs and/or require that all such photographs be taken by an official Employer photographer. In the latter event, the Contractor is required to make arrangements directly with the photographer for the taking of the photographs required by the Contractor for the purpose of the Progress Reporting Requirements.

### Contractor’s Equipment

- The Contractor provides all Equipment that is required to complete the works.

- The Contractor shall ensure that all his construction labour and equipment remains within the fenced off allocated construction area.

- The Contractor shall ensure that any staff, labour, or equipment moving outside his allocated construction site does not obstruct the normal operation of the ADF or the power station. Any additional access routes required must be coordinated with the Project Manager.

- The Contractor must keep daily records of his equipment used on Site and the Working Areas (distinguishing between owned and hired Equipment) with access to such daily records available for inspection by the Project Manager at all reasonable times.

- All Equipment used by the Contractor in providing the Works shall comply with the General Machinery Regulation 4 of the Occupational Health and Safety Act (Act 85 of 1993).

### Equipment provided by the Employer

No Equipment will be supplied by the Employer; however the Employer does reserve the right to negotiate with the Contractor that different equipment be used of another origin for whatever purpose that may become apparent at the time.

The Contractor supplies all equipment including cranes, scaffolding and other earthmoving equipment for the construction of the works.

### Site services and Facilities

#### Site Yard

Site Yard for the Contractor shall conform to the Employer’s Safety Health and Environmental Specification 240-166180310. It is required, for the proper co-ordination and execution of the works that the Contractor has an office on site for the duration of the Contract.

A site will be made available to the Contractor for his yard within the Power Station security area. The proposed site is shown on the Site Services General Arrangement drawings and will be shown to the Contractor during site meeting or clarification meeting. The yard is a raw site in size agreed upon by the Contractor and Project Manager and will be used by the Contractor for the establishment of his offices, workshop and stores.

The Contractor’s yard is subject to periodic inspection by the Project Manager/delegated person.

The location of the nearest, power distribution point, storm water channel and road access point is indicated by the Employer. The Contractor is responsible for connection to the closest point of supply.

#### Supply of Electricity

Electricity will be made available for construction purposes from power points which will be indicated by the Project Manager. The Contractor is responsible for the provision of the reticulation system from the point of supply. Both 220 (AC) Volt and 380 (AC) Volt are available on request. All points of supply requested by the Contractor are provided in terms of quantity and location at the discretion of the Project Manager. The Contractor should expect the connection will be metered for billing purposes.

No guarantees of power supply quality are given and power supply breaks of some duration may occur without warning.  Planned outages are also a possibility. The Contractor makes arrangements at his own expense to improve continuity and quality of power where necessary for any reason and no claim of any nature relating to power failures is considered.

No connection is made to the permanent installation at Tutuka Power Station without the prior acceptance of the Project Manager.

The power supply is managed in accordance with the latest revision of the Eskom safety regulations i.e.:

- 32-846, Operating Regulations for High-Voltage Systems.

- 36-681, Generation Plant Safety Regulations.

- COC for the site installation is required prior to power being switched on.

#### Lighting

The Contractor at his own expense provides temporary local lighting in accordance with the requirements of the OHS Act as amended.  The Project Manager provides no local lighting.  All construction lighting is the responsibility of the Contractor.

#### Water

The Contractor shall make provision for supplying both potable and construction water. The Contractor supplies at his own cost all the necessary connections, fittings, piping work, temporary plumbing and pumps necessary to supply to the various points where it is required. The Contractor is responsible for maintaining this equipment and for removing it at Completion of the whole of the works.

#### Roads

Main access roads to the ash dump are not surfaced and complete and may be used by the Contractor with the necessary care.  The Employer maintains the Site roads, described above, to a fair condition.  Any costs incurred by the Project Manager from damage caused to underground services, structures, etc. as a result of the Contractor not using the prescribed routes is recovered from the Contractor.

The Contractor provides temporary access points from the prescribed routes and roads to the points where the Contractor is required to perform work, having first obtained permission in writing from the Project Manager.

#### Setting-Out Beacons

The Project Manager provides permanent beacons marking the main setting out grid lines for the works, and permanent level benchmarks.

The Contractor takes reasonable steps to preserve beacons and benchmarks provided by the Project Manager who is not to be held responsible if any existing beacons are removed as long as other beacons exist.

### Facilities provided by the Contractor

#### Contractor’s Yard, Offices, Workshops and Stores

It is required, for the proper co-ordination and execution of the works that the Contractor has an office on Site for the duration of the contract.

The Contractor includes in his establishment prices for all further treatment of the yard areas that he considers necessary for his entire operation throughout his period of occupation and under all weather conditions. The Contractor also includes for all security fencing, security and access arrangements. The yard will be kept clean and tidy at all times, this will include all workshops and storage areas under the control of the Contractor. Maintenance of the yard is the Contractors responsibility and is for the Project Managers acceptance.

Outfall drainage of all surface run-off drains is constructed by the Contractor to the acceptance of the Project Manager to minimise erosion and to effect control of contaminated water. The Contractor’s plan for the layout of his yard area are accepted by the Project Manager prior to occupying the yard and the Contractor does not occupy any site area other than that allocated to him. The Contractor’s plan states fully what measures are taken regarding removal and storage of topsoil, stabilisation of eroded areas and further loss of topsoil.

The Contractor complies with the environmental policy given in the Site Regulations.  The Contractor provides, erects and maintains for his own use adequate size office accommodation and stores together with such drainage, lighting, heating, and hot and cold water services as may be required.  Provision is also made for adequate parking and a turning area adjacent to all the aforesaid structures.  The Supervisor prior to commencement of any work on Site accepts all designs and layouts for these provisions.

The Contractor dismantles and clears the yard of all such temporary structures and associated foundations and infrastructure at the direction of the Supervisor on Completion of the whole of the works.  No such dismantling and clearance work is carried out without prior acceptance from the Supervisor.

The Contractor shall make provision for carrying out of all quality control testing required in terms of the works involved. This shall include, but is not limited to, the following:

- Soil grading analysis from 0.075 mm up to 100 mm as per TMH 1 A.

- Soil grading analysis from 0.002mm up to 0.075nn as per TMH 1A5.

- Soil testing for Atterberg limits as per TMH 1 A2-A4.

- Soil density testing (nuclear and sand replacement as per TMH 1 A10).

- Soil testing for moisture content.

- DCP testing.

- In situ permeability testing on all facilities.

The Contractor shall either provide a laboratory on site or may make use of approved external laboratories (SANAS accredited) and/or laboratories of other contractors on site subject to the approval of the Supervisor.

Results of permeability testing will only be accepted if carried out by an accredited laboratory.

#### Employers Site Office

The Contractor shall provide and erect Site Offices for the Employer as specified in PS AB Engineer’s Offices. The layout of the Employer’s offices are to be approved by the Project Manager prior to erection.

#### Telecommunications

Neither a network point nor a telephone is available on site. Should the Contractor require one, he is to make his own arrangements with relevant authorities. Arrangements may also be made to use the telephones of the station if they are available. Calls from these will be charged for at prevailing GPO rates.

Should the Contractor wish to use radio communication equipment on site, he will make his own arrangements with the relevant authorities. In this case, he is requested to liaise with the head of security at the station to ensure that there is no interference with existing channels or equipment.

#### Sanitary Facilities and Refuse

The Contractor is to supply own sanitary facilities at his Contractor’s yard. A refuge control system will be established by the Contractor. All waste and refuge will be collected and disposed of as directed by the Project Manager, at the Power Station refuse disposal site.

#### Equipment/Appliances

Any electrical Equipment, or appliances, used by the Contractor conforms to the applicable OHS Act safety standards and is maintained in a safe and proper working condition.  The Project Manager has the right to stop the Contractor's use of any electrical Equipment, or appliance, which, in the opinion of Project Manager, does not conform to the foregoing. Inspection of equipment/appliance will be done as required by OSH Act.

The Employer may assist the Contractor with the off-loading of equipment, plant and material but the responsibility for off-loading remains with the Contractor.

Any special tools and equipment to be used on site for the execution of the works is the responsibility of the Contractor.

### Survey control and Setting Out of the Works

The Project Manager designates the working area boundary limits and assigns for the Contractor’s use access roads, parking areas, storage areas, existing facilities areas and construction areas. The Contractor does not trespass in or on areas not designated for his work.

The Contractor is responsible for keeping Contractor’s personnel out of areas not designated for Contractor’s use, except, in the case of isolated work located within such areas for which the Contractor is authorised to do so.

The control points will be established by the Contractor. Land surveys will be done by the Contractor before and after clear and grub, before and after topsoil strip and after final excavation before construction commences.

The Contractor will ensure that application for excavation permit is done well in advance before any excavation work can start in an area.  The Employer will need the drawings of the work to be conducted in the area to show the Excavation authorised person of Tutuka the drawings so that an excavation permit can be issued.  A copy of the excavation permit with the drawings will be handed to the Employer for record keeping.

In addition, the survey information is to be according to the National LO co-ordinate grid system and is to be provided in digital format (either YXZ format or preferably in Model Maker file system ver. 7 or above).

The following survey information is additionally required in order to approve construction works executed. This list is intended to give an indication of some of the survey work required, and is not intended to be an exhaustive list of all the surveys that will be required.

•	Detailed bottom of excavation survey, before placement of any layer works, clearly showing toe and crest lines of the basin excavation and embankment walls (for all works).

•	Survey of invert level subsoil and leakage detection collection collector and outlet pipes to verify falls and length of pipes installed.

•   Inverts levels of storm water drains.

•	As-built for all pipelines.

•	   Any extensions to stockpile areas.

Final As-Built survey information must be given to the Supervisor in the same format as what the setting out was given in the drawings. Final completion will not be processed before this survey information has been evaluated and verified using a DTM package.

### Control of Noise, Dust, Water and Waste

The Contractor maintains a high standard of cleanliness during the conduct of his activities at Tutuka Power Station. This includes areas allocated for storage of materials, site offices etc. to the satisfaction of the Project Manager. The Contractor keeps these areas clean and free from accumulation of waste materials and refuse regardless of the source.

The Contractor ensures during sweeping and dusting, that a minimum amount of dust is liberated into the atmosphere. Cleaning by vacuum cleaners is preferred and the use of compressed air for cleaning is prohibited.

The Contractor is responsible for the prompt removal of all waste to a designated disposal area. The disposal area will be on or in the vicinity of the Power Station and be indicated by the Project Manager.

For the purpose hereof, “waste” any matter, whether liquid or solid or any combination thereof, which is a by-product, emission, residue or remainder of any process or activity carried out in connection with the works and which is not reused on the Site in the in the ordinary course of carrying out the works within seven days of production.

The Contractor provides an adequate number of marked bins and containers at offices, in yards, at workshops and on the Site for the temporary storage of waste. These bins and containers are subject to approval by the Project Manager. The Contractor is required to segregate certain items of waste by type as designated by the Project Manager.

Bins and containers are emptied and waste removed to the designated area at least once a week. All the waste removed to the designated area at least once a week. All the temporary storage areas for bins and containers are kept tidy and must not constitute a nuisance to others. The Contractor takes all required steps to avoid spillage of waste alongside the bins and containers during removal and disposal thereof.

All waste that cannot be contained in either a bin or container is placed on a temporary waste site which the Project Manager identifies.  The waste is removed as soon as possible but in any event at least once a week. No burning of waste is allowed at the Power Station.

Hazardous waste is dealt with in accordance with the safety, health and/or environmental requirements of the works and the Contractor is solely responsible for the proper disposal thereof.  Hazardous waste will be disposed of at an authorised landfill site.  Waste manifest will be kept for record keeping and hand over at the end of the Project.

Controlling water from excavations is done as required by the Environmental legislation and only after a method statement to this regard has been accepted by the Project Manager.

The Contractor must ensure that adequate pumping capacity is provided for the continual pumping of water from excavations.  Water may be contaminated and should not be discharged into the environment unless tested.

### Sequences of Construction or Installation

The Contractor is responsible for the construction and installation of the equipment according to the Contractor’s construction and installation plans. The Contractor complies with the Employer’s Work Co-ordination Process.

Without derogating from the provisions of the Conditions of Contract, the Work Co-ordination Process is used by the Project Manager to monitor and manage activities on the Power Station and to facilitate the integration and co-ordination of the various works by Others.

If not included in the Contract, the Project Manager will notify the Contractor of the requirements of the Work Co-ordination Process prior to the date of site establishment by the Contractor.

The following prescriptive sequencing requirements of the Employer’s design shall be taken into account by the Contactor:

- DAMS – The new dams, PCD and RRD, will be constructed on existing operational dam’s footprint and the water in the existing dams is contaminated and cannot be discharged to the environment. These constraints necessitate works sequencing protocols for the construction of the dams.  The following sequencing is prescribed for the dams:

PCDs

  - The existing Settling Dam will be de-silted to increase the capacity from the present 40 000m3 to 150 000m3. This work may be executed by the Employer through another contract therefore it may be removed from this scope of work (refer to “Take-Out” option activities in Section 1.3.

  - A suitable temporary pumping and pipe system is to be installed at the Settling Dam to pump water from the Settling Dam to the ash dump for dust suppression.  Note: the water in the Settling Dam is ash contaminated water and the only licensed water use for it is dust suppression on the ash dump. Therefore, in order to drop down water levels in the dam, it must be pumped for dust suppression.

  - A coffer dam will be constructed downstream of the settling dam as detailed in drawing 0.61/96781/02. The function of the coffer dam is to contain any overflow water from the Setling Dam from reaching the works areas of the PCD Silt Trap.

  - A seepage well shall be constructed downstream of the coffer dam and a pump installed to allow pumping out of water back into the Settling Dam. The function of the seepage well is to continuously manage any groundwater seepage from the Settling Dam towards the working areas of the PCD Silt Trap and the PCD.  This shall be maintained until works at the Silt Trap are completed and such seepage would not hamper on the progress of the works.

  - Water shall be transferred from the Dirty Water Dam to the Settling Dam. This transfer is required to dry out the working areas at the Dirty Water Dam for the construction of the PCD. Water transfer shall be suitable for the construction of the first compartment as outlined in subsequent points below.

  - Construct the Silt Trap as detailed in drawings 0.61/96784/01-10. The Silt Trap will feed the PCD under normal operation.  Atleast one compartment should be constructed to enable commissioning of Compartment 2 of the PCD as outlined in subsequent points.

  - A seepage well shall be constructed in the RRD as shown on the drawing to minimize seepage water from the RRD footprint to the PCDs. Similarly, the seepage well shall be operated and maintained for the duration of the construction of the PCDs (at least one compartment) to provide dry working conditions for construction works.

  - Construct Compartment 2 of the PCD as detailed in drawing 0.61/96785/01

  - After completion of the PCD compartment 2 (commissioning), a licence to impound shall be obtained by the Employer. This license is critical and shall form a contractual milestone of Sectional Completion which will trigger commencement of the next section of constructing Compartment 1. Note: The dams are classified as Category II dams with a safety risk according to the Dam Safety Regulations of 2012. In order to commission Compartment 2, all requirements stipulated in the Dam Safety Regulations to obtain a License to Impound needs to be met. The Contractor is expected to review these requirements and incorporate them in the tender submission. Sectional completion will only be achieved following the attainment of a license to impound and upon successful completion of upstream ancillary works that are required to feed the PCD.  These will include, the Silt Trap (at least one compartment) and the Dirty Water Channels which will convey water to the PCD Silt Trap.

  - Water shall be transferred from the Compartment 1 zone of the Dirty Water Dam to the Settling Dam and if needed to the operational Compartment 2 of the PCD. This operation will allow a dry

  - Construction of the Compartment 1 (northern side) of the PCD shall be done.

  - After completion of the Compartment 1 of PCD (commissioning), a licence to impound shall be obtained by the Employer.

RRD

  - Decommission the Clean Dam South. Water quality of the dam should be confirmed and discharged of appropriately. If water quality does not meet license standards, the water shall be pumped to the Settling Dam but if the water quality is compliant, it shall be released to the stream. Draining the water will minimize seepage water to the construction site of the RRD.

  - Water shall be transferred from the RRD to the completed compartments (to manage the water levels in the RRD)

  - The RRD shall be constructed last.

- The basis of this prescribed sequence is to comply with GN 704 principles by managing the existing water bodies within the stated facilities. It is expected that at a minimum the Contractor adheres to the prescribed sequencing and ensures that water is managed on site to enable the execution of the works.

### Giving Notice of Work to be covered up

The Contractor provides a notice of work to be covered up to the Supervisor.

### Hook ups to Existing Works

The adjacent plant and equipment may not be modified without written permission from the Project Manager.  The Contractor complies with Eskom Life Saving Rules and will report any non-conformance.

## Completion, Testing, Commissioning and Correction of Defects

### Work to be done by the Completion Date

On or before the Completion Date the Contractor shall have done everything required to provide the Works.  The Project Manager cannot certify Completion until all the work has been done and is also free of Defects which would have, in his opinion, prevented the Employer from using the works and Others from doing their work.

### Use of the Works before Completion has been certified

In section Section 5.1.14. Sequences of Construction or Installation it is required that compartment 2 of the PCD be completed (commissioning), a licence to impound shall be obtained by the Employer. Water shall be transferred from the Dirty Water Dam to the RRD Settling dam and if needed to compartment 2 of the PCD.

After the construction of the  pre-deposition works and on approval from DFFE, the ADF will be open for operation.

### Materials Facilities and Samples for Tests and Inspections

Not application to this project.

### Commissioning

Commissioning is required before completion for all Mechanical, Control & Instrumentation and Electrical equipment/ installations work as specified within the scope of work and specification for the respective disciplines.

### Start-Up Procedures required to put the Works into Operation

The Contractor gives the Project Manager written notice that the works are ready for energisation. Such notice will suit the requirements of the Employer but will not, unless otherwise agreed, be less than 48 hours or more than fourteen (14) calendar days.

No alterations or adjustments will be made to the works after functional checks are done without the Project Manager’s written permission.

At this stage the following must have been achieved:

- Installation and pre-commissioning completed.

- Testing report and the associated certificates received.

- Signed erection and safety clearance certificates.

- Final Draft of the Technical, Operating, Maintenance manuals delivered.

- All Quality Control Plan (QCP) documentation received.

### Take Over Procedures

Refer to the Employer’s Procedure, Commissioning and Completion of Power Station Projects, 240-85416341.

### Access given by the Employer for correction of Defects

NEC Clause 43.4 requires that the Project Manager arranges for the Employer to allow the Contractor access to and use of a part of the works which has been taken over if needed to correct a Defect.

### Performance Tests after Completion

The Contractor shall carry out necessary tests after completion to demonstrate that the performance of the Plant is in accordance with the Employer’s Works Information requirements.

The Contractor will be required to provide a detailed method statement on how this verification will be achieved and any instrumentation/equipment required shall be part of the system provided by the Contractor.

### Training and Technology Transfer

The Contractor provides training on the equipment and systems included as part of the works to the various categories of the Employer’s technical staff (operators, maintenance and engineering personnel) for the duration of the works.

Training provided by the Contractor is directly applicable to the actual equipment supplied for the works. Generalised training based on similar equipment is not acceptable. The local facilities for training provided by the Employer is a suitably sized air-conditioned room, as well as trainee and trainer desks, an overhead projector and flipchart or white board. The number of personnel to be trained is as per the table below.

Table 5: Technical staff to be addressed in Training Proposal

| Department | Number of Personnel |
| --- | --- |
| Operators | 15 |
| Maintenance | 5 |
| Engineering | 5 |

The Contractor submits to the Project Manager for acceptance a detailed training programme as well as a prospectus for each course. Course material is provided for the number of trainees as per the table above.

The training schedule is incorporated in the Accepted Programme.

Practical hands-on training for each individual trainee forms an integral part of each of the following courses:

#### Training of Maintenance Personnel

Maintenance personnel will be trained in all components and functions of the Plant i.e. Method of maintenance, fault finding, correction, routine maintenance. Training will include familiarisation with documentation (maintenance plan, procedures etc.).

#### Training of Maintenance Operators

Operators will be trained and declared competent on the new systems. This will include familiarisation with documentation including drawing configuration logic, as well as operator interface familiarisation e.g. operational functions, alarms etc. The Contractor makes provision for training of all operators, for every shift.

#### Engineering Training

Formal engineering training will be provided on basic Plant design, capabilities and procedures upfront, prior to design freeze. Thereafter, training will be on-job training throughout the design process. The overview design and control/interface functions will be covered by this training. The engineering team should be trained sufficiently to enable them to work as part of the implementation team on and off site.

#### Training Documentation

The course material is in English and includes all third party documentation. A copy of the training documentation is supplied for each trainee with an additional 3 master sets for the Employer’s library and training department.

The training dates are included and shown in the Accepted Programme.  The supply of drafts, pre-print proofs and printed copies of training documentation is planned by the Contractor in such a way that the required training is complete before commissioning of the Plant.

Training manuals are continuously updated by the Contractor up to the date of issue of the Defects Certificate for the whole of the works.

### Operational Maintenance after Completion

It is not applicable to this Employer’s Works Information.

# List of Reference Procedures, Standards and Specifications

The Contractor complies with all standards, specifications and regulations as listed within this Works Information:

## General

Table 6: Eskom Project Management and Project Controls Specifications

| Applicable Eskom Specifications |  |  |
| --- | --- | --- |
| No | Document No | Description / Title |
| 1 | OHSA | Occupational Health and Safety Act South Africa No 85 and amendments |
| 2 | ISO 12944 | Paints and Varnishes - Corrosion Protection of Steel |
| 3 | SANS 1091 | National Colour Standard |
| 4 | ISO 1461 | Hot dip galvanized coatings on fabricated iron and steel articles |
| 5 | SANS 962-1 | Mechanical fasteners for conveyor belts Part 1: Plate-and-bolt type fasteners |
| 6 | SANS 962-2 | Mechanical fasteners for conveyor belts. Part 2: Hinged type and plate-and-rivet type fasteners |
| 7 | SANS 971 | Conveyor belting – Methods of testing fire retardant properties of all conveyor belting constructions |
| 8 | AGMA 6123-B06 | Design Manual for Enclosed Epicyclic Gear Drives |
| 9 | AGMA 2001–D04 | Fundamental rating factors and calculation methods for involute spur and helical gear teeth |
| 10 | AGMA 2003–B97 | Rating for pitting resistance and bending strength of generated straight bevel, zero bevel and spiral bevel gear teeth |
| 11 | AGMA 6010–F97 | Standard for spur, helical, herringbone and bevel enclosed drives |
| 12 | BS 970 | Specification for wrought steels for mechanical and allied Principaling purposes. General inspection and testing procedures and specific requirements for carbon, carbon manganese, alloy and stainless steels |
| 13 | BS 4235 | Specification for metric keys and keyways |
| 14 | ISO 5048 | Continuous mechanical handling equipment; belt conveyors with carrying idlers; calculation of operating power and tensile forces |
| 15 | ISO 281 | Rolling bearings – Dynamic load ratings and rating life |
| 16 | ISO 286-1 | Geometrical product specification – ISO code system for tolerances on linear sizes Part1: Basis of tolerances, deviations and fits |
| 17 | ISO 1940-1 | Mechanical vibration – Balance quality requirements for rotors in a constant (rigid) state – Part1: Specification and verification of balance tolerances |
| 18 | AGMA 9112 | Bores and Keyways for flexible Couplings (Metric Series) |
| 19 | ISO 15236-1 | Steel Cord Conveyor Belts – Part 1: Design, Dimensions and Mechanical Requirements for Conveyor Belts for General Use |
| 20 | ISO 14890 | Conveyor belts - Specification for rubber- or plastics-covered conveyor belts of textile construction for general use |
| 21 | ISO 1940-1 | Mechanical vibration -- Balance quality requirements for rotors in a constant (rigid) state -- Part 1: Specification and verification of balance tolerances |
| 22 | BS 5304 | Code of practice for safety of machinery |
| 23 | BS 1486-2 | Lubricating nipples. Heavy duty lubricating nipples |
| 24 | SANS 351 | Rolling bearings – Static load ratings |
| 25 | BS 1399-1 | Specification for rotary shaft lip seals. Dimensions of shafts and housings |
| 26 | ISO 113-2 | Rolling bearing accessories -- Part 2: Plummer block housings |
| 27 | BS 5265 | Mechanical balancing of rotating bodies. Recommendations on balance quality of rotating rigid bodies |
| 28 | SANS IEC 60034-1 | Rotating Electrical Machines: Part 1 Rating and Performance |

## Civil engineering and structural works

During the construction of the works there are numerous standards and specifications to which the Contractor must adhere to, the documents listed below is not bound in this document but must be adhered to during the construction of the works:

- SANS 1123: 	uPVC Rainwater Components

- SANS 62: 	Steel Pipes

- SANS 190: 	Expanded Metal

- SANS 191: 	Cast steel Gate Valves

- SANS 533: 	Polyethylene Pipes

- SANS 664: 	Cast Iron Gate Valves for Waterworks

- SANS 665: 	Cast Iron Gate Valves

- SANS 676:	Reinforced Concrete Pressure Pipes

- SANS 677:	Concrete Non-Pressure Pipes

- SANS 719:	Electric welded low carbon steel pipes for aqueous fluids (large bore)

- SANS 878:	Ready-mixed Concrete

- SANS 966:	uPVC Pipes

- SANS 986:	Pre-cast Concrete Culverts

- SANS 1123: 	Pipe Flanges

- SANS 1294:  Pre-cast Concrete Manhole Sections and Slabs

- SANS 1315:  Polypropylene Pressure Pipes

- SANS 1476:  Fabricated Flanged Steel Pipe work

- SANS 4427:  Polyethylene (PE) pipes for water supply – Specifications

- SANS 10221: 1998: The testing of Geotextiles

- SANS 1700-5-1: Fasteners Part 5: General requirements and mechanical properties Section 1: Mechanical properties of fasteners made of carbon steel and alloy steel - Bolts, screws and studs

- SANS 10085:  The Design Erection, Use and Inspection of Access Scaffolding

- SANS 1350: 	Guardrails for roads (W-section)

The most current revisions of following SANS 1200 Standard Specifications for Civil Engineering Construction shall form part of this Contract (these specifications are available at the Contractor's expense from the SA Bureau of Standards, 1 Dr Lategan Road, Groenkloof, Private bag X 191 Pretoria, 0001):

- SANS 1200 A: General

- SANS 1200 AB: Engineer’s Office

- SANS 1200 AD: General (small dams)

- SANS 1200 AH: General(Structural)

- SANS 1200 C: Site clearance

- SANS 1200 D: Earthworks

- SANS 1200 DE: Small earth dams

- SANS 1200 DK: Gabions and pitching

- SANS 1200 G: Concrete(Structural)

- SANS 1200 GA: Concrete (Small works)

- SANS 1200 GB: Concrete (Ordinary Buildings)

- SANS 1200 GE: Pre-cast Concrete (Structural)

- SANS 1200 GF: Pre-stressed Concrete

- SANS 1200 H:   Structural Steelwork

- SANS 1200 HA: Structural steelwork (sundry items)

- SANS 1200 HB: Cladding and Sheeting

- SANS 1200 HC: Corrosion Protection of Structural Steelwork

- SANS 1200 HE: Structural Aluminium work

- SANS 1200 L: Medium-Pressure Pipelines

- SANS 1200 LB: Bedding (Pipes)

- SANS 1200 LC: Cable Ducts

- SANS 1200 LD: Sewers

- SANS 1200 LE: Storm water Drainage

- SANS 1200 LF: Erf Connections (Water)

- SANS 1200 LG: Pipe Jacking

- SANS 1200 M: Roads (General)

- SANS 1200 ME:  Sub-base

- SANS 1200 MF: Base

- SANS 1200 MFL: Base (Light Pavement Structures)

- SANS 1200 MG: Bituminous Surface Treatment

- SANS 1200 MH: Asphalt Base and Surfacing

- SANS 1200 MJ: Segmented Paving

- SANS 1200 MK: Kerbing and Channelling

### Variations to the Standardised Specification

The following variations and additions to the Standardised Specifications will be applicable to this Contract. The Clauses in this portion of the Project Specification are numbered "PS" followed by a number corresponding to the number of the relevant clause in the Standardised Specifications or numbers following on the last item in the Standardised Specifications.

PSA: SANS 1200A: GENERAL

PSA 3 		Materials

PSA 3.1 	Quality

Substitute the second sentence of the first paragraph of A 3.1 with the following:

Materials shall bear the official mark of the appropriate standard. The Contractor is responsible for the cost of all testing to ascertain that the materials do comply with the specified minimum requirements of the relative materials and no additional payment will be made for such testing.

The Contractor shall inform the Project Manager of any control testing to be done timeously and at least 48 hours before such tests are required and must allow in his program for the time necessary for the tests and the processing of the results thereof. For testing that takes up more than two weeks, such as geomembrane conformance testing, the Contractor shall provide a schedule to the Project Manager for the testing from sampling up to the submission of the results.

PSA 4 		Plant

PSA 4.2 	Contractor’s office, stores and services

Add the following to A4.2:

1)	The Contractor shall make the necessary arrangements with the relevant authority for the provision of services such as electricity and water for domestic and/or construction purposes.

2)	The electrical wiring of all buildings shall be carried out by registered and licensed electricians in accordance with the requirements of SANS 0142 and the regulations of the local authority.

3)	Should the Contractor make use of local services, he shall make arrangements, where applicable, for connections to be made, complete with meters, from these services for use at the Site. All costs incurred in respect of these connections and the meters, pipes, cables, etc. from the connections to his facilities, the cost of the water consumed, the cost of the removal of sewage (not chemical toilets), and the cost for finally disconnecting and removing the services shall be paid by the Contractor, who shall include full compensation for such costs in his tendered price for the various items of work requiring the use of one or more of the services. The Contractor shall furnish the Project Manager with documentary proof that proper notice has been given to the relevant authority for termination of the services.

4)	The Contractor under this Contract shall supply his own distribution board for distributing the power to his facilities.  He shall be responsible for distribution of power and water supply to other mechanical and electrical contractors on the Site.  Payment for these services to Others shall be arranged between the Contractor under this Contract and the other contractors.  The Employer will not be involved in any arrangements in this regard.

5)	The Contractor shall deliver to the Project Manager a detailed drawing of the proposed layout of his offices, stores and services for approval and before erecting same.

6)	Sufficient backup services shall be provided to ensure the uninterrupted execution of the Works such as storage tanks for water for use in the mixing of concrete, standby electrical power for work at night and for electrical plant and equipment used on Site.

7)	The Contractor’s Site agent or representative must be contactable at all times by phone. Should use be made of radio and/or cellular-phone, these must be operational at all times with sufficient back-up batteries or recharging facilities.

There exists no housing facilities for the Contractor’s work force, and arrangements must be made by the Contractor to accomplish that as well as transport. The Contractor is solely responsible for all housing, or the arranging thereof, and no payment or extension of time will be allowed because of any delay and/or work damage that may arise.

PSA 5 		Construction

PSA 5.1 	Survey

PSA 5.1.1 	Setting out of Works

Substitute the first sentence of A 5.1.1 with the following:

The works shall be set out as shown on the drawings. Bench marks will be placed before handing over of the Site.

Add the following to sub-clause to 5.1.1:

Setting out of the works is the sole responsibility of the Contractor and shall be done from fixed points as indicated on the Drawings. The Contractor shall, within two (2) weeks after the Site has been handed over to him, ascertain himself of the correctness of all points. Any discrepancy shall immediately be reported in writing to the Project Manager. Any costs or subsequent costs arising from discrepancies that had not been reported to the Project Manager within the aforementioned period shall be the sole responsibility of the Contractor.

Setting out of the works will not be measured and paid for directly, and compensation for the work involved in setting out shall be deemed to be covered in the tendered Price.

PSA 5.2 	Watching, Barricading, Electric Lighting and Traffic Crossing

Add the following to A 5.2:

All excavations must be barricaded with solid barricading to satisfaction of the Project Manager. In the case where deep excavations are in close proximity of moving machinery and vehicle traffic, a berm will be constructed to ensure access is restricted to only the designated entrance and exit points.

PSA 5.4 	Protection of Overhead and Underground Services

Add the following to A5.4:

The Contractor shall as soon as possible after handing over of the Site, commence with the detection of existing services, continue with it without interruption and finalise it at least seven (7) days before excavation starts at the particular section. Detected existing services shall also be indicated on the "As-built" drawings.

Where the Contractor is responsible for the cost of repairs carried out by the Employer or others, the costs will be recovered by means of a deduction from the Contractor's monthly payment certificate.

PSA 5.5 	Dealing with Water on Works

Add the following to A5.5:

Special treatment of water on Site, where necessary, will specified separately (Refer to PSD 5.2.6)

PSA 5.7 	Health and Safety

With regards to Health and Safety, the Contractor shall comply with Sections 2.3 and 5.1.4 of this document.

PSA 5.9 	Workmen’s Compensation Act

It is a requirement of this contract that all labour employed on the Site is covered by the Workmen’s Compensation Act. The Contractor is to arrange a suitable method of complying with the Act including the payment of the necessary levies.

PSA 7 		Testing

PSA 7.4 	Statistical Analysis of Control Tests

Substitute A 7.4 with the following:

Test results shall not be evaluated by statistical methods. All results shall comply with the specified minimum requirements of the materials concerned.

SANS 1200 AB: ENGINEER'S OFFICE

PSAB 1	SCOPE

Replace this Clause with the following:

This section covers the provision of accommodation for the Employer’s resident staff.  This accommodation shall include the necessary additional offices and furniture as well as the provision of all the services required.  Six offices, one meeting room, two ablution facilities, one kitchen and ten covered car ports and 10 open space car ports are required for the use of the Employer’s staff on site.  All furniture and equipment supplied shall be new.

PSAB 3	MATERIALS

PSAB 3.2	OFFICE BUILDINGS

Replace this Sub-Clause with the following:

PSAB 3.2.1	Specification for Office Furniture

The following items shall be provided under this Contract:

- Twelve (12) office desks each with a surface area of at least 1.5m² with lockable drawers with keys (2 desks per office);

- Twelve (12) sturdy and comfortable chairs fitted with padded seats and backrests;

- Two (2) general purpose steel stationery cabinets each with a shelf area of at least 1.5m² and a volume of 0.70m³ each.  Each cabinet shall have a lock with two keys;

- Twelve (12) steel filing cabinets fitted with four drawers on runners.  The cabinets shall be fitted with two keys and shall be 1300mm high, 460mm wide and 600mm from front to back;

- Two (2) A4 black & White Laser Printers with two (2) spare cartridges each;

- Two (2) A3 colour Printer with two (2) spare cartridges;

- Six (6) drawing racks for A0 drawings.  The hangers shall be of the “Barhold” type with ten hangers per drawing rack;

- Six (6) A0 size inclined surface area drawing tables;

- Six (6) draughtsman’s stools fitted with padded seats and backrests, the height of which shall be adjustable;

- Six (6) 2700 x 900mm pinning board made of suitable material and fitted to the wall of the meeting room;

- Six (6) white boards each with an area of 1.5m² complete with a set of six (6) whiteboard marker pens;

- Venetian blinds or roller blinds, opaque type fitted to all six offices;

- Fifteen (15) sturdy and comfortable chairs fitted with padded seats and backrests (for the boardroom)

- One boardroom table to fit the size of the room. The table shall be fitted with two ICT connections.

- Ten (10) plastic chairs with metal frames; and

- Ten (10) plastic rubbish bins.

PSAB 3.2.2 Engineer’s Meeting Room and Employer’s Office

The Contractor shall provide one prefabricated site meeting room with at least 35m² in floor area.  The room shall be completed, furnished and ready for use not later than three weeks after the commencement date of the Contract.

The timber floor of the room, shall be at least 300mm above the surrounding ground level. Doors shall be provided at each end of the meeting room and each shall be provided with a suitable 3 lever lock and two keys.

Windows shall be provided, with a minimum glazed area of 15% of the floor area.  At least half of this area must be able to open, and shall be fitted with burglar bars and all the windows shall be fitted with venetian or other approved blinds.

The meeting room will be equipped with furniture supplied under PSAB 3.2.1.

Two (2) air conditioning units shall be supplied with the meeting room with capacity for the air volume of the room as per PSAB 3.2.6 and one (1) air conditioning unit shall be supplied for the Employer’s Office.

A 55 inch TV screen shall be provided and mounted on the wall of the meeting room.  All connections shall be provided to the two ICT connection points specified in PSAB 3.2.1.

Adequate electric fluorescent lighting and four (4) 15 amp power points.

PSAB 3.2.3 Kitchen

The Contractor shall provide a pre-fabricated kitchen with a timber floor (area of at least 12m²) and a ceiling height of not less than 2.4m. The kitchen shall be for the sole use of the Employer.

The door to the kitchen shall be provided with a suitable 3 lever lock and two keys.

The kitchen shall be provided with the following equipment:

1.	One refrigerator of not less than 150 litres capacity;

2.	One microwave oven;

3.	30 Litre electric hot water cylinder;

4.	One 1.5 litre electric kettle;

5.	Three holders for coffee, tea and milk;

6.	One kitchen sink with drain board, complete with hot and cold water supply;

7.	One kitchen table and six chairs;

8.	Electric lighting and four 15 Amp power points;

9.	All necessary plumbing to the existing waste tank;

10.	Two complete sets of cups and saucers for fifteen persons; and

11.	Cloths and dishwashing soap for the duration of the Contract

PSAB 3.2.4 	Car Ports

Carports shall be so constructed as to protect the vehicles parked under them at all times against rain, hail and sun.  Shade netting will not be permitted for the carports.  Preference is for corrugated iron sheeting for the roof and sides.  The carports shall each be at least 20 m² in area and their floors shall consist of a layer of broken stone or concrete to minimise dusty and muddy conditions. Ten car ports are required.

PSAB 3.2.5 	Areas surrounding offices

The access and other roads and parking areas surrounding the offices shall be treated and maintained to make them dust free either by using crushed stone or bituminous surfacing.  They shall be well drained and kept trafficable and free from mud and weeds at all times. They shall also be maintained and kept clean and tidy at all times.

PSAB 3.2.6 	Air-conditioning units and heaters

The Contractor shall provide and install air-conditioning units and heaters as specified.  The air-conditioning units shall be electrically operated compressor type with closed circuit, and not an evaporation type.  The air-conditioning units shall have a minimum capacity of 24000BTU.  The heaters shall preferably be of the space-heating type without exposed elements and shall have a capacity of not less than 1,5 kW.

PSAB 3.2.7 	Ablution units

The Contractor shall supply suitable and adequate chemical sanitary accommodation for the sole use of the Employer.  Such accommodation shall be to the satisfaction of the Employer and shall conform to the Local Authority requirement and any requisite Act(s).   The Contractor shall during tendering acquaint himself fully with these requirements.

The Contractor shall maintain in a thoroughly clean and orderly condition and finally remove from site all such sanitary accommodation and make good to the approval of the Engineer.

The position of the sanitary accommodation must be excluded from public view and their use will be strictly enforced.

PSAB 3.3	SERVICES

PSAB 3.3.2 	Water and Electricity

The Contractor shall provide a constant supply of clean potable water suitable for human consumption.

The cost of all electricity required for the Employer’s purposes shall be borne by the Contractor. All office/meeting rooms supplied shall include the provision of 220 V electricity.

PSAB 3.3.3 	Maintenance

The Contractor shall provide all labour, equipment and material which may be necessary to keep all accommodation in a neat and clean condition, and repairs shall be done without undue delay.

PSAB 3.4	GENERAL

a)	The Contractor shall not order any materials, equipment or fittings on the basis of their having been specified or scheduled without the written confirmation of the Employer having been obtained. No structure shall be erected without the Employer's written instructions as to the exact position and orientation of the building.

b)	Unless otherwise agreed upon, the meeting room shall be erected in close proximity to the Employer’s offices.

c)	The required facilities shall be completed, ready for occupation as specified, not later than three (3) weeks after the commencement date of the contract.

d)	The ownership of the meeting room, Employer’s Office and the kitchen shall remain the property of the Employer at the end of the Contract.

e)	The ownership of the furniture in PSAB 3.2.1 and PSAB 3.2.3 shall remain the property of the Employer.

f)	The Contractor shall take all reasonable precautions to prevent unauthorised entry to the offices and to ensure the general security of the offices and meeting rooms.

g)	No accommodation shall be erected without the prior approval of the Drawings by all local or Government authorities requiring such prior approval.

PSAB 3.5     INSURANCE

The Contractor shall keep all the site offices, furniture and equipment insured against loss, damage or breakage and shall indemnify the Employer, the Employer’s Designers and his staff against claims in this regards for the full duration of the Contract.

PSAB 4	PLANT

PSAB 4.2	SURVEY INSTRUMENTS

The Contractor shall supply and maintain for the sole use of the Employer and his staff, at least the following survey equipment, including for all necessary maintenance thereof:

Two (2) modern design automatic Engineer's levelling instruments complete with tripods;

Two (2) telescopic levelling staffs with metric graduations (4m long, 1cm graduations and 1mm graduations at the rear of the staff);

Two (2) staff bubbles;

One (1) x 100 metre steel tape graduated in millimetres throughout;

One (1) x 30 metre steel tape graduated in millimetres throughout;

Five (5) x 5 metre steel pocket tapes;

One (1) x measuring wheel;

Three (3) ranging rods; and

Steel or wooden pegs and hammer as required.

PSAB 5	CONSTRUCTION

PSAB 5.5	SURVEY ASSISTANTS

One or two survey assistants as and when required by the Engineer.

PSAB 8	MEASUREMENT AND PAYMENT

Payments for all items for the Employer’s Offices will be made according to the Activity Schedule, which outlines the specific tasks to be completed and their corresponding rates. The Contractor is required to plan and execute the works in accordance with this schedule to ensure timely and accurate compensation for services rendered.

PSC: SANS 1200 C: SITE CLEARANCE

PSC 5 		Construction

PSC 5.1 	Areas to be cleared and grubbed

Substitute the first sentence of 5.1 with the following:

Clearing and grubbing shall only be done in areas as instructed in writing by the Project Manager. Clearing and grubbing shall be done in accordance with the detailed design drawings and pipe and cable routes shall be limited to a 3 m wide strip. If it is deemed that the pipe or cable routes require a wider strip to be cleared, the Contractor shall in writing provide motivation for the wider strip for approval. Only once approval has been received from the Project Manager may the works commence. Measurement and payment for clearing and grubbing shall occur for areas as required by the Project Manager.

Substitute the last paragraph of 5.1 with the following:

The Contractor shall program his work in such a manner that re-clearing will not be necessary. The cost of re-clearing shall be borne by the Contractor.

PSC 5.2 	Cutting of trees

PCS 5.2.3 	Preservation of Trees

Add the following to paragraph to 5.2.3:

Trees outside the area to be excavated for the new structures must be left standing and undamaged, except when otherwise ordered, in writing, by the Project Manager. A financial penalty as determined by the Project Manager and Employer will be charged for removing or damaging any trees outside of the area to be cleared.

PSC 5.9 	Existing fencing

The fences around the Site shall be realigned as per the provided design drawings. If any section is damaged it shall be repaired immediately after any damage to them has incurred. The Contractor is strongly advised to make sketches and, where applicable, take photographs of existing fences before they are removed so as to avoid, as far as possible, arguments that may arise between himself and the property owner as to the quality of the re-erected fences.

PSD: SANS 1200 D: EARTHWORKS

PSD 3 		Materials

PSD 3.1 	Classification of excavation purposes

PSD 3.1.2 	Classes of excavation.

The Tendered Price shall include excavation in all materials and no excavation will be classified as soft, intermediate or hard excavations, this will including overbreak and backfilling inline with the Project Specifications that will form part of the Tendered Price. The Contractor will refer to the geotechnical report for guidance. No claims regarding these items will be entertained

PSD 3.3 	Selection

PSD 3.3.1 	General

Substitute the second paragraph of D3.3.1 with the following:

The Contractor shall deal in such a way with materials from all excavations to ensure that suitable material is not contaminated with unsuitable material, should no suitable material be found during excavations the contractor will inform the Project Manager in writing during excavations. All stockpiles will be classified by the Contractor as the stockpile progresses to ensure only suitable material is stockpiled for reuse and unsuitable material is stockpiled in an unsuitable stockpile. If suitable material is contaminated, such contaminated material shall be removed and replaced with material of standard at least equal to material as required by the Works Information or IFC Drawings, all at the Contractor's expense. No additional payment shall be made in respect of this and all relevant costs shall be deemed to be included in the tendered price.

PSD 4		 Plant

PSD 4.3	Contractor’s Construction Plant

Add the following to D4.3:

If during the course of the Contract, the Project Manager or the Supervisor considers that any item or items of constructional plant are in any way inefficient or inadequate to complete the works within the contract period, or do not meet the required safety standards, he shall have the right to call on the Contractor to either:

- put the constructional plant in order, or

- remove such constructional plant and replace it with other efficient and/or safe plant, or

- provide additional similar plant or plant of greater capacity.

The Employer shall have the right to stop all or part of the works where constructional plant does not complying with required safety standards is being used until such time as the plant has been made safe or replaced with approved plant.

No additional payment will be made to the Contractor for expenses incurred in complying with any or all of the above.

PSD 4.5 	Avoiding Quagmire Conditions

Add the following to D4:

In order to prevent quagmire conditions occurring in the excavations, relatively static plant such as back-actors shall be used combined with hand trimming to complete the excavation to final level. Should the Contractor allow quagmire conditions to develop, he shall, at his own expense, take such steps to rectify the conditions as the Project Manager may order.

PSD 5 		Construction

PSD 5.1 	Precautions

PSD 5.1.1 	Safety

PSD 5.1.1.2 	Safeguarding of Excavations

Add the following Sub-clause after 2 f):

The Contractor shall be responsible for the design and construction of measures to ensure stability of the excavation walls. Such designs shall be done by suitably qualified specialists and before the measures are implemented the designs shall be submitted to the Project Manager for his information.

PSD 5.1.2 	Existing Services

PSD 5.1.2.2 	Detection, location and exposure

Add the following to D5.1.2.2:

The requirements of PSA 5.4 shall apply mutatis mutandis.

If existing services are not shown on the drawings but the existence thereof can be reasonably expected, the Contractor shall, in conjunction with all relevant authorities, determine the exact depth and location of such services before the commencement of construction.

After locating the exact position of services, whether indicated on the drawings or not, such services shall be deemed to be known services and the Contractor shall be liable for all costs and subsequent costs arising from the damage thereof as a result of the Contractor's activities. These services must also be indicated on the "As Built" drawings.

PSD 5.1.4	Nuisance

PSD 5.1.4.1 	Dust Nuisance

Add the following to D5.1.4.1:

The Contractor is responsible for dust control and is liable for all claims that may result from dust nuisance on all parts of the Site and at all times from the date of handing over of the Site to the completion date of the contract. No payment regarding the above-mentioned will be made and all costs shall be deemed to be covered by the tendered price.

PSD 5.2 	Methods and Procedure

PSD 5.2.1.2 	Conservation of topsoil

Remove the last sentence of D5.2.1.2 and add the:

The designated areas for stockpiling of topsoil are provided in the design drawings and will be stockpiled accordingly. The removal of topsoil shall only occur in areas approved by the Project Manager in writing.

PSD 5.2.2 	Excavation

PSD 5.2.2.3 	Disposal

Substitute the second sentence of D5.2.2.3 with the following:

Any surplus material excavated shall be stockpiled as specified in the detailed design drawings. Caution shall be taken by the Contractor to ensure the materials utilised in the various construction activities shall be kept separate and each at its designated stockpile area as specified in the detailed design drawings. Survey and testing will be done on a weekly basis on all stockpiles to confirm the material properties and elevations and will be submitted to the Project Manager and Supervisor for record keeping purposes. Contamination of material will be avoided at all times by the Contractor and should contamination of material be witnessed the Contractor will replace such material at his own cost.

PSD 5.2.3 	Placing and Compaction

PSD 5.2.3.1 	Embankment

PSD 5.2.3.2 	Backfilling of Trenches and Backfilling of Filling against Structures

Replace the second paragraph of D5.2.3.2 with:

Where shown on the detail design drawings or as instructed by the Project Manager all trenches and excavations around structures shall be carefully backfilled with suitable approved excavated material from the basin or excavtion in layers not exceeding 150mm.

When placing backfill and fill, the following precautions shall be taken:

In so far as it is possible, the material shall be placed simultaneously to approximately the same elevation on both sides of a structure or structural member where appropriate. If conditions require that backfill for fill be placed appreciably higher on one side than on the opposite side, the additional material on the higher side shall not be placed until authorised by the Project Manager and preferably not until the concrete had been place for 14 days, or until tests show that the concrete has attained sufficient strengths to withstand any pressure safely that has been created by the backfill or fill or by the method of construction.

ii) The material behind structural members restrained at the top by the superstructure, e.g. portal-type structures, shall be placed as stated on the Drawings or as directed by the Project Manager.

iii) The material behind the walls of concrete culverts shall not be placed until the top slab has been placed and cured, unless otherwise authorised by the Project Manager.

Excavated areas around structures, between the structure and the vertical walls of surrounding excavation, shall be backfilled with suitable approved material from the basin excavation in horizontal layers not exceeding 150mm in depth after compaction, to the level of the original ground surface or to the level specified on the Drawings.

Each layer shall be moistened or dried to the optimum moisture content for the material and be compacted to a density of not less than 90% of modified AASHTO density, except that, in a road prism, the material shall be compacted to a density of not less than 95% Standard Proctor density at -2% to 2% OMC. In cases where backfill next to structures such as the penstock bases and drain outlet pipe structures occur the compaction shall be 98% Standard Proctor density at -2% to 2% OMC.

PSD 5.2.3.3 	Foundation fill

If, during the course of excavation, it is found that the material at the indicated founding depth does not have the required bearing capacity as specified on the Drawings, the excavations shall be extended at the discretion of the Project Manager until satisfactorily founding material is encountered. The Project Manager reserves to himself the right to order the Contractor to make up the difference in levels with foundation fill.

PSD 5.2.6 	Dewatering of the Works

Over and above his general obligations in regard to dealing with water as specified in SANS 1200 A, the Contractor shall be responsible for preventing the ingress of water into the foundation excavations. The preventative measures shall include the construction of proper drainage channels, diversion channels, berms, sumps, and the supply, operation and maintenance of the necessary bailing and pumping equipment.

The dewatering measures, , shall be maintained until the backfilling has been completed, after which all settled silt, mud, etc. shall be removed from the exposed surfaces where necessary. Between the various construction stages, pumping may be interrupted as may be decided by the Project Manager. The draining or pumping of water from the works shall be so done that no concrete materials will be carried away. The above mentioned will be included in the Contractors Tendered Price and no additional payments or claims will be entertained. All manholes will be continuously pumped to ensure a free flow of subsoil and leachate systems at all times until completion of the works, this shall be included in the tendered price.

PSD 7 		Testing

PSD 7.2 	Taking and Testing of Samples

Add the following to sub-clause D 7.2:

The frequency of testing to satisfy conformance of the materials used in the construction activities are as follows:

- For construction of the basin and starter embankment: A minimum of four sample for every 1000 m³ of material placed for any construction activity, to determine the material conformance in terms of grading, Atterberg limits and Standard Proctor density at OMC.

- For construction of the subsoil drains:

A minimum of one sample for every 50 m³ to determine the material conformance in terms of grading, Atterberg limits and Standard Proctor density at OMC.

- For construction of the leachate drains:

A minimum of one sample for every 50 m³ to determine the material conformance in terms of grading, Atterberg limits and Standard Proctor density at OMC.

- All test results to be kept on file. A copy thereof shall be submitted to the Project Manager upon completion of each test for the full duration of the contract and a copy of all tests to be included in the QCA package to be submitted to the Project Manager after completion of the project.

- All test locations will be logged via GPS and the test with the survey information (Survey in Excel and DWG as per design drawing S.O.P) will be submitted to the Project Manager and Supervisor for approval to ensure compliance with the Project Specification.

PSDB: SANS 1200 DB: EARTHWORKS (PIPE TRENCHES)

PSDB 1 	Scope

Add the following to DB 1.1:

This specification also covers the excavation for cable trenches.

PSDB 2 	Interpretations

PSDB 2.2 	Application

Substitute “from trenches” with “from trenches or excavations for structures” in DB			2.2

PSDB 3 	Materials

PSDB 		Backfill Materials

Substitute “from trenches” in DB 3.5(a) with “from trenches or excavations from structures”

PSDB 4	 Plant

PSDB 4.1 	Excavation equipment

Add the following to DB 4.1:

All excavations exceeding the specified widths shall be backfilled with approved selected material. No payment shall be made for this and all relevant costs shall be deemed to be included in the tendered price.

PSDB 5 	Construction

PSDB 5.1 	Precautions

PSDB 5.1.2 	Stormwater, Seepage, and Dewatering of Excavations

Substitute DB 5.1.2 with the following:

The costs of dealing with water shall be deemed to be included in the tendered price for excavation and no additional payment shall be made in this respect.

PSDB 5.1.4 	Existing services that intersect or adjoining trenches

Add the following to DB 5.1.4

The conditions of PSA 5.4 shall apply mutatis mutandis

PSDB 5.1.5 	Hand Excavation

Certain trenches will have to be excavated by hand, because of limited access and space. The Contractor is to ensure that all excavation done by hand is in strict accordance with the requirements of the Occupational Health and Safety Act.

PSDB 5.2 	Minimum Base Widths Specified

Substitute paragraph (b) of DB 5.2 with the following:

The minimum base width for pipes of external diameter not exceeding 160 mm shall be 600 mm, irrespective of the depth at which they are laid.

The minimum base width for electric cable trenches shall be 300 mm. Where two or more cables are installed in the same trench, the base width shall become 300 mm plus the distance specified between cables. The minimum distance between cables shall be 50 mm.

PSDB 5.4 	Excavation

Add the following to DB 5.4:

The provisions of PSD 5.2.2.4 shall apply mutatis mutandis for hand excavation.

PSDB 5.5 	Trench Bottom

Add the following Sub-Clause:

Unsuitable material shall only be excavated once the Project Manager has given a written instruction to this effect and stockpiled on the unsuitable stockpile.  Backfilling material for over excavation shall comply with the requirements of SANS 1200 LB: 1983 (2002-07-30) and shall be compacted to 93% Standard Proctor at -2% to 2% OMC or a specified by the Project Manager. No payment shall be made for this and all relevant costs shall be deemed to be included in the tendered rates price.

PSDB 5.6 	Backfilling

PSDB 5.6.1 	Backfilling

Add the following Sub-Clause:

Pipe joints shall be left open for 300 mm to either side until the pipeline has successfully been tested and approved by the Project Manager.

PSDB 5.6.2 	Material for Backfilling

Substitute "from trench excavations" in the first paragraph of DB 5.6.2 with "from excavations for trenches and structures.

PSDB 5.6.3 	Disposal of Soft Material

Add the following to DB 5.6.3:

The provisions of PSD 5.2.2.3 shall apply mutatis mutandis.

PSDB 5.7 	Compaction

PSDB 5.7.1 	Areas not Subject to Traffic Loads

Substitute the Sub-Clause with the following:

Except as specified in PSDB 5.7.2, each trench shall be backfilled in layers of thickness (after compaction) not exceeding 150mm and the material shall be compacted to 95% Standard Proctor density at -2% to 2% OMC.

PSDB 5.7.2 	Areas Subjected to Traffic Loads

Substitute the Sub-Clause with the following:

In areas subject to traffic loads, each trench shall be backfilled in layers of thickness (prior to  compaction) no exceeding 150mm and the material shall be compacted to 95% Standard Proctor density at -2% to 2% OMC.

PSDE: SANS 1200 DE: SMALL EARTH DAMS

PSDE 5 	Construction

PSDE 5.2 	Methods and Procedures

PSDE 5.2.1 	Clearing and Stripping of Site

The requirements of PSC 5.1 and PSD 5.2.1.2 shall apply mutatis mutandis.

PSDE 5.2.2 	Excavation

PSDE 5.2.2.2 	Preparation of exposed surfaces

Add the following Sub-clause:

All excavations shall be inspected and approved by the Project Manager before any construction (including earth embankment, casting of foundations, placing of blinding and laying of pipework under structures) commences.

Should some areas of the exposed surface prove to be too rough (containing sharp rock edges etc.) that may inhibit proper compaction of the first embankment or low permeability layer, the areas will be cleared of rocks and the surface will be ripped and re-compacted to 95% Standard Proctor density at -2% to 2% OMC. Once completed the areas identified as to rough will be approved by the Project Manager. Should the surfaces still not be the satisfaction of the Project Manager the process will continue until a smooth surface is achieved which is approved by the Project Manager.

PSDE 5.2.3.3 	Rockfill, rip-rap, drains and filters

PSDE 5.2.3.4 	Backfilling around structures (outlet works)

The requirements of PSD 5.2.3.2 shall apply mutatis mutandis.

PSDE 5.2.4.3 	Topsoiling

Delete this Sub-clause and refer to Section PSW.

PSDE 5.2.4.4 	Grass or other vegetation

Delete this Sub-clause and refer to Section PSW.

PSDE 5.2.5.2 Free haul

Add the following Sub-Clause to DE 5.2.5.1:

Any material movement whether by truck or any other method of transport on the designated Site area from the designated stockpile areas as per the detailed design drawings shall be considered as free haul and should be allowed for in the tender price.

PSDE 7 	Testing

PSD 7.2 	Taking and Testing of Samples

Add the following to sub-clause DE 7.2:

PSDE 7.2.2	PCD and RRD

The specification on taking samples at the PCD and RRD will be carried out as follows:

- Density control shall be either by the sand replacement method or by an approved nuclear density meter.  The use of the nuclear density meter will be subject to the following provisions:

  - The test will not be valid if performed within 1 m of concrete structures or in a confined space of width less than 2m.

  - For each 10 nuclear density meter tests carried out on the embankments, a minimum of 1 corresponding sand replacement test shall be performed.

  - For each 10 nuclear density meter tests carried out on the clay layers, a minimum of 2 corresponding sand replacement tests shall be performed.

  - The accuracy of any nuclear density meter shall be proved by performing at least five comparative nuclear density and sand replacement tests on each type of soil used in the embankment and clay liner before the results of the nuclear density meter will be accepted as valid.  Thereafter the correlation between the nuclear density meter and sand replacement tests shall be reviewed on a fortnightly basis.

  - Each nuclear density meter shall be required to have a certificate provided by the supplier of the machine stating that the machine is in good working order.  Each density meter shall be re-calibrated by the supplier at least once a year.  Certificates of proof of re-calibration will be required.

  - In the event of disagreement on the quality of compaction, results of sand replacement tests shall be accepted in preference to nuclear density meter test results.

PSDE 7.2.2.1 Embankment and Fill

The minimum testing frequency on field density and OMC that will be required from the Contractor shall be:

- Four tests per 500 cubic meter (4 per 500m3) or part thereof with a minimum of 4 tests per production lot for ordinary fill.

- Four tests per 2000 square meter (4 per 2000m2) or part thereof with a minimum of 4 tests per production lot for the top 300mm of fill and road bed.

- In addition to the above, the tests shall be done daily or a minimum of one (1) test per day throughout the construction.

- A minimum of one in situ permeability test for every 10 000 m² of every 300mm compacted clay layer that is placed to determine the conformance of the material to the permeability requirements. The in-situ permeability can be determined by the use of a double ring infiltrometer and no flow greater than 1X10-6 cm/s will be accepted. The Contractor will divide his basin into suitable sections to track permeability testing.

A production lot shall be taken to mean a portion of fill in a particular zone of the embankment placed and compacted in one process, using material from a single zone in the excavation.  If production continues uninterrupted, a production lot will usually be taken as the product of one day’s work and shall not exceed one days production.  A production lot of reduced quantity will be assumed, if:

- the fill material being used shows abnormal variation in quality.

- an area is obviously of lesser quality than the rest.

- a very high production rate is maintained.

Density tests shall be carried out within twenty four (24)hours of completion of compaction on the particular layer concerned.  The results thereof shall be submitted to the Project Manager without delay, in any case not later than 24 hours after these become available.

The Construction Manager/ Project Manager reserves the right to change the frequency of test work required to confirm conformance for any infrastructure for the PCD and RWD should he deem it necessary. He will notify the Contractor in advance and in the form of a site instruction issue the Contractor whit a change in required testing frequency.

Density control for all infrastructure for which a compaction specification has been specified shall be either by the sand replacement method or by an approved nuclear density meter.  The use of the nuclear density meter will be subject to the following provisions:

- The test will not be valid if performed within 1 m of concrete structures or in a confined space of width less than 2m.

- For each 10 nuclear density meter tests carried out on the embankments, a minimum of 1 corresponding sand replacement test shall be performed.

- For each 10 nuclear density meter tests carried out on the clay layers, a minimum of 2 corresponding sand replacement tests shall be performed.

- The accuracy of any nuclear density meter shall be proved by performing at least five comparative nuclear density and sand replacement tests on each type of soil used in the embankment and clay liner before the results of the nuclear density meter will be accepted as valid. Thereafter the correlation between the nuclear density meter and sand replacement tests shall be reviewed on a fortnightly basis.

- Each nuclear density meter shall be required to have a certificate provided by the supplier of the machine stating that the machine is in good working order.  Each density meter shall be re-calibrated by the supplier at least once a year.  Certificates of proof of re-calibration will be required.

- In the event of disagreement on the quality of compaction, results of sand replacement tests shall be accepted in preference to nuclear density meter test results.

PSG: SANS 1200 G: CONCRETE (STRUCTURAL)

PSG 2.3		Definitions

PSG 2.3 b)		Quality

Change the following Sub-Clause:

Sample (of concrete). The minimum volume of uncompacted freshly mixed concrete required in terms of SANS Method 861-2 for a designated test (e.g. 32 dm3 for the compressive strength test for 6 cubes of nominal side 150 mm).

Add the following Sub-Clause:

Set (of concrete cubes). A set of cubes shall consist of 6 cubes of nominal side 150mm of which 3 will be crushed at 7 days after casting and the remaining 3 at 28 days.

PSG 2.3 c)		Strength

Change the following Sub-Clause:

Valid test result. The average result obtained from the testing of three test cubes of concrete in accordance with SANS Method 862-1, Method 861-3 and Method 863.

PSG 3.2		Cement

PSG 3.2.1		Applicable Specifications

Change this Sub-Clause as follows:

Cementitious materials for concrete shall comply with:

- SANS 50197-1-Cement-part 1: Composition, specification and conformity criteria for common cements.

- SANS 55167-1: 2011 Part 1-Ground granulated blast-furnace slag.

- SANS 55450-1: 2011 Part 2-Fly ash.

- SANS 53263-1: 2011 Silica fume for concrete Part 1.

Under no circumstances shall a “masonry cement” complying with SANS 50413-1 be used for concrete.

Before any concrete is produced, the Contractor shall submit full details of the cement to be used for the production of concrete to the Project Manager for approval.

The name of the manufacturer of the cement and the place of manufacture shall also be submitted for approval.

PSG 3.2.2		Alternative types of cementitious materials:

Add the following to this Sub-Clause:

It must be clearly stated on the tender which materials are to be used. The concrete in the tender must be priced using CEM1 (Portland Cement) for dams and general structures and Fibre Reinforced concrete for channels. If the tenderer wants to use a Site blend as indicated below, he shall indicate this alternative in his tender letter indicating any benefits to the employer from a cost or otherwise point of view. The following materials may be used:

- CEM II as described in SANS EN 197-1.

- Site blend comprising, by mass:

- 70 parts of CEM I.

- 30 parts of fly ash.

Fibre Reinforced concrete with synthetic macro fibres with an aspect ratio (length/diameter) between 40 and 80 for channels.

A concrete Mix Design must be provided:

Water-Cement Ratio: Maintain a consistent water-cement ratio, both with and without fibre addition, to ensure uniform properties.

Aggregate Size: Use a maximum aggregate size of 19 mm, ensuring the fibre length is greater than the largest aggregate particle size.

Special consideration: Confirm the dosing rate and compatibility with the approved mix design.

The use of ground blast furnace slag and condensed silica fume will not be permitted.

The type of cementitious material to be used for specific structures or structural elements may be specified by the Project Manager. For concrete pavements and floors that have joints sawn at an early age, the strength class of the cementitious material shall be 42,5N; 42,5R; 52,5N or 52,5R.

PSG 3.2.3		Storage of Cement

Add the following to this Sub-Clause:

Where the cement is supplied in bags, the bags shall be closely and neatly stacked to a height not exceeding 12 bags, and they shall be so arranged that they can be used in order in which they were delivered to the Site.

Cement shall not be kept in storage for longer than 6 weeks from the date of manufacture without the Project Manager’s permission.

PSG 3.4.1	 	Applicable Specification

Add the following Sub-Clause:

Aggregates for concrete in contact with sewage or sewage gases shall be of dolomitic origin.  All concrete for sewers and sewerage works, except concrete for the following, shall therefore be made with aggregates of dolomitic origin:

- Blinding.

- Mass concrete for foundation fill.

- Concrete for encasing and bedding pipes.

The quantity of insoluble matter in respect of concrete made with aggregates of dolomitic origin, determined according to the method described in SANS 677, Appendix C, shall not be more than 15%.

PSG 3.5       	Admixtures

PSG 3.5.3	  	Specifications:

Add the following Sub-Clause:

Admixtures shall comply with the requirements of ASTM C-494 and full details of the brand and type shall be submitted to the Project Manager for approval.  Air entraining agents shall comply with the requirements of ASTM C-260 and full details of the brand and type shall be submitted to the Project Manager for approval.

PSG 4          	Plant

PSG 4.2       	Batching plant

Add the following Sub-Clause:

- Admixtures may be batched to an accuracy of within 2 % of the mass required.

PSG 4.5       	Formwork

PSG 4.5.2		Finish

Add the following to this Sub-Clause:

All exposed external corners shall be chamfered by the fixing of fillet strips into the corners of the formwork to form 20 mm x 20 mm chamfers, all at no extra payment.

PSG 4.5.3    	Ties

Add the following to this Sub-Clause:

Ties must be suitable for grouting to a depth at least equal to the concrete cover or 50 mm.  Details of ties to be used shall be submitted to the Project Manager for approval.

PSG 5          	CONSTRUCTION

PSG 5.1.3	 	 Cover

Add the following to this Sub-Clause:

The cover of concrete over reinforcement shall be measured from the outside of any reinforcement bar or stirrup.  The minimum cover shall be in accordance with the dimensions shown on the relevant drawing. Unless otherwise shown on the drawings, minimum cover to reinforcement shall be 40mm.

PSG 5.2.1	  	Classification of Finishes

- Smooth

Add the following to this Sub-Clause:

Smooth formwork is required where concrete will be in contact with backfill or where exposed formed surfaces will not readily be visible.

Special

Add the following to this Sub-Clause:

Special smooth formwork is required where concrete surfaces are exposed and is to be carried down to 150mm below adjoining ground or paving level.

Imperfections such as small fins, bulges, irregularities, surface honeycombing, and slight surface discolorations shall be made good and repaired by approved methods including rubbing down or grinding to the complete satisfaction of the Project Manager. The finish of the concrete shall be accurate to Degree of Accuracy I as defined in terms of Clause 6. Patching of the tie holes to match the colour of the concrete where exposed.

PSG 5.2.2	  	Preparation of Formwork

Add the following to this Sub-Clause:

Surfaces of formwork that are to be in contact with concrete shall be treated with an approved release agent to prevent adhesion of the concrete during stripping.  The joints between continuous formwork elements shall be closely butted and, where necessary, if undue leakage is expected, the joints shall be caulked, taped or packed with a sealing gasket, all at no extra payment.  Paper, cloth or similar materials shall not be used for this purpose. Any discolouration to the concrete by the release agent shall be permanently removed.

PSG 5.5.1.2 	Consistency

Add the following to this Sub-Clause:

The slump, measured in accordance with SANS Method 862-1, shall be not less than 50 mm and not more than 80 mm, unless permitted otherwise by the Project Manager for specific applications.

PSG 5.5.1.5 	Durability

Add the following to this Sub-Clause:

All water retaining structures shall be deemed to be exposed to severe conditions.  The cement/water ratio shall be determined by the strength of the concrete specified but shall not be less than 2.0.

In addition to these requirements the cementitious material content shall not be less than 325 kg/m3 for structural concrete Grade 35/20.

PSG 5.5.1.7 	Strength Concrete

Add the following to this Sub-Clause:

Before the commencement of any construction work, the Contractor shall submit a concrete mix design report to the Project Manager for approval.  A reputable commercial laboratory shall compile this concrete mix design report. Unless specified differently the grade of concrete to be used shall be as follows:

- Grade 35/20: All reinforced concrete structures.

- Grade 35/20: All paving slabs and floor slabs.

- Grade 15/20: Unreinforced foundations, pipe encasements and blinding.

- Grade 10/40: Mass concrete and concrete filling.

- Grade 15/10: Screeds and benching.

- 25 MPa Fibre Reinforced concrete channels. Synthetic macro fibres with an aspect ratio (length/diameter) between 40 and 80.

PSG 5.5.2		Batching

Add the following to this Sub-Clause:

Equipment for mass batching shall be clearly marked to show the mass of each material required for a batch.

PSG 5.5.2.3 	Aggregates

Add the following to this Sub-Clause:

Batching of aggregates shall be by mass to an accuracy of within 2 % of the mass required. No volume batching will be permitted.

PSG 5.5.6 		Compaction

Add the following to this Sub-Clause:

Compaction shall be carried out by mechanical vibration.  Compaction by hand shall not be permitted.

Add the following Sub-Clause:

Particular care shall be taken with the top section of the walls of circular tanks to prevent cracking.

PSG 5.5.7	Construction Joints

Add the following to Sub-Clause 5.5.7.3:

Construction joints when concrete is not more than 24 hours old:

The surface of the concrete shall be brushed with a wire brush, and loose material removed. New concrete shall be placed directly in contact with the old concrete and compacted thoroughly. Construction joints when concrete is more than 24 hours old:

The surface of the concrete shall be sand blasted or chipped with a light hammer, and swept clean. The surface shall then be wetted and allowed to become surface-dry before new concrete is placed directly in contact with the old concrete and compacted thoroughly.

Add the following Sub-Clause:

No vertical construction joints will be permitted in circular tanks

PSG 5.5.8 	Curing and protection

Add the following to this Sub-Clause:

The minimum period of moist curing shall be:

- 5 days for normal weather (temperature 18°C to 22°C, 65 % RH, low wind speeds).

- 7 days for hot weather with drying winds.

- 9 days for cold weather (temperature 5°C to 12°C).

PSG 5.5.11 	Watertight Concrete

Add the following to this Sub-Clause:

All structures shall be deemed to be water retaining unless otherwise specified.

PSG 5.5.13 	Grouting

PSG 5.5.13.1	Materials for Grouting

Water - Water for grout shall comply with the requirements given in Sub-Clause 3.3 of SANS 1200 G.

Aggregates - Notwithstanding the requirements of Sub-Clause 3.4.1 of SANS 1200 G, the grading of fine aggregate (sand) and coarse aggregate (stone or pea gravel) shall conform to the gradings given in Tables 1 and 2, respectively, below.

Cementitious material - This shall be type CEM II complying with SANS EN 197-1 and of strength class 42,5 N or higher.

Admixtures - Admixtures shall comply with the requirements of Sub-Clause 3.5 of SANS 1200 G and shall have a proven record of satisfactory performance under conditions encountered in the Republic of South Africa.

Proprietary grouting materials - Unless otherwise approved by the Project Manager, proprietary grouting materials shall be obtained ready mixed in sealed pockets as supplied by the manufacturers.

Table 7: Sand and Stone Grading

| Table 1 – Sand |  | Table 1 – Stone |  |
| --- | --- | --- | --- |
| Test sieve nominal aperture size (mm) | % Passing (by Mass) | Test sieve nominal aperture size (mm) | % Passing (by Mass) |
| 9.75 | 100 | 9.5 | 100 |
| 4.75 | 95 – 100 | 4.75 | 95 – 100 |
| 1.18 | 45 – 65 | 2.36 | 0 – 5 |
| 0.3 | 5 – 15 |  |  |
| 0.15 | 0 – 5 |  |  |

PSG 5.5.13.2		Preparation and procedures

- Before a machine or structural bedplate is placed on the concrete the following steps shall be carried out:

  - All defective concrete, laitance, dirt, oil, grease, and loose material shall be removed from the concrete foundation by bush-hammering, chipping, or other means until sound clean concrete is obtained.  The surface of the foundation shall be scabbled, but shall not be so rough as to interfere with proper placing of the grout.  All foundation bolt sleeves shall be cut out, or cut off flush if the sleeves cannot be removed.  The top of the foundation shall be re-shaped if necessary.

- The underside of each steel base, particularly in the bearing areas, shall be cleaned and any burrs and ragged edges removed before the base is placed in its final location.

- All holding-down bolt sleeves shall be thoroughly cleaned of any materials that may prevent the grout from flowing freely to the bottom of the bolt sockets.

- The base shall be properly aligned and levelled and shall be maintained in that position during grouting.

- After the machine or structural bedplate has been placed the following precautions shall be observed:

  - Shimming shall be kept to a minimum.  Steel plates shall be used for packing and shall be ground to the required thickness, where necessary.

  - Before grouting is started all loose dirt, oil, grease, and other foreign matter on the surface of the foundation, the undersides of bedplates, and in the bolt holes shall be removed by means of compressed air or other approved means.

  - The surface of the foundation slab shall be thoroughly saturated with clean water, and all free water shall be removed from the surface and the bolt holes just before the grout is placed.

  - Grouting shall not be carried out until the alignment of all units to be grouted has been checked and approved by the Project Manager.

  - Special care shall be taken with grouting in hot or cold weather to ensure proper setting and gain of strength and, in the case of proprietary grouting materials, by having ice or hot water available, as the case may be, in accordance with the instructions of the manufacturer.

  - Enclosures shall be provided for the grout such that, until it has set, its temperature will be in the range 15°C -27°C. Shields to protect the grout from the sun and from hot winds shall be provided by the Contractor when so ordered.

##### PSG 5.5.13.3	Formwork

Formwork for grouting shall comply with the applicable requirements of Clause 5.2 of SANS 1200 G. Forms shall be caulked where necessary. Adequate clearance between forms and bedplates shall be provided to enable the grout to be worked into place.

PSG 5.5.13.4	Mixing (all free-flowing grouts except epoxy grouts)

The grout shall be mixed to a homogeneous uniform mixture and delivered ready for placing at a temperature between 15°C and 25°C. The materials and water shall be mixed in a mortar mixer for at least 3 min. or, in the case of small jobs only, shall be thoroughly mixed by hand, the entire mass being turned over enough times to ensure even distribution of its components.

The mixing shall be done as close as possible to the place(s) where the grout is placed.  No more grout shall be mixed at any one time than can be placed in a period of 20 min.  After the grout has been mixed it shall not be retempered by the addition of water.

PSG 5.5.13.5	Grouting (all free-flowing grouts except epoxy grouts)

The grout shall be placed quickly and continuously to avoid the undesirable effects of over-working. (These effects are segregation, bleeding, and breaking-down of initial set).  The method of placement shall be subject to approval. The means of placing the grout shall be such that the grout will completely fill the space to be grouted, will be thoroughly compacted, will be free of air pockets, and will have evenly distributed contact over an area in excess of 80% or, in the case of expanding grout, 95% of the bearing area of the item to be supported.

Wherever practicable, grout shall be placed from one side only and where this is not practicable, care shall be taken to ensure that any entrapped air is released.

After the grout has taken its initial set:

    - The forms shall be removed.

    - Excess grout shall be so cut away as to leave a smooth and neatly finished job.

    - except where the grout is intended to provide resistance to side thrust, all edges shall be trimmed at 45° to the vertical, from the bottom edge of the bedplate; and

    - All excess grout on or about the bedplates shall be removed.

Damage to paintwork, if any, shall be repaired within 24 hours.  Packing plates, shims, and other levelling devices shall remain in position.

PSG 5.5.13.6	Dry-packed grout (standard dry sand and cement grout)

Dry-packed grout shall have a minimum compressive strength at 28 d of 20 MPa.  The quantity of water added after placing shall be kept to a minimum consistent with placing conditions, and the cement, sand and, where applicable, pea gravel proportions by mass shall be as follows:

- Where the clearance between bedplate and foundation is 25 mm or less: 1 part of cement and 2 parts of sand.

- Where the clearance exceeds 25 mm: 1 part of cement, 1 part of sand, and 1 part of pea gravel.

- Dry-packed grout shall be rammed by means of tamping rods against formwork placed along three sides of the bedplate.

PSG 5.5.13.7	Non-shrink grout with metallic aggregate

The manufacturer's instructions shall be observed when non-shrink grout with metallic aggregate is used.

Where the clearance between the bedplate and the foundation is less than 50 mm a sand-based mix shall be used.  Where the clearance exceeds 50 mm the Project Manager may order a mix with a base of sand plus pea gravel to be used.

PSG 5.5.13.8	Expanding grout with powdered aluminium additive

The manufacturer's instructions shall be observed when an expanding grout with powdered aluminium additive is used.  Where the clearance between the bedplate and the foundation is less than 25 mm, a sand-based mix shall be used.

Where the clearance exceeds 25 mm the Project Manager may order mix with a base of sand plus pea gravel to be used.

Each batch shall be mixed for at least 6 min. after the powdered aluminium has been added.  Where a ready-mixed grout is used, the powdered aluminium shall be added at the placing Site and the batch mixed as specified in PSG 9.4.  Grout shall be placed within 45 min. after the addition of the powdered aluminium.

The Contractor shall not use powdered aluminium additive when the ambient temperature is below 5°C.

PSG 5.5.13.9	Epoxy grout (epoxy mortar type only)

The manufacturer's instructions shall be observed when an epoxy grout is used.

PSG 5.5.13.10 Testing (Clause 7)

The Contractor shall, where so ordered, carry out a Site test for each grouting procedure and each grouting gang to be used. The tests shall be carried out on a dummy bedplate similar in configuration to that, which is to be grouted, but not exceeding 1 m in area unless otherwise ordered.

When the dummy bedplate is dismantled, the underside shall show a minimum grout contact area of 80% with reasonably even distribution of the grout over the surface grouted except that, in the case of expanding grout, the minimum grout contact area shall be 95%. The test shall show evidence of good workmanship and materials and the results shall be to the satisfaction of the Project Manager.

The Contractor shall, when so ordered, make standard test cubes from various grout mixtures and subject them to compression tests to determine whether the specified strength has been achieved.  Test procedures shall comply with the relevant requirements of Sub-Clause 7.2.1 to 7.2.4 SANS 1200 G.

##### PSG 5.5.16 	No-Fines Concrete

###### PSG 5.5.16.1	Materials

Cement, aggregate and water shall comply with the requirements of Clause 3 of this section. Each size of aggregate shall be a single-sized aggregate graded in accordance with SANS 1083.

###### PSG 5.5.16.2	Classes of no-fines concrete

No fines concrete shall be classified by the prefix NF and the size of the aggregate to be used.  Class NF 20 means a nofines- concrete with a 19 mm nominal size aggregate.

The volume of aggregate per 50 kg of cement for each class of nofines- concrete shall be as follows:

Table 8: Volume of aggregate per 50kg of cement for each class of NF concrete

| Class | Aggregate per 50kg cement |
| --- | --- |
| NF 40 | 0,33 m3 |
| NF 20 | 0,30 m3 |
| NF 10 | 0,27 m3 |

###### PSG 5.5.16.3	Batching and mixing

Cement shall be measured by mass or full bags of 50 kg each and aggregate shall be measured by volume in approved measuring boxes or barrows.

The quantity of water added shall be just sufficient to form a smooth grout that will adhere to and completely coat each and every particle of aggregate and to be just wet enough to ensure that, at points of contact of the aggregate, the grout will run together to form a small fillet to bond the aggregate together.  The mix shall contain no more than 20 l of water per 50 kg of cement. Mixing shall be carried out in an approved batchtype mechanical mixer, but small quantities may be hand mixed.

Fibre Reinforced concrete Mixing Requirements

Mixing Duration:

- If fibres are added with other ingredients: Mix concrete for a minimum of 5 minutes at full mixing speed.

- If fibres are added post-mix: Increase mixing time by 1 minute per m³ of concrete volume.

Dosing: Dosage to be as per supplier recommendation, based on concrete volume or kg/m³.

- Synthetic macro fibre dosage typically ranges between 4-10 kg/m³.

- If steel fibres are used, increase dosage to 50 kg/m³, accounting for adjustments in mix design to coat fibres and maintain workability.

###### PSG 5.5.16.4	Placing

No-fines concrete shall be placed in accordance with the procedure agreed on by the Project Manager. It shall be placed in its final position within 30 minutes of mixing.

The nofines concrete shall be worked sufficiently to ensure that it completely fills the space to be concreted and that adjacent aggregate particles are in contact with one another. Excessive tamping or ramming shall be avoided and under no circumstances may the nofines concrete be vibrated.

Fibre Reinforced concrete Mixing Requirements:

Bleed Water Management: Allow all bleed water to fully evaporate before any finishing processes.

Fibre Post-Treatment:

- Steel fibres (if used): Cut flush after finishing.

- Synthetic polypropylene fibres: Burn off if necessary to maintain surface aesthetics.

###### PSG 5.5.16.5	Protection

All no-fines concrete shall be protected from the elements and loss of moisture.  Protection against loss of moisture shall be accomplished in one or more of the following ways:

- Retaining formwork in place.

- Covering exposed surfaces with sacking or other approved material kept continuously wet.

- Covering exposed surfaces with plastic sheeting.

No-fines concrete placed during cold weather shall be adequately protected against frost for at least 3 days.

###### PSG 5.5.17	Joints in structures

###### PSG 5.5.17.1	Materials

###### General

All materials used in the forming, construction and sealing of permanent joints, as well as all proprietary or custombuilt -expansionjoint- assemblies shall be subject to the approval of the Project Manager.

When required by the Project Manager, the Contractor shall submit test certificates from an approved independent testing authority to show that the respective materials comply with the specified requirements, or a certificate from the patent holder or designer to certify that the manufactured item complies in all respects with relevant product specifications.

Where steel shear dowels are required in joints, the dowels must be given a single coat of Zinc-rich epoxy/paint as a corrosion protection measure.  The cost of painting the dowels shall be included in the cost for providing and installing the dowels.

Joint filler

Joint filler shall comply with the requirements of the following specifications:

- American Association of State Highway Officials (A.A.S.H.O.) Standard Specification M153-54 Type I and III.

- National Transport Commission "Standard Specification for Roads and Bridge Works".

- Department of Public Works PW471 "Specification of Materials and Methods to be used" Section 3.13 Expansion Joints.

Joint fillers shall consist of closed cell expanded polyethylene with a density of not less than 120 kg/m³.

Sealants

Joint sealers shall consist of a two-component polyurethane sealing compound complying with the requirements of SANS 1077.

Other sealants may be used if approved by the Project Manager after submission of full specifications and information by the Contractor at tender stage.

Waterstops

Waterstops shall be of natural rubber, or plasticized, virgin, non-biodegradable PVC, and of the type specified or shown on the Drawings.

- Natural rubber waterstops shall comply with the requirements of CKS 388.

- Flexible polyvinyl chloride (PVC) rubber waterstops shall comply with the requirements of CKS 389.

Accessory materials

- Primers

When a primer is to be used in conjunction with the sealant, it shall be of theprescribed proprietary material.

(ii)	Adhesive

Adhesives used in conjunction with preformed seals shall be of a proven and approved type, which is compatible with the material of the seal.

(iii)	Bond breakers

Flat PVC adhesive tape or similar approved material may be used where bond breakers are required.  The use of halfround or rounded backup chords as bond breakers is strictly prohibited.

(iv)	Back-up material

Back-up materials shall be compatible with the sealant used. Material containing bitumen or volatiles shall not be used with thermosetting chemically curing sealants.

(f)	Storage

All materials used in the forming, construction and sealing of permanent joints and all proprietary or custom built expansion-joint assemblies shall be stored off the ground under cover that provides adequate protection against sunlight, physical or chemical damage or other factors that may cause deterioration.

###### PSG 5.5.17.2	Filled Joints

Filled joints shall be accurately formed to the dimensions shown and with the filler material specified in PSG 5.5.17.1 (b). The filler shall be secured in position so that it will not be displaced during or after concreting if the filler is to remain permanently in the joint.  In addition the filler shall be provided with a cut line prior to installation.

This cut line, intended to aid removal of a portion of the filler to make room for the sealant, shall be in a position, which coincides with the depth of the sealant.

Wherever polystyrene or a similar material, which is susceptible to damage, is used to form joints it shall be lined with a hard surface on the side to be concreted. The hard surface shall be sufficiently resilient to ensure that the joint and surfaces can be formed free from defects.

###### PSG 5.5.17.3	Sealing of Joints

General

Sealed joints shall be made watertight over the full length of the joints, unless otherwise permitted by the Project Manager, and the joint dimensions shall be as shown on the Drawings.

Preparation of joints

The reaming of joints by sawing or other means shall be undertaken when edge spalling or ravelling can be avoided and shall be subject to the Project Manager's approval.

After removal of the temporary filler material up to the cut line or the breaking-out of the excess concrete, the inside faces of the joint shall be wire-brushed or grit-blasted to remove all laitance and contaminants. Thereafter the joint shall be cleaned and blown out with compressed air to remove all traces of dust.  Solvents shall not be used for removing contaminants from concrete and porous surfaces.

Immediately prior to the priming and sealing of the joints the Contractor shall call for inspection of the joint preparation by the Project Manager.  The joint preparation shall be inspected and signed off in the Site instruction book by the Project Manager immediately prior to the application of the primer and sealant.  The signing off of the joint preparation shall not relieve the Contractor of his obligations under the Contract.

Care shall be taken to ensure that primers or adhesives are applied only to surfaces that are absolutely dry. The primer or adhesive shall be applied strictly in accordance with the manufacturer's instructions.  Unless otherwise specified, the primer shall be applied within the temperature range of 10°C to 40°C and the sealant shall be applied after the curing period of the primer and within the period during which the primer remains active.

A flat PVC adhesive bond breaking tape shall be applied to the filler prior to adding the sealant in order to prevent bondage between sealant and filler.

Sealants

Sealants and primers shall be applied strictly in accordance with the manufacturer's instructions by a person skilled in the use of the particular type of sealant. The trapping of air and the formation of voids in the sealant shall be avoided.  The sealant shall be finished to a neat appearance flush with the edges of the concrete or to the specified depth.

Thermoplastic hot-poured sealants shall not be poured into the joints when the temperature of the joint is below 10°C.  The safe heating temperature shall not exceed the specified pouring temperature by more than 10°C.

Two-part thermosetting chemically curing sealants shall not be applied after expiry of the specified pot life period, which shall commence once the base and activator of the sealant have been combined.

Preformed compression seals

The seal shall be inserted and secured with a lubricant adhesive which covers both sides of the seal over the full area in contact with the inside faces of the joint. The lubricant adhesive shall be applied immediately before the seal is inserted.

The seal shall be installed in a compressed state, with the appropriate equipment, so that the seal will remain in compression even under the most adverse conditions. The final position of the seal shall be as shown on the Drawings or as directed by the Project Manager.

Joints in seals shall be bonded or fused and shall be only at positions agreed on by the Project Manager.

Waterstops

General requirements

The waterstops shall be supplied in unjointed standard production lengths. Site jointing shall be limited to the absolute minimum.  Where lengths in excess of the standard production lengths are required, such longer lengths shall preferably be factory jointed.

At intersections, transitions and abrupt changes of direction, factory-moulded watertight junction pieces shall be used so that any Site jointing can be restricted to simple butt joints.

When a waterstop with a centre bulb is intersected, the centre bulb shall be continuous throughout the intersection irrespective of the make-up of the intersection.

Rubber waterstops

All joints shall be vulcanized and shall have a tensile strength of at least eighty (80) per cent of that of the unjointed material for water-retaining structures, and fifty (50) per cent for other structures.

Site joints shall be vulcanized joints made in accordance with the requirements of these Specifications and the manufacturer's instructions, and with equipment prescribed or supplied by the manufacturer and approved by the Project Manager.

The vulcanizing process shall be a hot process with strict control on the pressure, the temperature and the time. The vulcanizing temperature shall be between 150ºC and 160ºC.  The rubber shall not be heated above 160ºC. The vulcanizing time for the specific type of rubber of the waterstops involved shall be determined with a curometer for the abovementioned vulcanizing temperatures before a vulcanized joint is made. The recommended pressure between the two sections which must be vulcanized is 3,4 MPa and the minimum allowable pressure is 2,4 MPa.

The contact faces of the sections to be jointed shall be accurately and evenly cut at the angle shown on the Drawings or prescribed by the Project Manager to obtain a precise fit and complete contact.

Care shall be taken to keep centre bulbs unobstructed at the joints so that the lateral flexibility of the waterstops will not be affected by the presence of clotted rubber inside the bulbs. The rubber of the waterstop shall not have any porosity of voids between the contact faces of the sections and/or at the finished vulcanized joint, especially at the centre bulb.

The vulcanizing equipment shall comply with the following minimum requirements:

The heating elements shall be equipped with an automatic temperature-control device to keep the elements at the required temperature.

It shall be equipped with an automatic temperature-control device to keep the heating elements at the required temperature, with a device to measure the temperature at the vulcanizing plane, a device to measure the temperature applied to the external faces of the rubber, and with a pressure gauge to regulate the applied pressure within the specified limits in relation to the liquidity of the rubber.

During the vulcanizing process the pressure shall be spread evenly over the entire contact area and the pressure plates shall be sufficiently rigid that they will not bend under the applied pressure. The cut-out forms of the pressure plates shall fit accurately over the waterstops so that all the faces of the waterstops will be in contact with the pressure plates.

The planes of contact of the two sections of the waterstops to be joined together shall be prevented from sliding from each other when pressure is applied to the plates. A shield shall be available to shield the apparatus against wind, rain, etc. when joints are made in the open to ensure proper temperature control.

The apparatus as a whole shall be safe in all respects and shall comply with all the appropriate statutory requirements.

Plasticized, flexible PVC waterstops

The waterstops shall be manufactured from high-quality virgin material and shall not contain any scrap or reclaimed material. The waterstops shall be light coloured so as to reduce heat absorption when exposed to sunlight.

The waterstops shall be precision moulded or extruded to the required cross-sectional profile, they shall be free from porosity or other imperfections, and shall be provided with eyelets so that they can be securely fixed to prevent displacement during concreting.

All joints shall be butt-jointed hot-welded joints. Where joints cannot be factory made, Site joints shall be made in accordance with the manufacturer's instructions with equipment prescribed or supplied by the manufacturer and approved by the Project Manager.

Bandages

Bandages shall consist of a highly flexible, waterproof and weatherproof polymer sheeting between two layers of two component, solvent free, moisture insensitive, high viscosity, epoxy paste adhesive.  The material, method of application, names of supplier and instance doing the installation shall all be to the approval of the Project Manager.

###### PSG 5.5.18	Building in of Pipes

The Contractor under this Contract shall be responsible for building-in or caulking and making watertight around all pipes and fittings which pass through walls or under floors of the structures, irrespective of whether the Contractor himself supplies and installs the pipes and fittings, or the Employer purchases the pipes and fittings and the Contractor under this Contract takes delivery and installs them, or some other Contractor (e.g. a plant supplier) supplies and installs the pipes and fittings in recesses or through holes left in the various structures for the reception of such pipes and fittings.  In the latter case the Contractor under this Contract will be paid for forming the openings for and caulking of these pipes or fittings under the item provided for this purpose in the Schedule of Quantities.

Where pipes or specials are required to pass through or be set into concrete work, holes shall be left in the concrete.

Before commencing the positioning in holes of any pipes/specials the Contractor 		shall:

- Cut the reinforcement to allow the pipe to be installed.

- Remove all shuttering and boxing remaining in the holes.

- Make any alterations required to the position and shape of the holes.

- Thoroughly clean the sides of the holes so as to obtain a satisfactory bond surface for the new concrete; and

After accurately positioning the pipes/specials in their respective holes, the Contractor shall fix the pipes/specials in the holes. Immediately before grouting is carried out by the placing of mortar and concrete around the pipes, the surface of the existing concrete shall be saturated with water.  All surplus water shall be removed and the surface covered with a layer, approximately 12 mm thick, of mortar consisting of 3 parts of concrete sand and 1 part of cement.

The concrete ingredients shall be mixed and placed as dry as possible to obtain a dense, waterproof concrete.  Where a watertight seal is required, the concrete shall be carefully worked around the puddle flange, if any, and the pipe barrel or body of the special, and shall be vibrated in layers so as to obviate any falling away from pipe/special surfaces of the concrete already placed. The whole shall, when set, form a dense, homogeneous, and waterproof mass.  A spare vibrator with an independent power source shall be kept in readiness to ensure continuity of placing in the event of the breakdown of the duty vibrator.

Smooth formwork that has been suitably strengthened for use with a vibrator shall be provided for facing the concrete around each pipe/special.

Alternatively, pipes may be cast into the wall in which case the pipes shall be installed in the required position with the formwork fixed around them and the concrete worked thoroughly into contact.

###### PSG 5.5.19	Foundations for Mechanical Equipment

The Mechanical Contractors shall supply the holding down bolts for all mechanical equipment, together with all dimensions and other details necessary for the construction of the pedestals and holding down bolt pockets, or the fixing of the bolts.  The Contractor shall either form pockets for the holding down bolts to be installed at a later stage or he shall position the bolts before the concrete is cast as ordered by the Project Manager.  The Mechanical Contractor shall fix, align and level the mechanical equipment after which the Contractor shall grout up the units solidly by filling the voids inside and under the base plates as ordered with an approved non-shrink grout.

###### PSG 5.5.20	Testing for Water tightness

The structure that has to be tested for water tightness shall be filled with water at a uniform rate not exceeding 2,0m in 24 hours until the top water level has been reached. The water level will then be carefully noted and recorded by the Project Manager in relation to a fixed bench-mark, and the structure shall be allowed to remain filled for a period of two weeks to permit complete absorption of water by the concrete.

Any loss of water which may have occurred shall then be made up by again filling the structure to the top water level and by allowing the water to remain undisturbed for a period of not less than four days.  The structure shall be considered to be watertight if the drop in level in 96 hours (less the drop caused by evaporation) does not represent more than 0,06% of the volume of the structure.

The evaporation shall be measured by the mean drop in level caused by the evaporation of the water in three flat containers floating in the water, being recorded.

The Contractor is free to attend the taking of all measurements by the Project 	Manager.

In the event of an appreciable leakage being evident or visible at any stage of the filling or testing, or in the event of the final degree of watertightness being unsatisfactory, the Contractor shall, when so ordered by the Project Manager, discontinue such filling or testing that shall, at his own expense, take approved steps to rectify the leakage, until a test proves that a sufficient degree of watertightness has been obtained.

Before the expiry of the Defects Liability Period, the Project Manager shall have the right to retest the structure for watertightness; results of such further tests will be made available for the information of the Contractor.  In the event of these tests indicating an unsatisfactory degree of watertightness, the Project Manager will, before issuing the final certificate, again require the Contractor to rectify the leakage, at his own expense, in such a manner as will the soundness of the work, to the satisfaction of the Project Manager.

Water for testing purposes is will have to be available from the existing Chlorination Contact Tank but all costs connected to the conveyance of the water from the tank to the structures to be tested including the emptying of the structures afterwards will be for the Contractor’s account.

The costs of retesting the structure for water tightness shall be borne by the Contractor.

PSG 7		Tests

PSG 7.1.1		Facilities

Testing will be done in accordance with SANS Methods 860, 861-3 and 863.

PSG 7.1.2.2		Add the following to the end of this Sub-Clause: “or part thereof”

PSG 7.1.2.3		Add the following:

The minimum sampling frequency shall be as follows:

- One set/ batch/day or

- One set/ delivery or

- One set/ 50m3

The Construction Manager reserves the right to change the frequency of test work required to confirm conformance for any infrastructure for the ADF should he deem it necessary. He will notify the Contractor in advance and in the form of a site instruction issue the Contractor with a change in required testing frequency

PSG 8.11 APPLICABLE STANDARDS

Delete the following standards:

BS 1370			Low heat Portland cement.

SANS 471		Portland cement (ordinary, rapid-hardening, and sulphate-resisting).

SANS 626		Portland blast furnace cement.

SANS 831		Portland cement 15 and rapid-hardening Portland cement15.

SANS 		Methods 856, 861, 862 and 863.

Add the following standards:

SANS EN 197-1		Cement – Part 1: Composition, specifications and conformity criteria for common cements.

SANS 1491: Part 1		Ground granulated blast furnace slag.

SANS 1491: Part 2		Fly ash.

SANS 1491: Part 3		Condensed silica fume.

SANS Method 860: 1994		Concrete tests – dimensions, tolerances and uses of cast specimens.

SANS Method 861-2: 1994		Concrete tests – sampling of freshly mixed concrete.

SANS Method 861-2: 1994		Concrete tests – making and curing of test specimens.

SANS Method 862-1: 1994		Concrete tests – consistency of freshly mixed concrete – slump test.

SANS Method 863: 1994		Concrete tests – compressive strength of hardened concrete.

ASTM C494/C494M	Standard Specification for Chemical Admixtures for Concrete.

ASTM C260	Standard Specification for Air-Entraining Admixtures for Concrete.

PSH: 		SANS 1200 HA STRUCTURAL STEELWORK (SUNDRY ITEMS)

PSHA 2 	Interpretation

PSHA 2.1 	Supporting specifications

(C) SANS 1200 H: 1990 (2002-07-30)

PSHA 3 	Materials

PSHA 3.3 	Bolts, Nuts and Washers

PSHA 3.3.1 	Bolts and Nuts (other than friction grip)

Add the following to this Sub-Clause:

All bolts and nuts shall comply with the requirements of SANS 136:1988/150 1458: 1988 and shall be 4.6 strength grade.  Washers shall be provided at each nut and shall be of the same material (or coating where applicable) to match the bolt and nut.  Single coil square section spring washers shall be fitted to all nuts subject to vibration. Bolts other than jacking bolts shall project not less than 3 mm and not more than 10 mm from the heads of the nuts after tightening.

Holding down bolts to be built into concrete work as well as bolts to be installed above ground level directly above and under water shall all be of stainless steel grade 304.  Bolts for flexible couplings and flanges for underground installation shall be hot-dip galvanized in accordance with the requirements of SANS 763.

Bolts to be installed inside buildings shall be hot-dip galvanized in accordance with the requirements of SANS 763 and afterwards painted with the pipework and fittings as specified in the Standardized Corrosion Protection and Painting Specification for Civil Engineering Construction Suitable plastic sleeves and/or washers shall be used for protection against corrosion by metallic action. All elements to be of grade 304L stainless steel or as specified on the drawings

PSHA 5.2 	Fabrication and Assembly

PSHA 5.2.6 	Handrails

Substitute the first sentence of HA 5.2.6 with the following:

Handrails shall be of the tube and sphere type similar to Monoweld and shall be manufactured by an approved firm specialising in such works. Stainless steel will be used, unless other material specifically been described in schedules of quantities.

Handrails shall be 1 000 mm high and shall consist of a handrail and a knee-rail, both manufactured of steel tubing of nominal thickness 2,6 mm and of nominal outside diameter of at least 34 mm.

Stanchions shall be manufactured pre-formed in one piece and shall be of steel tubing of nominal thickness of 2,6 mm and of nominal outside diameter of at least 42 mm. The bases of the stanchions shall be manufactured of 150 mm x 75 mm x 12,5 mm flat bars and shall be pre-formed to suit the situation in which they are to be installed (i.e. for platform- or side mounting, and for horizontal- or sloped-mounting on concrete), and the stanchion spheres shall be pre-formed to suit right angled or other angled intersections), all as shown on the drawings.

Stanchions shall be spaced at intervals not exceeding 1,5 m and shall be fixed with two M16 bolts, washers and nuts each. All joints shall be welded. Kicker plate should be installed along the length of the handrailing and should be 3mm stainless steel plate, 100mm high and should be fixed to the stanchions.

All stainless steel components shall have a No. 1 surface finish and surfaces shall be pickled and passivated in accordance with the requirements of the Standardized Corrosion Protection and Painting Specification for Civil Engineering Construction. Materials shall be as shown on the drawings or as scheduled

PSHA 5.2.11 	Stainless Steel Flat Bar for Batten to anchor liner

PSHA 5.2.11.1Ash Disposal Facility

Battens holding down the geomembrane liner to the outlet drain structures shall be manufactured from 304L Stainless Steel or as otherwise specified on the detailed design drawing. If no dimensions are shown the batten shall be 40mm wide by 6mm thick. The holes for the bolts will be drilled on Site and will suite a M10 wedge bolt 100mm in length at 150mm spacing c/c. The material between the concrete surface and the geomembrane and geomembrane and batten will be a 40mm wide 6mm thick neoprene rubber gasket.

PSHA 5.2.11.2 PCD and RRD)

Battens holding down the geomembrane liner to the concrete penstock bases and outlet drain structures shall be manufactured from 304L Stainless Steel or as otherwise specified on the detailed design drawing. If no dimensions are shown the batten shall be 50mm wide by 6mm thick. The holes for the bolts will be drilled on Site and will suite a M10 chemical anchor bolt 100mm in length at 200mm spacing c/c.

The anchor system selected is to be approved by the Project Manager prior to installation. The approved anchor is to be installed as per the manufacturers’ recommendation. A torque wrench is to be used when fastening the holding down bolts to the required specification. The material between the concrete surface and the geomembrane and geomembrane and batten will be a 40mm wide 6mm thick neoprene rubber gasket. An adhesive sealant known as Sikaflex -11 FC+ is to be applied between an around each anchor in a continuous strip prior to the 1st gasket being placed.

PSHA 5.2.21	Sluice Gates

All parts shall be designed for the duty required, but the minimum factor of safety against structural failure shall not be less than 3, based on the working stress of the material.  In the design, due consideration shall be given to the thickness of materials with regard to corrosion and operating conditions.  The force required at a handwheel or crank to raise a gate or open a penstock shall not exceed 120 Newton.

Unless otherwise scheduled the frames and gates of sluice gates shall be made of grade 304 stainless steel with a thickness suitable for the duty required but shall not be less than 3,5mm thick.

All gates shall be well guided with no possibility of jamming.  The gates of wall mounted types shall be held uniformly against the side facings of the frames by the action of adjustable wedges and shall provide drop-tight closure.  Sluice gates (any seating condition) shall not spill water over the top or sides of the frame other than through the opening provided in the penstock for the water to pass through.

All sluice gates shall be of the level invert type fitted with renewable seals of a non-biodegradable material on the invert.

Sluice gates shall have rising spindles protected by suitable transparent nylon sleeves, the latter providing convenient visual inspection and greasing facilities.  Handwheels shall be of cast iron with diameters to suit operating either directly on the head frame or on a tubular pedestal of the same material to suit the installation depth, as shown on the Drawings.  Where necessitated by the mass of the gate and/or the pressure against the gate, suitable gearing shall be provided.

All sluice gates measured in the Schedules of Quantities shall be supplied and installed by the Contractor under this Contract.  In the case of gates to be fixed against concrete walls, holding down bolts made of 304 stainless steel must be supplied and installed into the concrete work.  The Contractor shall also execute the complete grouting of the penstocks and carry out all necessary adjustments to ensure proper and smooth operation of the gates.

PSHA 5.2.21	Adjustable Weirs

The Weirs shall have the following design parameters:

- It shall be of the bottom hinged type.

- It shall be 3 sided sealing.

- The flow over the top of the weir shall be controlled by adjusting the height of the weir.

- The weir shall be of robust construction and suitably braced to avoid distortion.

- It shall be manufactured of 6 mm thick stainless steel 304.

- Bearings shall be suitable for submerged operation.

- Each outlet weir shall fit on a concrete wall 250 mm thick, in an opening 5,0 m wide.

- The concrete wall on which the weir is fitted is 500 mm below the normal water level.

- It shall be possible to lower the water level with 200 mm below the normal water level.

- It shall also be possible to raise the water level with 200 mm above the normal water level.

- The weir shall be fitted with a hand wheel on a pedestal for normal operation.

- The weir shall also be fitted with an actuator on the pedestal for automatic operation.

PSL: SANS 1200 L: MEDIUM PRESSURE PIPELINES

PSL 2		Interpretations

PSL 2.2 	Application

Add the following to L 2.2:

The following specification will be applicable to High Density Polyethylene (HDPE) solid, drilled High Density Polyethylene (HDPE) solid and perforated (slotted) pipes unless specified otherwise in the detailed engineering drawings.

PSL 3 		Materials

PSL 3.8 	Jointing Materials

PSL 3.8.3 	Flanges and Accessories

Add the following to this Sub Clause:

Unless otherwise scheduled the dimensions and drilling of standard flanges shall comply with the requirements of SANS 1123: 2003 table 16 for pipes and fittings with a diameter of 150 mm and smaller and in accordance with table 10 for diameters exceeding 150 mm.  Flanges shall be machined flat, i.e. without a raised joint face.  Puddle flanges shall have the same dimensions as standard flanges but shall be undrilled.

Faces of flanges which will be in contact with jointing gaskets shall receive a protective coating similar to the corrosion protection specified for the internal surface of the pipes and fittings of such thickness and consistency as will not impair the air/gas/water tightness of the joint The jointing gaskets shall comply with the requirements of BS 3063 and shall be cut to the full width of the flange and holed for bolts.

PSL 3.9 	Corrosion Protection

Delete this Clause and refer to the Standardized Corrosion Protection and Painting Specification for Civil Engineering Construction (Corrosion Protection Specification for Civil, Mechanical and Electrical Engineering Construction, New revised 2006 Edition, prepared by Golder Associates Africa), obtainable from Golder Associates Africa (Pty) Ltd.

PSL 3.12 	HDPE pipes material quality.

Unless specified otherwise in the detailed design drawings the HDPE used shall be PE 100 pipes Class 20 for solid and drilled pipes. For corrugated and corrugated perforated pipe the following specification is applicable:

Table 9: Physical properties of HDPE pipes

| Physical properties description | Property value | Test method |
| --- | --- | --- |
| Material density | 940g/m3 | ISO 1183 |
| Material MFI | 0.45g/10min | ISO 1883 |
| Tensile strength at yield | 27 MPa | ISO 527 |
| Resistance to compression | Type 450 | SANS 61386-24 |
| Minimum slot diameter | 15mm |  |

PSL 4 		Plant

PSL 4.3 	Testing

Add the following to L 4.3:

The Contractor must ensure that the test equipment is in good working order and that it is calibrated.

PSL 7 		Testing

PSL 7.3 	Standard Hydraulic Pipe Test

PSL 7.3.1.2 	Test Pressure

Substitute L 7.3.1.2 with the following:

The test pressure for field testing shall be 1,5 times the rated maximum working pressure of the pipe. Subsoil and leachate collection systems shall be tested to 2 Bars or 200 KPa.

PSLB: SANS 1200 LB: BEDDING (PIPES)

PSLB 1 	Scope

Add the following to LB 1.1:

This specification also covers the bedding required for electric cables.

PSLB 3 	Materials

PSLB 3.1 	Selected Granular Material

Substitute LB 3.1 with the following:

Selected granular material shall be an aggregate, sand or granular material, all of a non-cohesive nature and free from any organic material, of which the grading analysis shows 100 % passing a 13,2 mm sieve and not more than 5 % passing a 0,075 mm sieve.

In very wet conditions and if so ordered by the Project Manager, a non-plastic crushed material with the specification as stated underneath should be used for bedding cradle.

Table 10: Grading envelope for pipe bedding material

| Sieve size (mm) | % passing lower limit | % passing upper limit |
| --- | --- | --- |
| 19.0 | 100 | 100 |
| 13.2 | 84 | 100 |
| 9.5 | 70 | 84 |
| 4.75 | 45 | 65 |
| 2.36 | 29 | 47 |
| 1.18 | 19 | 33 |
| 0.6 | 13 | 25 |
| 0.3 | 10 | 18 |
| 0.15 | 6 | 13 |
| 0.075 | 4 | 10 |

Note: The Aggregate Crushing Value (ACV) determined at 13.2mm and 0.5mm fraction, must exceed 25

PSLB 3.2 	Selected Fill Material

Substitute LB 3.2 with the following:

The requirements of PS LB 3.1 shall apply mutatis mutandis.

PSLB 3.3 	Bedding

Add the following to LB 3.3:

All pipes shall be classified as flexible pipes and shall be laid on the appropriate bedding unless specified otherwise in the detailed engineering drawings.

PSLB 3.4.1 	Suitable Material Available From Trench Excavations

Substitute LB 3.4.1 with the following:

The provisos of PSD 3.3.1 shall apply mutatis mutandis.

PSLB 5 	Construction

PSLB 5.1 	General

PSLB 5.1.2 	Class of bedding

Unless otherwise directed on the detailed design drawings or instructed by the Project Manager, all pipes shall be laid on Class B bedding for rigid pipes or flexible pipe bedding.

PSLB 5.1.4 	Compacting

Substitute “90% MOD AASHTO in LB 5.1.4 with “93% Standard Proctor density at -2% to 2% OMC.”

PSLB 5.5 	Draining of Trenches

Where ground water is present to such an extent that, in the opinion of the Project Manager, it would hamper the placing and consolidation of the fine granular bedding or the placing of the concrete bedding in the bottom of the trench, as the case may be, or would cause buoyancy of the pipes, the Project Manager may order the provision of a drain in the bottom of the trench to assist in dewatering during construction and until the trench has been backfilled to such an extent as to prevent buoyancy of the pipes. No payment shall be made for this and all relevant costs shall be deemed to be included in the tendered price.

The drain ordered will be one of the types shown on the Drawing.  The particular one to be used will depend on the amount of water present and will be determined by the Project Manager in each individual case.

At certain points along the trench, depending upon the amount of water to be handled, sumps shall be formed from which the water may be pumped to prevent a build-up of water in the trench to a level above that of the top of the layer of stone forming the underdrain.

The stone in the underdrain shall consist of nominal 40 mm crushed stone complying with the grading as specified for 'Stone for Concrete' in Table 5 of SANS 1083: 2002 (as amended 1979), and shall be well compacted to provide a uniform support for the pipe bedding to be placed on top of it.

Before placing the granular bedding or the concrete bedding the underdrain shall be covered with building paper to prevent ingress of granular material or mortar into the interstices of the underdrain.

SANS 1200LE: STORMWATER DRAINAGE

PSLE 1		Scope

PSLE 1.1		Add the following:

This specification covers all the work in connection with the construction of subsurface drains and drainage blankets at the locations and to the size, shapes, grades and dimensions as shown on the Drawings or as directed by the Project Manager.

PSLE 2		Interpretations

#### PSLE 2.1	Supporting specifications

#### Submittals prior to construction

The following documentation shall be submitted by the Contractor to the Project Manager for approval prior to construction.

- Certificates of compliance on materials furnished, and Manufacturer's brochures containing complete information and instructions pertaining to the storage, handling, installation, and inspection of pipe and appurtenances furnished.

- The pipe and fittings manufacturer shall have an established quality assurance program responsible for inspecting incoming and outgoing materials.  The pipe manufacturer MUST be a member of the South African Plastic Pipe Manufacturers Association (SAPPMA).

- At a minimum, incoming polyethylene materials shall be inspected for density per ISO 1183, melt flow index as per ISO 1133, and contamination.  All incoming polyethylene materials shall be certified by the supplier.  Certification shall be verified by Quality Assurance.  Incoming materials shall be approved by Quality Assurance before processing into finished goods.

- The pipe and fittings manufacturer shall have an established quality assurance program responsible for assuring the long-term performance of materials and products.  Representative samples of polyethylene materials shall be tested against the physical property requirements of this specification.

- Each extrusion line and moulding machine shall be qualified to produce pressure rated products by taking representative production samples and performing sustained pressure tests in accordance with ASTM D-1598.

- Quality assurance test for representative pipe and fitting samples shall include:

Table 11: Quality assurance test

| Test | Test Method | Pipe | Fittings |
| --- | --- | --- | --- |
| Ring ESCR | ASTM F-1248 | Yes | Not Applicable |
| Sustained pressure at 80°C/5000 kPa hoop stress | ASTM D-1598 | Yes (f0>100 h) | Yes (f0>100 h) |
| Sustained pressure at 23°C/11000 kPa hoop stress | ASTM D-1598 | Yes (f0>100 h) | Yes (f0>100 h) |

- All outgoing materials shall be inspected for diameter, wall thickness, length, straightness, out-of-roundness, concentricity, toe-in, inside and outside surface finish, markings, and end cut.  Quality Control shall perform tests of density, melt flow rate, carbon content, and carbon dispersion.  In addition, samples of the pipe per ASTM D-1599 or ring tensile per ASTM D-2290.  Moulded fittings shall be subject to X-ray inspection for voids, and tests for knit line strength.  All fabricated fittings shall be inspected for fusion quality and alignment. The pipe and fitting manufacturer shall maintain permanent QC and QA records.

- The pipe and fitting manufacturer shall package products for shipment in a manner suitable for safe transport by commercial carrier.  When delivered, a receiving inspection shall be performed, and any shipping damage reported to the pipe and fittings manufacturer.  Pipe and fittings shall be handled, installed, and tested in accordance with manufacturer’s recommendation, and the requirements of this specification.

- The Contactor shall submit to the Project Manager verified copies of all the pressure testing carried out on the pipelines.

#### PSLE 3		Materials

##### PSLE 3.1		Physical Properties

The Materials used for the manufacturer of polyethylene pipe and fittings shall meet the following physical property requirements for PE100:

Table 12: Physical property requirements for PE100

| Physical Properties | Test Method | Values | Unit |
| --- | --- | --- | --- |
| Density | ISO 1183 | 0.958 | g/cm3 |
| Melt flow index (190°C/21.6Kg) | ISO 1133 | 6.5 | g/10 min |
| Melt flow index (190°C/5Kg) | ISO 1133 | 0.23 | g/10 min |
| Vicat softening point (5Kg) | ISO 306 | 67 | °C |
| Crystalline melting range | ISO 3146-85 | 130-133 | °C |
| Viscosity number | ISO 1628-3 | 390 | cm3/g |
| Mechanical Properties | Test Method | Values | Unit |
| Shore D, Hardness | ISO 868 | 61 | - |
| Tensile @ Yield | ISO 527 | 25-30 | MPa |
| Ultimate Tensile | ISO 527 | 35 | MPa |
| Ultimate Elongation | ISO 527 | >600 | % |
| Elastic Modulus | ISO 527 | >800 | MPa |
| Flexural Stress (3.5% deflection) | ISO 178 | 19 | MPa |
| Notched Impact (Charpy) acN 23°C | ISO 179 | 20 | KJ/m2 |
| Notched Impact (Charpy) acN -30°C | ISO 179 | 6 | KJ/m2 |
| Thermal stability (OIT, 210°C) | 1SO 10837 | >60 | min |
| Carbon Black Content | ASTM 1603 | 2.0 – 2.5 | % |

There shall be no evidence of splitting, cracking or breaking when the pipe is tested in accordance with PSC 4.3 d). The pipe and fittings shall be homogenous throughout and free from visible cracks, holes, foreign inclusions or other injurious defects.  The pipe shall be as uniform as commercially practical in colour, opacity, density and other physical properties

##### PSLE 3.2		Pipe and Fittings

- Dimensions:

    - For pump conveyance pipes, SDR 13.6, PN 20

      - Pipe Dimensions: The nominal inside diameter of the pipe shall be true to the specified pipe size in accordance with ASTM D-2513.  Standard laying lengths shall be 6m.

      - Fitting Dimensions: Fittings such as coupling, wyes, tees, adaptors, etc. for use in laying pipe shall have standard dimensions that conform to ASTM D-3261.

- Where possible, pipe and fittings should be produced by the same manufacturer from identical materials meeting the requirements of this specification.  Special or custom fittings may be exempt from this requirement.

- Pipe and fittings shall be pressure rated to meet the service pressure requirements specified by the Project Manager.  Whether moulded or fabricated, fittings shall be fully pressure rated to at least the same service pressure rating *as the pipe to which joining is intended.

- Moulded fittings shall meet the requirements of ASTM D-3261 and this specification.  At the point of fusion, the outside diameter and minimum wall thickness of fitting butt fusion outlets shall met the diameter and wall thickness specifications of the mating system pipe.  Fitting markings shall include a production code from which the location and date of manufacture can be determined.  Upon request, the manufacturer shall provide an explanation of this production code.

- Each standard and random length of pipe and fitting in compliance with this standard shall be clearly marked with the following information:

    - ASTM Standard Designation

    - Pipe Size

    - Class and Profile Number

    - Production Code

    - Standard Dimension Ratio

##### PSLE 3.3		Source quality control

- The pipe and fitting manufacturer shall certify that samples of his production pipe have undergone stress regression testing, evaluation, and validation in accordance with ASTM D-2837 and PPI TR-3.  Under these procedures, the minimum hydrostatic design basis shall be certified by the pipe and fitting manufacturer to be 11000 kPa at 23°C and 5500 kPa at 60°C.

- Inspection requirements:

    - Notification:	If inspection is specified by the purchaser, the manufacturer shall notify the purchaser in advance of the date, time and place of testing of the pipe in order that the purchaser may be represented at the test.

    - Access:	The owner’s representative shall have free access to the inspection area of the manufacturer’s plant.  The manufacturer shall make available to the owners representative, without charge, all reasonable facilities for determining whether the pipe meets the requirements of this specification.

    - Certification:	As the basis of the acceptance of the material, the manufacturer will furnish a certificate of conformance of these specifications upon request.  When prior agreement is being made in writing between the purchaser and the manufacturer, the manufacturer will furnish other conformance certification in the form of affidavit of conformance, test results, or copies of test reports.

- Physical Test Requirements

    - Sampling: The selection of the sample of pipe shall be as agreed upon by the purchaser and the manufacturer.  In case of no prior agreement, any sample selected by the manufacturer shall be deemed adequate:

      - Sample size for flattening test will be one sample size and class of pipe per project.

      - Conditioning:	Conditioning of samples prior to and during test shall be as agreed upon by the purchaser and manufacturer.  In case of no prior agreement, the conditioning procedure used by the manufacturer shall be deemed adequate.

    - Test Methods

      - Flattening: Three specimens of pipe, a minimum of 300mm long, shall be flattened between parallel plates in a suitable press until the distance between the plates is 40 percent of the outside diameter of the pipe.  The rate of loading shall be uniform and such that the compression is completed within 2 to 5 minutes.  Remove the load, and examine the specimens for splitting cracking or breaking

.

Pipe Ring Stiffness Constant:  The pipe ring stiffness constant shall be determined utilising procedures similar to those outlined in ASTM D-2412.  The stiffness of HDPE pipe is defined in terms of the load, applied between parallel plats, which causes 1% reduction of pipe diameter.  Test specimens shall be a minimum of two pipe diameter of 1.2m in length, whichever is less.

PSLE 3.5		Geofabric Blanket

Delete this Sub-Clause and refer to Sub-Clause PSLE 3.7(c).

Add the following Sub-Clauses:

PSLE 3.6		Pipes

Pipes for the works shall be one of the following types as specified on the drawings:

    - Solid HDPE pipes and Solid HDPE drilled pipes as specified which comply with the requirements of SANS 4427.

    - Corrugated and corrugated HDPE perforated pipes as specified which comply with the requirements of DIN 4262 Part 1.

    - Perforated or slotted unplasticised PVC pipes which comply with the requirements of SANS 791.

    - Porous concrete pipes which comply with the requirements of BS 1194.

    - Vitrified clay pipes which comply with the requirements of  SANS 559 (excepting the requirement regarding nominal diameter) and which have special joints intended for subsoil  drains may be specified or used if the Project Manager's approval is obtained in advance, provided that, where the gaps at the joint do not conform to the requirement for the  slots specified below, the grading of the permeable material shall be suitable adapted to meet the design requirements for preventing permeable material from entering the pipe.

The size of perforations in perforated corrugated pipes shall in all cases be 15 mm in diameter ± 1,5 mm, and the number of perforations per metre shall not be fewer than 26 for 160 mm pipes. Perforations shall be spaced evenly in four rows or as  specified on the drawings.

Pipes without slots or perforations required for transporting subsoil water from the subsoil drain proper to the point of discharge shall be unperforated, sealed solid HDPE pipes as specified in the drawings.

PSLE 3.7		Permeable Material

Sand, crushed stone and geotextiles used as permeable filter materials for subsurface drains and drainage blankets shall conform to the following requirements:

- Sand

Sand shall be clean, washed river sand obtained from approved sources. The grading of the sand shall be subject to the Project Manager's approval and shall meet the grading envelop specified on the drawings. The requirements in respect of each type and the comparative prices of sand from the available sources will determine which source is to be used.

The Contractor shall submit samples and prices from available sources when so instructed by the Project Manager and will submit a grading analysis for each delivery to site for approval. All results will be documented and included in the final QCA pack after completion of the project.

- Crushed stone

Crushed stone shall be clean, washed, hard, durable crushed stone from approved sources. The aggregate crushing value of the stone shall exceed 25 when tested in accordance with method B1 of TMH1.

- Crushed stone for graded filters

Crushed stone for graded filters shall meet the grading envelop specified on the drawings and be washed. The aggregate shall be evenly graded between the coarse and fine fractions with no undue discontinuities. The aggregate crushing value of the stone shall exceed 25 when tested in accordance with method B1 of TMH1.

- Crushed stone for filters which incorporate geotextiles

Crushed stone for filters which incorporate geotextiles shall meet the grading envelop specified on the drawings and be washed.  The Project Manager shall indicate the type of stone to be used in each particular case. The aggregate crushing value of the stone shall  exceed 25 when tested in accordance with method B1 of TMH1.

- Geotextiles

If not otherwise specified, Geotextiles shall be a nonwoven, spun or -thermicbonded- continuous filament fabric consisting of at least 85% by mass of poly propylene, polyester or other approved material and manufactured for civil- -engineering applications by a recognized manufacturer. The brand and type of geotextile to be used shall be as specified in the Project Specifications or on the Drawings or as directed by the Project Manager.

PSLE 3.8		Polyethylene Sheeting

Polyethylene sheeting shall be black in colour with a minimum thickness of 0,15 mm and manufactured by a recognized manufacturer.

PSLE 5		Construction

PSLE 5.2.4   		Pipes with open joints laid with geofabric blanket wrapping

Delete this Sub-Clause and refer to Sub-Clause PSLE 3.6.

Add the following Sub-Clauses:

PSLE 5.8		Graded Filter Drains

After the completion of the excavations, the bottom portion of the trench shall be compacted and lined with polyethylene sheeting as shown on the Drawings. The top edges of the vertical portions of the sheeting shall be anchored  outside the excavation,  no nails or by any other holes will be allowed to anchor the polyethylene sheets . The sheeting shall be heat bonded at the laps with a minimum overlap of 300mm in the direction of water flow.  Geotextile- damaged during installation or construction shall be replaced at the Contractor's cost.

A layer of permeable material of the class and thickness as shown on the Drawings shall be placed on the polyethylene sheeting on the bottom of the trench and shall be lightly tamped and finished to the required gradient to serve as a bedding for the pipes.

Pipes of the type and size required shall then be firmly bedded in the permeable material, true to level and grade, and shall be coupled where required.  Where spigot and- socket pipes are used, the socket ends shall be laid upgrade with the spigot fully entered into the adjacent socket. Where plain butt- -ended pipes are used, they shall be laid firmly together to prevent the infiltration of backfill material.

Perforated and slotted pipes shall be joined by couplers and Solid HDPE or Solid Drilled HDPE pipes will be heat bonded by means of a hot plate machine and will be inspected by a certified HDPE inspector and the Engineer prior to backfilling as stated in PSDB 5.6.1.

Perforated and drilled pipes shall be laid with the perforations at the top unless otherwise shown on the Drawings or instructed by the Project Manager, in writing.  The higher end of a subsurface drain  pipe shall be sealed off with a loose concrete cap, and at the  lower end the pipe shall be built into a concrete headwall to  provide a positive outlet, or it shall be connected to stormwater  pipes or culverts, all as shown on the Drawings or as directed by the Project Manager.

All Stormwater or drainage conveyance systems shall be constructed from the lower en working upwards, care shall be taken by the contractor that no material enter the pipes and pipes and filter material will be sealed off during rain or during completion of construction each day. Should the Engineer suspect that material has entered the pipe or that pipes have been damaged due to the Contractors construction methodology, he will instruct the Contractor to perform a camara inspection at his own cost, the contractor will include for a camara inspection in his tender rate.

Successive layers of permeable material shall be placed after the pipes have been laid.  Permeable material shall be placed in layers not exceeding 300 mm at a time, and shall be lightly compacted. The total thickness of each type of permeable material shall be carefully controlled by means of spacers.

When successive layers are placed, the lower layer shall not be walked on and shall, as far as is possible, not be disturbed. Care shall be taken to prevent the contamination of permeable material during construction of the subsurface drains, and all permeable material contaminated by the soil or silt shall be removed and replaced by the Contractor at his expense.  Care shall also be taken at all stages not to perforate or otherwise damage the polyethylene lining.

The remainder of the trench shall be immediately backfilled with approved impermeable material preferably obtained from the excavations, in layers not exceeding 100 mm and compacted to 90% of modified AASHTO density, unless otherwise ordered by the Project Manager.  The trench must be specially protected against the ingress of water, soil and silt until the backfilling with impermeable material has been completed.

Permeable material in subsoil drains shall not be taken to the surface but shall be discontinued at such heights as will be determined by the Project Manager. Any section of a subsurface drain constructed from pipes without perforations or slots shall be backfilled with impermeable backfill material as described above.

PSLE 5.9		Filter Drains Which Incorporate Geotextiles

After the completion of the excavations, the bottom portion of the trench shall be compacted and  lined with geotextile sheeting as shown on the Drawings. The top edges of the vertical portions of the geotextile sheeting shall be  anchored outside the excavation, no nails or by any other holes will be allowed to anchor the polyethylene sheets.  An overlap of at least 300 mm shall be provided at each joint and heat bonded.  Geotextile sheeting damaged during the installation or construction shall be replaced at the Contractor's cost.

A layer of permeable material of the class and thickness as shown on the Drawings shall be placed on the geotextile sheeting on the bottom of the trench and shall be lightly tamped and finished to the required gradient to serve as a bedding for the pipes.

Pipes of the type and size required shall then be firmly bedded in the permeable material, true to level and grade, and shall be coupled where required.  Where spigot and- socket pipes are used, the socket ends shall be laid upgrade with the spigot fully entered into the adjacent socket. Where plain butt- -ended pipes are used, they shall be laid firmly together to prevent the infiltration of backfill material.

Perforated and slotted pipes shall be joined by couplers.  Perforated pipes shall be laid with the perforations at the top unless otherwise shown on the Drawings or instructed by the Project Manager, in writing.  The higher end of a subsurface drain  pipe shall be sealed off with a loose concrete cap, and at the  lower end the pipe shall be built into a concrete headwall to  provide a positive outlet, or it shall be connected to stormwater  pipes or culverts, all as shown on the Drawings or as directed by the Project Manager.

All Stormwater or drainage conveyance systems shall be constructed from the lower en working upwards, care shall be taken by the contractor that no material enter the pipes and pipes and filter material will be sealed off during rain or during completion of construction each day. Should the Engineer suspect that material has entered the pipe or that pipes have been damaged due to the Contractors construction methodology, he will instruct the Contractor to perform a camara inspection at his own cost, the contractor will include for a camara inspection in his tender rate.

Solid HDPE or Solid Drilled HDPE pipes will be heat bonded by means of a hot plate machine and will be inspected by a certified HDPE inspector and the Engineer prior to backfilling as stated in PSDB 5.6.1.

Successive layers of permeable material shall be placed after the pipes have been laid.  Permeable material shall be placed in layers not exceeding 300 mm at a time, and shall be lightly compacted. The total thickness of each type of permeable material shall be carefully controlled by means of spacers.

When successive layers are placed, the lower layer shall not be walked on and shall, as far as is possible, not be disturbed. Care shall be taken to prevent the contamination of permeable material during construction of the subsurface drains, and all permeable material contaminated by the soil or silt shall be removed and replaced by the Contractor at his expense.  Care shall also be taken at all stages not to perforate or otherwise damage the geotextile lining.

The remainder of the trench shall be immediately backfilled with approved impermeable material preferably obtained from the excavations, in layers not exceeding 100 mm and compacted to 90% of modified AASHTO density, unless otherwise ordered by the Project Manager.  The trench must be specially protected against the ingress of water, soil and silt until the backfilling with impermeable material has been completed.

Permeable material in subsoil drains shall not be taken to the surface but shall be discontinued at such heights as will be determined by the Project Manager.

After the pipes have been laid and the specified layer of crushed stone filter material has been completed, the protruding vertical sections of the geotextile sheeting shall be folded back across the filter material so that the filter material will be completely enwrapped in the geotextile sheeting. An overlap of at least 300 mm shall be provided between the portions folded back and shall be heat bonded.

PSLE 5.10 		Leachate Drain

Drainage layers shall be constructed in accordance with the details shown on the Drawings.  Firstly a 300mm filter sand layer will be placed on top of the geomembrane section ( The Contractor is advised that Ash can not be placed prior to the dirtywater channel and PCD’s not being completed and approved to retain water by the authorities). Then permeable material of the type specified shall be placed on the filter sand layer to the specified depth.  The Contractor shall take care not to contaminate or damage the filter sand or any geomembrane material in the work area. The permeable material shall be finished to the required level.

The consecutive drainage layers on top of the first drainage layers shall be constructed in such a manner that the permeable material will not be displaced or damaged.

##### PSLE 5.11	Field Quality Control

- Pipe may be rejected for failure to conform to specifications or following:

  - Fractures or cracks passing through pipe wall, except single crack not exceeding 50mm in length at either end of pipe which could be cut off and discarded.  Pipes within one shipment shall be rejected if defects exist in more than 5% of shipment or delivery.

  - HDPE pipes where a scratch or damage is more then 1% of the pipe thickness.

  - Cracks sufficient to impair strength, durability or serviceability of pipe.

  - Defects indicating improper proportioning, mixing, and moulding.

  - Damaged ends, where such damage prevents making satisfactory joint.

  - Acceptance of fittings, stubs or other specifically fabricated pipe sections shall be based on visual inspection at job Site and documentation of conformance to these Specifications.

Notify Project Manager prior to backfilling trench. Contractor is to obtain as-built top of pipe coordinates and elevations.

##### PSLE 5.12	Installation

- Heat fusion of pipe to be single pressure with high fusion jointing pressure in accordance with ISO 21307 and SABS 0268 as specified in the table below:

Table 13: ISO 21307 and SABS 0268

| Parameter | Unit | Value |
| --- | --- | --- |
| Heater plate temperature | ºC | 200 – 230 |
| Initial bead-up fusion jointing pressure | MPa | 0.52 +/- 0.01 |
| Min heat soak time | sec | (11 +/- 1) x en |
| Min bead size after heating | mm | 0.15 en + 1 |
| Heat soak pressure | MPa | 0 to drag pressure |
| Max heater plate removal time | s | 0.1 en + 8 |
| Fusion jointing pressure | MPa | 0.52 +/- 0.01 |
| Min cooling time in the machine under pressure | min | 0.43 en |
| Min cooling time out the machine | min | a |
| a = A cooling time out of the machine and before rough handling may be recommended but in most cases is not necessary with these cooling times |  |  |

- Provide fusion operators certified by the pipe manufacturer.

- Butt fusion equipment for joining procedures shall be capable of meeting conditions recommended by pipe manufacturer including, but not limited to, temperature requirements, alignment, and fusion pressures.

- For cleaning pipe ends, planning unit and heater surfaces, solutions such as detergents and solvents, when required, shall be used in accordance with manufacturer’s recommendations. A clean lint-free cloth is to be used every time.

- Do not bend pipe to greater degree than minimum radius recommended by manufacturer for type and grade.

- Do not subject pipe to strains that will overstress or buckle piping or impose excessive stress on joints.

- Branch saddle fusions shall be joined in accordance with manufacturer’s recommendations and procedures.  Branch saddle fusion equipment shall be of size to facilitate saddle fusion within trench.

- Clamp the components in the butt fusion jointing machine and adjust as necessary to achieve proper alignment.

- Plane the pipe or fitting ends to establish clean, parallel mating surfaces.

- Remove any shavings from the pipe or fittings. Inspect the pipe for incomplete planning, voids or other imperfections and then bring them together to check for proper alignment.

- Measure the gauge pressure required to overcome the frictional drag force of the machine and pipe. This pressure shall be added to the calculated bead-up and fusion jointing pressure.

- Install the heater plate in the machine and bring both pipe ends simultaneously into full contact with the heater plate to produce molten surfaces for fusion jointing.

- At the completion of the heat soak time, pull the pie from the heater plate then remove the heater plate and bring the pipes together in a controlled manner. The joint shall be held at the jointing pressure for the prescribed jointing time.

- The molten joint shall be held immobile under pressure in the machine for the prescribed time.

- Cover at end of each working day open ends of fused pipe.  Cap to prevent entry by animals or debris.

- Use compatible fusion techniques when polyethylenes of different melt indexes are fused together.  Refer to manufacturer’s specifications for compatible fusion.

- Remove shavings inside pipe caused by perforation drilling prior to jointing.

##### PSZA 5.13	Pipe placement

- Pipe placement to be conducted as follows:

- Grade Control equipment shall be of type to accurately maintain design grades and slopes during installation of pipe.

- Dewatering:  Remove standing water in trench before pipe installation.

- Unless otherwise specifically stated, install pipe in accordance with manufacturer’s recommendations.

- Maximum lengths of fused pipe to be handled as one section shall be placed according to manufacturer’s recommendations as to pipe size, pipe SDR, and topography so as not to cause excessive gouging or surface abrasion; but not to exceed 120m.

- Cap pipe sections longer than single joining (usually 12m) on both ends during placement except during fusing operations.

- Notify Project Manager prior to installation pipe into trench and allow time for Project Manager’s inspection, correct irregularities found during inspection.

- Complete tie-ins within trench whenever possible to prevent overstressed connections.

- Allow pipe sufficient time to adjust to trench temperature prior to testing, segment tie-ins or backfilling activity.

- Install reducers adjacent to laterals and tees.

- To reduce branch saddle stress, install saddles at slope equal to and continuous with lateral piping.

- Place in trench by allowing minimum 300mm/30m for thermal contraction and expansion.

Coordinate construction of pipes near access roads with Client to limit impediment of landfill operations or operations of other Contractors.

#### PSLE 7	Testing

##### PSLE 7.1		Preparation

- Commence test procedures when the following conditions have been met.

- Pipe section to be tested is clean and free of dirt, sand or other foreign material.

- Plug pipe outlets with test plugs.  Brace each plug securely to prevent blowouts.  Use concrete if necessary.

- Add water  slowly.

- Pressurizing equipment shall include regulator set to avoid over-pressurizing and damaging an otherwise acceptable section of pipe.

- Provide necessary pipe connections between the section of line being tested and the compressed air supply, together with test pressure equipment, meters, pressure gauge, and other equipment, materials, and facilities necessary to perform the specified tests.

- Furnish and install bulkheads, flanges, valves, bracing, blocking or other temporary sectionalising devices that may be required.

- Remove temporary sectionalising devices after tests have been completed

##### PSLE 7.2		Testing equipment

- Contractor shall provide all equipment required for this testing procedure.

- Testing Equipment shall include, but may not be limited to:

- Polyethylene flange adapter with steel blind flange.

- Temperature gauge (0ºC to 100ºC) tapped and threaded into blind flange.

- Pressure gauge (0 to 1000 mb) ASME Standard B40.1 Grade 2A (accuracy of ±0.5% of full scale) with minor graduation marks no greater than 10 mb.

- Inlet valve to facilitate water hose.

- Ball valve to release pipe pressure at test completion.

- Polyethylene reducers to be used to adapt test flange to size of pipe being tested.

- Compressor shall provide adequate water supply for testing.

- Pressurizing equipment shall include a regulator set to avoid over-pressurizing and damaging otherwise acceptable pipe.

- Provide verification and results of gauge calibration prior to (less than 60 days) and after Project completion.

##### PSLE 7.3		Testing

- Employer and Project Manager shall be given 24-hr notification prior to test.

- Appropriate Safety precautions must be in-place.

- Pipe Test Segments:

- Butt-fusion weld pipe segments.

- Less than 610 meter in length.

- Blind flange with test apparatus on one end and fused cap or blind flange assembly on the opposite end.

- Environment:

- Place test segment in trench or lay test segment on ground surface and allow it to reach ambient temperature before test.

- Perform test during period when pipe segment will be out of direct sunlight to minimize pressure changes as a result of temperature fluctuations.

- Test:

- Testing shall be done inline with SANS 1200L Sub-section 7.3.1:

##### PSLE 7.4		Test report

- Each test shall be reported in writing, on Attachment 1 included with this section.

- Include following information if failure occurs:

- Location of failure segment.

- Nature of leaks.

- Details of repairs performed.

- Retest.

SANS 1200LG: PIPE JACKING

PSLG 5	Construction

PSLG 5.1	General

PSLG 5.1.1        Authority to Jack Pipeline under Facilities Controlled by Third Parties

Add the following:

The Contractor shall be bound by and shall observe the requirements and/or conditions imposed by the service provider in granting any such permission as specified. Although the general supervision and control of the Works falls under the authority of the Employer, the service provider reserves and shall have the right to instruct the Contractor directly in any matter that has a direct bearing on the safety of the service and the protection of the interests of the service provider.

PSLG 5.6            Backfilling and Disposal of Excavated Material

Add the following Sub-Clause:

The thrust and reception pits shall be backfilled with material obtained from the pit excavations.  Hard and rock material shall be incorporated in the backfill only to the extent approved by the Employer’s Agent.  Depending on the quality of the material, the Employer’s Agent may direct that it be mixed with other backfill material.

If, in the opinion of the Employer’s Agent, insufficient or no suitable material is available for this purpose within the freehaul distance, and the shortage of such material has not been caused by the methods used by the Contractor, the Employer’s Agent may instruct the Contractor to import sufficient suitable material.  The Contractor shall so arrange his work that the importance of backfill material is kept to a minimum in respect to both quality and overhaul.

##### PSW: LANDSCAPING AND GRASSING

##### PSW 1		Scope

This section covers the landscaping and/or the establishing of vegetation on all areas on site that will be disturbed by construction works. The aim is to rehabilitate the entire site (more specifically the work areas).

##### PSW 2		Interpretations

PSW 2.1	Supporting Specifications

The following specifications shall, inter alia, form part of the Contract Document:

(a)	SANS 1200A

(b)	SANS 1200D

##### PSW 3 		Materials

PSW 3.1 	Fertilizer

The type of fertilizer to be used shall be as specified or scheduled.

PSW 3.2 	Grass Cuttings

Grass cuttings shall be fresh and in a good condition for planting, with sufficient root material to ensure good growth.  Species to be planted shall be as specified or scheduled.

PSW 3.3 	Grass Seed

Only fresh certified grass seed shall be used and the types of seeds in the seed mixture shall be as specified or as advised by the grassing specialist.

Mixing of various types of grass seeds for obtaining the prescribed grass-seed mixture shall be done on Site in the presence of the Project Manager.  Storing and identifying the grass seeds and the grass-seed mixtures on the Site shall be the responsibility of the Contractor.

Table 14: Application Rates

| GRASS SPECIES | APPLICATION RATE (kg/ha) |
| --- | --- |
| Chloris gayana | 2 |
| Eragrostis curvula | 3 |
| Eragrostis tef | 3 |
| Aragrostis chloromelas | 1 |
| Aragrostis lehmanniana | 1 |
| Enneapogon cenchroides | 2 |
| Aragrostis echonochloidea | 1 |
| Themeda triandra | 1 |
| Digitaria eriantha | 2 |
| Cynodon dactylon | 2 |
| Hypperrhenia hirta | 1 |
| Panicum maximum | 1 |
| TOTAL | 20 |

The Contractor must carry out the following technical functions:

- Appoint specialist sub-contractor to sample the specific soils that will be used and test to determine the soil improvement requirements if any

- Determine the soil improvement requirements

- Verify the suitability of the above seed mixture

PSW 3.4 	Trees, Shrubs and Ground Cover

Plants shall be of the variety and size shown on the Drawings.

When trees, shrubs and ground covers are supplied and delivered to the Site by the Employer, the Contractor shall give the Project Manager at least six weeks advance notice of his requirements.  Upon receipt of the plants, the Contractor shall ensure that the plants are in good condition and free from obvious diseases and shall accept full responsibility to maintain the plants in good condition throughout the Contract.  The plants shall be fully maintained and watered during this period, and any losses of plants due to lack of maintenance or diseases developing during the Contract period shall be replaced at the Contractor's expense.

Plants shall be handled and packed in the approved manner for the particular species or variety, and all necessary precautions shall be taken to ensure that plants will arrive at the point of use in proper condition for successful growth. Trucks used for transporting plants shall be equipped with covers to protect plants from windburn. Containers shall be in a good condition.

Plants supplied by the Contractor shall be healthy, shapely and well rooted. Roots shall not show any evidence of having been restricted or deformed at any time. Plants shall be well grown and free from insect pests and diseases.

PSW 3.5 	Grass Sods

Grass sods shall be of approved quality and shall be harvested, delivered and planted within 36 hours, unless otherwise authorized by the Project Manager. Grass sods shall be free from noxious weeds and diseases and shall contain a minimum of 30 mm of soil.

Sods shall be of the variety of grass specified or scheduled. The grass shall have been grown specifically for sod purposes, mown regularly and maintained to provide an approved quality of uniformity. It shall be harvested by special machines manufactured for this purpose to ensure an even depth of cut with sufficient root material and soil.

PSW 3.6 	Anti-Erosion Compounds

Anti-erosion compounds shall consist of a plastic material in dispersion, such as Verdyol or a similar approved compound, which can be sprayed onto the soil to bind and protect it against erosion.

PSW 3.7 	Topsoil

Topsoil shall consist of fertile loamy soil selected from areas showing a good coverage of natural vegetation, preferably grasses. It shall be free from deleterious matter such as large roots, stones, refuse, stiff or heavy clays and noxious weeds, which would adversely affect its suitability for the planting of grass.

Topsoil shall be obtained wherever suitable material occurs; either from the Site or from borrow areas to be cleared, as described in Sub Clause 5.2.1.2 of SANS 1200D. The Project Manager shall indicate his requirements to the Contractor regarding the quantity of topsoil required and the areas at which it shall be selected and when it shall be removed. Unless otherwise specified or as instructed by the Project Manager, topsoil shall not be taken from more than 400 mm below the original undisturbed surface. If the Contractor fails to conserve topsoil as instructed, he shall obtain suitable substitute material from other sources at no extra cost to the Employer.

Where so specified, the Contractor shall procure and supply topsoil from his own sources outside the Site. Such sources shall be subject to the approval of the Project Manager.

Topsoil shall be stockpiled in separate loose heaps as tipped from the trucks and shall not be stockpiled higher than 3,0 m.

PSW 3.8 	Manure

Manure shall, unless another type is approved by the Project Manager, be pure "kraal" manure, free from soil, weed seed or other objectionable material. It shall not contain any particles that will not pass through a 50 mm screen. Only manure which has been approved by the Project Manager shall be delivered to the Site.

PSW 3.9 	Compost

Compost shall be well decayed, friable and free from weed seed, dust and other objectionable materials.

PSW 4		Plant

Not applicable to this Section.

PSW 5		Construction

PSW 5.1	Landscaping of areas

PSW 5.1.1	Shaping

Areas that require shaping which involves bulk earthworks, such as contoured areas, shall be excavated, filled, compacted when required, and shaped to the correct contours to within a tolerance of plus or minus 150 mm. Such work shall be considered as earthworks and measurement and payment shall be made under SANS 1200D, except that quantities may be measured by means of a grid of levels taken at 10 m intervals before and after shaping, or by means of levelled cross sections.

PSW 5.1.2 	Trimming

Trimming shall consist of bringing the existing or previously shaped ground to an even surface with the final levels generally following the original surface. Trimming shall normally be done by grader, or, in more confined or steep areas, by bulldozer.  Where machine operations are not practicable because of confined spaces or steep slopes, trimming shall be done using hand tools.

All trimming alongside roads and streets shall be completed before landscaping commences. Such trimming shall be carried out on both sides of the road or street up to the boundaries of the road reserve unless otherwise specified or instructed by the Project Manager. Where applicable, trimmed surfaces shall be left slightly rough to facilitate binding with topsoil or the natural establishing of vegetation.

When subsequent grassing is required or when instructed by the Project Manager, areas previously shaped shall be trimmed as described above to within a tolerance of plus or minus 25 mm, with all undulations following a smooth curve.

The above tolerance shall apply only to areas where the final contours are given in the Drawings. During trimming, all stones in excess of 50 mm in size and all excess material shall be removed. The trimming of any areas requiring grass shall be done in such a way that, after cultivation and application of any topsoil, the finished surface of the area shall be approximately 25 mm below the top of adjacent kerbing, channelling or pavement.

PSW 5.1.3 	Plant rates

The Project Manager shall be entitled to pay for shaping and trimming as described above on the basis of the hourly rates for motor graders and bulldozers. The motor grader and bulldozer to be provided shall each have a fly wheel power of not less than 93 kW.

PSW 5.2	Preparation of areas for Grassing

The various areas to be grassed shall be prepared as follows:

PSW 5.2.1 	Areas not requiring topsoil

Where the areas to be grassed consist of organically suitable material, they shall be scarified to a minimum depth of 150 mm.  All loose stones larger than 30 mm on areas to be mowed by machine shall be removed.

PSW 5.2.2 	Areas requiring topsoil

Where areas to be grassed consist of organically unsuitable material, the surface shall be roughened to ensure a proper bonding between the topsoil and the subsoil. If required, the area shall be scarified as described in Sub Clause PA 5.2.1 above.

Topsoil shall be placed on the prepared surfaces and trimmed to the uniform thickness required. The topsoil shall be prepared by means of hand rakes or light rotavators to obtain a smooth surface. All stones shall be removed as specified for areas not requiring topsoil in Sub Clause PA 5.2.1 above.

PSW 5.2.3 	Fertilizing

The Contractor shall have the top 150 mm of the prepared surfaces tested to determine the amount and type of fertilizer required for establishing proper growing conditions for the grass. The fertilizer shall be evenly applied over all surfaces where grass is to be planted and shall then be thoroughly mixed with the soil, either mechanically or manually, to a depth of 150 mm.  Where hydroseeding is to be performed, the fertilizer may be mixed with the cellulose pulp and water used in hydroseeding.

PSW 5.3	Grassing

The method of establishing grass shall depend on the circumstances relating to each case. The method to be used in each case shall be agreed on by the Project Manager and the Contractor.

PSW 5.3.1 	Planting of grass cuttings

The areas to be planted shall, unless they are wet, be thoroughly watered before planting to ensure that the soil will be uniformly wet over a depth of at least 150 mm during planting.

The Contractor shall plant an approved variety of grass cuttings, using his own method, in such a way as to obtain a sufficient number of live and actively growing plants per square metre to provide an acceptable cover as defined in Sub Clause PA 5.4.2 of this section. At least 70 grain bags of cuttings shall be planted per hectare. Only fresh cuttings shall be used. Grass cuttings that have been allowed to dry out shall not be used.  Immediately after planting the grass cuttings shall be given a copious watering and when sufficiently dry shall be rolled with a light agricultural roller.

PSW 5.3.2 	Sodding

Areas to be grassed by sodding shall be given a layer of topsoil at least 75 mm thick unless the Project Manager instructs that the topsoil be omitted where suitable subsoil is present. The areas to be sodded shall be thoroughly watered beforehand so that they will be wet to a depth of at least 150 mm after sodding. The surface shall be slightly roughened to ensure a good penetration of roots into the soil. Sods shall be protected against drying out and shall be kept moist from the time of harvesting until finally placed.

Wherever possible, the first row of sods shall be laid in a straight line and, if on a slope, laying shall be started at the bottom of the slope. The sods shall be butted tightly against each other and care shall be taken not to stretch or overlap the sods. Where a good fit cannot be obtained, the intervening space shall be filled with topsoil.

The next row shall similarly be placed tightly against the bottom row with the joints staggered, and so on, until the entire area is covered with sods. On the instructions of the Project Manager, sods shall be held in position on steep slopes by a sufficient number of robust wooden stokes approximately 300 mm in length by 20 mm in diameter. Each section of completed sodding shall be lightly rolled and thoroughly watered.

PSW 5.3.3 	Hydro-seeding

The types and mixtures of seeds to be used shall be as specified or scheduled if not so specified and shall be agreed on by the Project Manager and the Contractor before any seed is ordered for use by the Contractor. The Contractor shall be solely responsible for establishing an acceptable grass cover, and any approval by the Project Manager of seed or seed mixtures proposed for use shall not relieve him of this responsibility.

Cellulose pulp shall be added to the hydro-seeding mix at a rate of 25 kg of pulp per kilo-litre of water used, except where otherwise instructed for flat slopes.

Hydro-seeding shall then be carried out with the use of an approved hydro-seeding machine at a rate of application of not less than 38 kg of seed mixture per hectare, unless otherwise specified in the Project Specifications.

When the use of an anti-erosion compound such as Verdyol is required and the compound is to be applied simultaneously with the hydro-seeding, it shall be mixed with the hydro-seeding mixture before application. In this case the amount of cellulose pulp shall be decreased by one third to a half, depending on the amount of compound added.

PSW 5.3.4 	Grassing of borrow pits, temporary bypasses, camp Sites, access roads and stockpile Sites

Prior to any grassing that may be required on borrow areas, the finishing off of borrow pits as described in Sub Clause 5.2.2.2 of SANS 1200D, the obliteration of bypasses and access roads as described in clause 5.8 of SANS 1200A and the clearing of camp Sites as described in SANS 1200A shall have been carried out as specified in the relevant sections.

PSW 5.4	Establishing and Maintenance of grass

PSW 5.4.1 	Watering, weeding, cutting and replanting

All sodded and planted areas shall be adequately watered at frequent and regular intervals in order to ensure proper seed germination and the growth of grass until the grass has established to an acceptable cover and thereafter until the beginning of the maintenance period of the grass. The amount and frequency of watering shall be subject to the Project Manager's approval. Where hydro-seeding is carried out, the commencement of watering may be postponed until a favourable time of the year, but watering shall in any case commence and continue as soon as the seeds have germinated and growth begins.

The Contractor shall mow the grass on all areas that have been grassed, whenever so instructed by the Project Manager, until the end of the contract period. All grass cuttings shall be collected and disposed of if so directed by the Project Manager. Weeds shall be controlled by means of pulling or cutting or by any other approved means. Any bare patches where the grass has not taken, or where it has been damaged or has dried out shall be re-cultivated, planted, sodded or hydro-seeded at the Contractor's expense.

PSW 5.4.2 	Acceptable cover

An acceptable grass cover shall mean that not less than 75% of the area planted or hydro-seeded shall be covered with grass and that there shall be no bare patches the maximum dimension of which shall not exceed 500 mm. In the case of sodding, acceptable cover shall mean that the full area shall be covered with live grass at the end of any period of not less than three months after sodding.

PSW 5.5	Trees, Shrubs And Ground Covers

PSW 5.5.1	Positions of plants

The positions in which trees, shrubs and ground covers are to be planted shall be as indicated on the Drawings or as determined by the Project Manager, and care shall be taken that the taller plants will not obscure traffic signs.

PSW 5.5.2 	Preparation of plant holes

Unless otherwise directed by the Project Manager, holes for trees and shrubs shall be placed and prepared as follows:

- All holes shall be square in plan.

- For shrubs the holes shall be at least 500 mm square by   600 mm deep.

- For trees the holes shall be at least 600 mm square by   700 mm deep.

- The planting holes shall be refilled with selected and approved topsoil, thoroughly mixed with manure or compost (one heaped spadeful added to every plant hole) and, depending on soil test reports, the required amount and type of fertilizer.

- The holes shall be thoroughly watered before planting.  Where the local soil has poor drainage, 150 mm of broken rock shall be placed at the bottom of the planting hole before filling it with soil.

PSW 5.5.3 	Planting

Before planting the plants shall be well watered before they are removed from their containers.

Ground cover plants shall be carefully lifted from their containers and transferred to holes in the prepared soil, which holes shall be just large enough to accommodate the plant and the adhering soil. Care shall be taken to avoid exposure of the roots during planting. Soil for ground covers shall be prepared as for grassing as specified in clause PA 5.2.

Directly after the planting, plants shall be well watered to establish them firmly in the soil. After the soil has set, additional soil shall, in the case of trees and shrubs, be added where necessary to bring the backfill material to within 150 mm of the ground surface to ensure the retention of sufficient water. All trees shall be tied to a suitable creosote treated timber stoke planted firmly in the ground. The stoke shall have a minimum diameter of 35 mm and shall be at least 300 mm longer than the planted tree, with a maximum length of 3 m above the ground.  After planting the ground surface around the plants shall be covered with straw or grass or any other type of mulch to minimize evaporation.

PSW 5.6	General

PSW 5.6.1 	Time of planting

The planting of grass, trees, shrubs and ground covers shall be carried out as far as is practicable during periods most likely to produce beneficial results. The Contractor shall make every effort to programme his operations to make this possible.

PSW 5.6.2 	Traffic on grassed areas

The Contractor shall not plant grass until all operations that may require construction equipment to be taken over the grassed areas have been completed. No equipment, trucks or water carts shall be allowed on areas that have been grassed and only equipment required for the preparation of areas, the application of fertilizer and the spreading of topsoil will be allowed to operate on areas ready for grassing.

PSW 5.6.3 	Erosion control

During construction, the Contractor shall protect all areas susceptible to erosion by installing all necessary temporary and permanent drainage works as soon as possible and by taking such other measures as may be necessary to prevent the concentration of surface water and the scouring of slopes, banks and other areas.

Runnels or erosion channels developing during the construction period or during the maintenance period shall be backfilled and consolidated and the affected areas shall be restored to their former proper condition. The Contractor shall not allow large scale erosion to develop before effecting repairs and all erosion damage shall be repaired as soon as possible and in any case not later than three months before the end of the maintenance period. Topsoil washed away shall be replaced.

PSW 5.6.4 	Proprietary brand materials used for erosion control

Proprietary brands of materials that may be required for erosion protection to enable natural grass to become established shall be to the approval of the Project Manager.

PSW 5.6.5 	Responsibility for establishing an acceptable cover

Notwithstanding the fact that the method of grassing and the type of seed or grass used and the rate of seed application may be specified or agreed to by the Project Manager, and that the frequency of mowing will be as instructed by him, the Contractor shall be solely responsible for establishing an acceptable grass cover and for the cost of replanting or re-hydro-seeding where an acceptable cover has not been obtained. Where, however, in the opinion of the Contractor, it is doubtful from the outset whether an acceptable cover can be established, he may inform the Project Manager of his reasons for this, and the Project Manager shall, if he agrees, either adopt another grassing method or agree to accept whatever cover can be obtained, provided that all reasonable efforts are made to establish a good cover by the method proposed. Such agreement shall only be valid if given in writing by the Project Manager.

PSW 6		Tolerances

Not applicable to this Section.

PSW 7		Testing

Soil Testing:

    - Assess soil pH, nutrient content, and drainage capacity to inform soil improvement measures.

Topsoil Quality Assessment:

    - Test for contaminants, organic matter content, and structure to ensure suitability for planting.

Seed Germination Test:

    - Evaluate the viability of grass seeds before application.

    - Moisture Content Testing

    - Regularly check soil moisture levels to ensure adequate watering practices are being followed.

Erosion Assessment

    - Monitor erosion-prone areas for signs of soil loss and implement corrective measures as necessary..

PSW 8		Payment

Payments for the rehabilitation works will be made according to the Activity Schedule, which outlines the specific tasks to be completed and their corresponding rates. The Contractor is required to plan and execute the works in accordance with this schedule to ensure timely and accurate compensation for services rendered.

# List of Drawings

## Drawings Issued by the Employer

The following list of drawings is issued by the Employer at or before the Contract Date and which apply to this contract.

Note:  Some drawings may contain both Works Information and Site Information.

### Civil and Structural

| ESKOM DWG NO | ESKOM DWG SHEET NO | DESCRIPTION |
| --- | --- | --- |
| SECTION 01 - (GA) GENERAL ARRANGEMENT |  |  |  |
| 0.61/96346 | 0 | DRAWING LIST |  |
| 0.61/96346 | 1 | LAYOUT OF EXISTING SERVICES |  |
| 0.61/96346 | 2 | LAYOUT OF EXISTING SERVICES TO BE REMOVED |  |
| 0.61/96346 | 3 | GENERAL ARRANGEMENT |  |
| SECTION 02 - (SS) SITE SERVICES |  |  |  |
| 0.61/96768 | 1 | CLEAN WATER CHANNEL No. 1 - LONGITUDINAL SECTION (1 OF 4) |  |
| 0.61/96768 | 2 | CLEAN WATER CHANNEL No. 1 - LONGITUDINAL SECTION (2 OF 4) |  |
| 0.61/96768 | 3 | CLEAN WATER CHANNEL No. 1 - LONGITUDINAL SECTION (3 OF 4) |  |
| 0.61/96768 | 4 | CLEAN WATER CHANNEL No. 1 - LONGITUDINAL SECTION (4 OF 4) |  |
| 0.61/96768 | 5 | CLEAN WATER CHANNEL No. 1 - CROSS SECTIONS (1 OF 3) |  |
| 0.61/96768 | 6 | CLEAN WATER CHANNEL No. 1 - CROSS SECTIONS (2 OF 3) |  |
| 0.61/96768 | 7 | CLEAN WATER CHANNEL No. 1 - CROSS SECTIONS (3 OF 3) |  |
| 0.61/96768 | 8 | CLEAN WATER CHANNEL No. 2 - LONGITUDINAL SECTION |  |
| 0.61/96768 | 9 | CLEAN WATER CHANNEL No. 2 - CROSS SECTIONS |  |
| 0.61/96768 | 10 | CLEAN WATER CHANNEL No. 3 - LONGITUDINAL SECTION (1 OF 3) |  |
| 0.61/96768 | 11 | CLEAN WATER CHANNEL No. 3 - LONGITUDINAL SECTION (2 OF 3) |  |
| 0.61/96768 | 12 | CLEAN WATER CHANNEL No. 3 - LONGITUDINAL SECTION (3 OF 3) |  |
| 0.61/96768 | 13 | CLEAN WATER CHANNEL No. 3 - CROSS SECTIONS (1 OF 2) |  |
| 0.61/96768 | 14 | CLEAN WATER CHANNEL No. 3 - CROSS SECTIONS (2 OF 2) |  |
| 0.61/96769 | 1 | DIRTY WATER CHANNEL No. 1 - LONGITUDINAL SECTION (1 OF 5) |  |
| 0.61/96769 | 2 | DIRTY WATER CHANNEL No. 1 - LONGITUDINAL SECTION (2 OF 5) |  |
| 0.61/96769 | 3 | DIRTY WATER CHANNEL No. 1 - LONGITUDINAL SECTION (3 OF 5) |  |
| 0.61/96769 | 4 | DIRTY WATER CHANNEL No. 1 - LONGITUDINAL SECTION (4 OF 5) |  |
| 0.61/96769 | 5 | DIRTY WATER CHANNEL No. 1 - LONGITUDINAL SECTION (5 OF 5) |  |
| 0.61/96769 | 6 | DIRTY WATER CHANNEL No. 1 - CROSS SECTIONS (1 OF 4) |  |
| 0.61/96769 | 7 | DIRTY WATER CHANNEL No. 1 - CROSS SECTIONS (2 OF 4) |  |
| 0.61/96769 | 8 | DIRTY WATER CHANNEL No. 1 - CROSS SECTIONS (3 OF 4) |  |
| 0.61/96769 | 9 | DIRTY WATER CHANNEL No. 1 - CROSS SECTIONS (4 OF 4) |  |
| 0.61/96769 | 10 | DIRTY WATER CHANNEL No. 2 - LONGITUDINAL SECTION (1 OF 3) |  |
| 0.61/96769 | 11 | DIRTY WATER CHANNEL No. 2 - LONGITUDINAL SECTION (2 OF 3) |  |
| 0.61/96769 | 12 | DIRTY WATER CHANNEL No. 2 - LONGITUDINAL SECTION (3 OF 3) |  |
| 0.61/96769 | 13 | DIRTY WATER CHANNEL No. 2 - CROSS SECTIONS (1 OF 2) |  |
| 0.61/96769 | 14 | DIRTY WATER CHANNEL No. 2 - CROSS SECTIONS (2 OF 2) |  |
| 0.61/96769 | 15 | DIRTY WATER CHANNEL No. 3 - LONGITUDINAL SECTION (1 OF 3) |  |
| 0.61/96769 | 16 | DIRTY WATER CHANNEL No. 3 - LONGITUDINAL SECTION (2 OF 3) |  |
| 0.61/96769 | 17 | DIRTY WATER CHANNEL No. 3 - LONGITUDINAL SECTION (3 OF 3) |  |
| 0.61/96769 | 18 | DIRTY WATER CHANNEL No. 3 - CROSS SECTIONS (1 OF 2) |  |
| 0.61/96769 | 19 | DIRTY WATER CHANNEL No. 3 - CROSS SECTIONS (2 OF 2) |  |
| 0.61/96769 | 20 | DIRTY WATER CHANNEL No. 4 - LONGITUDINAL SECTION |  |
| 0.61/96769 | 21 | DIRTY WATER CHANNEL No. 4 - CROSS SECTIONS |  |
| 0.61/96769 | 22 | DIRTY WATER CHANNEL No. 5 - LONGITUDINAL SECTION |  |
| 0.61/96769 | 23 | DIRTY WATER CHANNEL No. 5 - CROSS SECTIONS |  |
| 0.61/96769 | 24 | DAM BY-PASS CHANNEL No. 1 - LONGITUDINAL SECTION |  |
| 0.61/96769 | 25 | DAM BY-PASS CHANNEL No. 1 - CROSS SECTIONS |  |
| 0.61/96770 | 1 | REHAB WATER CHANNEL No. 1 - LONGITUDINAL SECTION (1 OF 8) |  |
| 0.61/96770 | 2 | REHAB WATER CHANNEL No. 1 - LONGITUDINAL SECTION (2 OF 8) |  |
| 0.61/96770 | 3 | REHAB WATER CHANNEL No. 1 - LONGITUDINAL SECTION (3 OF 8) |  |
| 0.61/96770 | 4 | REHAB WATER CHANNEL No. 1 - LONGITUDINAL SECTION (4 OF 8) |  |
| 0.61/96770 | 5 | REHAB WATER CHANNEL No. 1 - LONGITUDINAL SECTION (5 OF 8) |  |
| 0.61/96770 | 6 | REHAB WATER CHANNEL No. 1 - LONGITUDINAL SECTION (6 OF 8) |  |
| 0.61/96770 | 7 | REHAB WATER CHANNEL No. 1 - LONGITUDINAL SECTION (7 OF 8) |  |
| 0.61/96770 | 8 | REHAB WATER CHANNEL No. 1 - LONGITUDINAL SECTION (8 OF 8) |  |
| 0.61/96770 | 9 | REHAB WATER CHANNEL No. 1 - CROSS SECTIONS (1 OF 6) |  |
| 0.61/96770 | 10 | REHAB WATER CHANNEL No. 1 - CROSS SECTIONS (2 OF 6) |  |
| 0.61/96770 | 11 | REHAB WATER CHANNEL No. 1 - CROSS SECTIONS (3 OF 6) |  |
| 0.61/96770 | 12 | REHAB WATER CHANNEL No. 1 - CROSS SECTIONS (4 OF 6) |  |
| 0.61/96770 | 13 | REHAB WATER CHANNEL No. 1 - CROSS SECTIONS (5 OF 6) |  |
| 0.61/96770 | 14 | REHAB WATER CHANNEL No. 1 - CROSS SECTIONS (6 Of 6) |  |
| 0.61/96770 | 15 | REHAB WATER CHANNEL No. 2 - LONGITUDINAL SECTION (1 OF 2) |  |
| 0.61/96770 | 16 | REHAB WATER CHANNEL No. 2 - LONGITUDINAL SECTION (2 OF 2) |  |
| 0.61/96770 | 17 | REHAB WATER CHANNEL No. 2 - CROSS SECTIONS |  |
| 0.61/96771 | 1 | ACCESS ROAD No. 1 - LONGITUDINAL SECTION (1 OF 3) |  |
| 0.61/96771 | 2 | ACCESS ROAD No. 1 - LONGITUDINAL SECTION (2 OF 3) |  |
| 0.61/96771 | 3 | ACCESS ROAD No. 1 - LONGITUDINAL SECTION (3 OF 3) |  |
| 0.61/96771 | 4 | ACCESS ROAD No. 1 - CROSS SECTIONS (1 OF 3) |  |
| 0.61/96771 | 5 | ACCESS ROAD No. 1 - CROSS SECTIONS (2 OF 3) |  |
| 0.61/96771 | 6 | ACCESS ROAD No. 1 - CROSS SECTIONS (3 OF 3) |  |
| 0.61/96771 | 7 | ACCESS ROAD No. 2 |  |
| 0.61/96771 | 8 | ACCESS ROAD No. 2 |  |
| 0.61/96771 | 9 | ACCESS ROAD No. 4 - LONGITUDINAL SECTION (1 OF 2) |  |
| 0.61/96771 | 10 | ACCESS ROAD No. 4 - LONGITUDINAL SECTION (2 OF 2) |  |
| 0.61/96771 | 11 | ACCESS ROAD No. 4 - CROSS SECTIONS |  |
| 0.61/96772 | 1 | TYPICAL DETAILS |  |
| 0.61/96772 | 2 | TYPICAL DETAILS |  |
| 0.61/96772 | 3 | FENCING LAYOUT |  |
| 0.61/96772 | 4 | FENCING DETAILS |  |
| 0.61/96772 | 5 | TYPICAL ENERGY DISSIPATION OUTLET STRUCTURE |  |
| 0.61/96772 | 6 | TRAFFIC LAYOUT |  |
| 0.61/96773 | 1 | CULVERT No. 1 - LAYOUT, SECTIONS & DETAILS (SHEET 1 OF 2) |  |
| 0.61/96773 | 2 | CULVERT No. 1 - LAYOUT, SECTIONS & DETAILS (SHEET 2 OF 2) |  |
| 0.61/96773 | 3 | CULVERT No. 2 - LAYOUT, SECTIONS & DETAILS |  |
| 0.61/96773 | 4 | CULVERT No. 3 - LAYOUT, SECTIONS & DETAILS |  |
| 0.61/96773 | 5 | CONCRETE PIPE No. 4 - LAYOUT, SECTIONS & DETAILS |  |
| 0.61/96773 | 6 | CULVERT No. 5 & 6 - LAYOUT, SECTIONS & DETAILS (SHEET 1 OF 2) |  |
| 0.61/96773 | 7 | CULVERT No. 5 & 6 - LAYOUT, SECTIONS & DETAILS (SHEET 2 OF 2) |  |
| 0.61/96773 | 8 | CULVERT No. 7 - LAYOUT, SECTIONS & DETAILS |  |
| 0.61/96773 | 9 | CULVERT No. 8 - LAYOUT, SECTIONS & DETAILS (SHEET 1 OF 2) |  |
| 0.61/96773 | 10 | CULVERT No. 8 - LAYOUT, SECTIONS & DETAILS (SHEET 2 OF 2) |  |
| 0.61/96773 | 11 | CULVERT No. 9 - LAYOUT, SECTIONS & DETAILS |  |
| 0.61/96773 | 12 | CONCRETE PIPE No. 10 - LAYOUT, SECTIONS & DETAILS |  |
| 0.61/96773 | 13 | CULVERT No. 11 - LAYOUT, SECTIONS & DETAILS |  |
| 0.61/96774 | 1 | EASTERN STORMWATER DRAINAGE DETAILS SHEET 1 OF 1 |  |
| Section 03 - Dams |  |  |  |
| 0.61/96781 | 1 | DAMS GENERAL ARRANGEMENT |  |
| 0.61/96781 | 2 | STORMWATER MANAGEMENT LAYOUT |  |
| 0.61/96781 | 3 | SETTING OUT |  |
| 0.61/96781 | 4 | SUB SOIL DRAINAGE LAYOUT |  |
| 0.61/96781 | 5 | SUB SOIL DRAINAGE - DATA TABLES |  |
| 0.61/96781 | 6 | GROUND PROFILES |  |
| 0.61/96781 | 7 | DAM CONCRETE LINING LAYOUT |  |
| 0.61/96781 | 8 | DAM FENCING LAYOUT |  |
| 0.61/96782 | 1 | TYPICAL DETAILS - EMBANKMENT & LINER DETAILS (DWG) |  |
| 0.61/96782 | 2 | TYPICAL DETAILS - SUB-SOIL DETAILS (DWG) |  |
| 0.61/96782 | 3 | TYPICAL DETAILS - GUARD & SAFETY EQUIPMENT DETAILS (DWG) |  |
| 0.61/96782 | 4 | TYPICAL DETAILS - HANDRAIL GATE DETAILS |  |
| 0.61/96782 | 5 | TYPICAL DETAILS - PCD & RRD OUTLET STRUCTURES SHEET 2 |  |
| 0.61/96782 | 6 | TYPICAL DETAILS - HANDRAIL DETAILS |  |
| 0.61/96783 | 1 | PCD - SPILLWAY |  |
| 0.61/96783 | 2 | RRD - SPILLWAY |  |
| 0.61/96784 | 1 | PCD - SILT TRAP CONCRETE DETAILS (1 OF 5) |  |
| 0.61/96784 | 2 | PCD - SILT TRAP CONCRETE DETAILS (2 OF 5) |  |
| 0.61/96784 | 3 | PCD - SILT TRAP CONCRETE DETAILS (3 OF 5) |  |
| 0.61/96784 | 4 | PCD - SILT TRAP CONCRETE DETAILS (4 OF 5) |  |
| 0.61/96784 | 5 | PCD - SILT TRAP CONCRETE DETAILS (5 OF 5) |  |
| 0.61/96784 | 6 | RRD - SILT TRAP CONCRETE DETAILS (1 OF 5) |  |
| 0.61/96784 | 7 | RRD - SILT TRAP CONCRETE DETAILS (2 OF 5) |  |
| 0.61/96784 | 8 | RRD - SILT TRAP CONCRETE DETAILS (3 OF 5) |  |
| 0.61/96784 | 9 | RRD - SILT TRAP CONCRETE DETAILS (4 OF 5) |  |
| 0.61/96784 | 10 | RRD - SILT TRAP CONCRETE DETAILS (5 OF 5) |  |
| 0.61/96785 | 1 | PCD - DIVISION WALL DETAILS |  |
| 0.61/96786 | 1 | PCD - INLET STRUCTURES |  |
| 0.61/96786 | 2 | RRD - INLET STRUCTURES |  |
| 0.61/96787 | 1 | PCD OUTLET STRUCTURE - BUILDING ELEVATIONS |  |
| 0.61/96787 | 2 | PCD OUTLET STRUCTURE - LAYOUT, SECTIONS AND DETAILS |  |
| 0.61/96787 | 3 | PCD OUTLET STRUCTURE - 3D VIEWS & SECTIONS |  |
| 0.61/96787 | 4 | RRD OUTLET STRUCTURE - BUILDING SECTIONS |  |
| 0.61/96787 | 5 | RRD OUTLET STRUCTURE - BUILDING ROOF AND ELEVATIONS |  |
| 0.61/96787 | 6 | RRD OUTLET STRUCTURE - LAYOUT, SECTIONS AND DETAILS |  |
| 0.61/96787 | 7 | RRD OUTLET STRUCTURE - 3D VIEWS AND SECTIONS |  |
| 0.61/96788 | 1 | ACCESS RAMP 1 |  |
| 0.61/96788 | 2 | ACCESS RAMP 2 |  |
| 0.61/96788 | 3 | ACCESS RAMP 3 |  |
| 0.61/96788 | 1 | ACCESS RAMP 1 |  |
| Section 04 – Eastern Services (Take Out Option) |  |  |  |
| 0.61/96346 | 3 ES | GENERAL ARRANGEMENT (INCLUDING EASTERN SERVICES) |  |
| 0.61/96769 | 17 ES | DIRTY WATER CHANNEL No. (6) - LONGITUDINAL SECTION (1 OF 2) |  |
| 0.61/96769 | 18 ES | DIRTY WATER CHANNEL No. (6) - LONGITUDINAL SECTION (2 OF 2) |  |
| 0.61/96769 | 22 ES | DIRTY WATER CHANNEL No. (6) - CROSS SECTIONS |  |
| 0.61/96771 | 19 ES | ACCESS ROAD No. 5 - LONGITUDINAL SECTION (1 OF 3) |  |
| 0.61/96771 | 20 ES | ACCESS ROAD No. 5 - LONGITUDINAL SECTION (2 OF 3) |  |
| 0.61/96771 | 21 ES | ACCESS ROAD No. 5 - LONGITUDINAL SECTION (3 OF 3) |  |
| 0.61/96771 | 25 ES | ACCESS ROAD No. 5 - CROSS SECTIONS (1 OF 3) |  |
| 0.61/96771 | 26 ES | ACCESS ROAD No. 5 - CROSS SECTIONS (2 OF 3) |  |
| 0.61/96771 | 27 ES | ACCESS ROAD No. 5 - CROSS SECTIONS (3 OF 3) |  |
| 0.61/96772 | 2 ES | TYPICAL DETAILS |  |
| 0.61/96773 | 12 ES | CULVERT No. 13 - LAYOUT, SECTIONS & DETAILS |  |
| 0.61/96773 | 13 ES | CULVERT No. 14 - LAYOUT, SECTIONS & DETAILS |  |

## Documents Issued by the Employer

The following list of document is issued by the Employer at or before the Contract Date and which apply to this contract.

| Doc Number | Revision | Title |
| --- | --- | --- |
| TECHNICAL |  |  |
| 36-946 |  | Works Instructions for Electrical Drawings |
| 36-945 |  | Works Instructions for P&ID |
| 36-681 |  | Generation Plant Safety Regulations. |
| 32-846 |  | Operating Regulations for High-Voltage Systems. |
| 240-49230046 |  | Eskom FMEA Guideline |
| 240-49230111 |  | Eskom HAZOP Guideline |
| 240-53113685 | 2 | Design Review Procedure |
| 240-53114026 | 2 | Project Engineering Change Management Procedure |
| 240-62937990 | 1 | Tutuka AKZ Plant Labelling Guideline |
| 240-85416341 |  | Commissioning and Completion of Power Station Projects |
| 240-86973501 | 1 | Engineering Drawing Standard - Common Requirements |
| DOCUMENT CONTROL |  |  |
| 240-65459834 |  | Gx Projects Documentation Deliverable Requirements Specification |
| 240-66920003 | 1 | Documentation Management Review and Handover Procedure |
| 240-76992014 |  | Technical Document and Record Management Work Instruction |
| 240-83561037 |  | Reporting Data Requirements Specification for Contractors |
| 32-6 | 1 | Eskom Document and Record Management Procedure |
| SAFETY HEALTH AND ENVIRONMENT |  |  |
| 14RISKENV |  | Tutuka Waste Management Procedure |
| 32-726 |  | Contract and Contractor OHS Management |
| 240-77471499 |  | Annexure B: Acknowledgement Form for Eskom OHS legal and other requirements |
| 240-77471651 |  | Annexure C: OHS Tender Evaluation Template (High risk) |
|  |  | Tutuka ADF Civil Occupational Health and Safety Baseline Risk Assessment |
| ESK-TUT-230-40 | 0 | Tutuka Power Station Ash Disposal Facility Volume Increase Civil Works Project (OHS specification) |
| 559-452571793 | 0 | Environmental Specification for Ash Dump Main Civil and Earthworks Project at Tutuka Power Station |
| GEM23_DOC072 |  | Generation Ash Disposal Facility Rehabilitation |
| DEA/EIA/0001416/2012 |  | Final Environmental Management Programme, For The Proposed Continuous Disposal of Ash at Tutuka Power Station, Mpumalanga Province |
| 08/C11K/ABCFDI/1016 |  | Tutuka Power station Integrated Water Use Licence |
| QUALITY |  |  |
| 240-105658000 |  | Employer’s Supplier Contract Quality Requirements Specification (QM58) |
| 240-126469599 | 6 | Method Statement Template |
| 240-109253302 |  | ITP Template |
| 240-68099512 | 9 | Form A 2020 Cat-1 |
| 240-109253698 | 3 | CQP Template |
| 240-12248652 | 6 | Category 2 – List of Tender Returnables Documents |