ESKOM HOLDINGS SOC Ltd
                                                                                                                        CONTRACT NO:

EMERGENCY PREPAREDNESS PUBLIC ADDRESS SYSTEM at MEDUPI POWER STATION


	[image: image2.jpg]R Eskom






NEC3 Engineering & Construction Contract
	Between


	ESKOM HOLDINGS SOC Ltd 

(Reg No. 2002/015527/30) 

	and


	[Insert at award stage]
(Reg No. ____________)

	for


	Design, Supply, Install, Testing and Commissioning, Storage, and optimisation of the Emergency Preparedness Public Address System. Insert title of the works

	
	

	Contents:


	
	No of pages

	Part C1
	Agreements & Contract Data
	[●]

	Part C2
	Pricing Data
	[●]

	Part C3
	Scope of Work
	[●]

	Part C4
	Site Information
	[●]

	
	
	

	CONTRACT No.
	[Insert at award stage]

	
	

	
	

	
	


Part C1: Agreements & Contract Data
	Contents:


	
	No of pages

	C1.1
	Form of Offer and Acceptance 

[to be inserted from Returnable Documents at award stage]
	[●]

	C1.2a
	Contract Data provided by the Employer
	[●]

	C1.2b
	Contract Data provided by the Contractor.
[to be inserted from Returnable Documents at award stage]
	[●]

	C1.3
	Proforma Guarantees
	[●]


C1.1 Form of Offer & Acceptance

Offer

The Employer, identified in the Acceptance signature block, has solicited offers to enter into a contract for the procurement of:

Design, Supply, Install, Testing and Commissioning, Storage, and optimisation of the Emergency Preparedness Public Address System.
The tenderer, identified in the Offer signature block, has examined the documents listed in the Tender Data and addenda thereto and by submitting this Offer has accepted the Conditions of Tender.

By the representative of the tenderer, deemed to be duly authorised, signing this part of this Form of Offer and Acceptance the tenderer offers to perform all of the obligations and liabilities of the Contractor under the contract including compliance with all its terms and conditions according to their true intent and meaning for an amount to be determined in accordance with the conditions of contract identified in the Contract Data. 

Delete the Options which do not apply

	Options A 
	The offered total of the Prices exclusive of VAT is 
	R [●]

	
	Value Added Tax @ 15% is
	R [●]

	
	The offered total of the amount due inclusive of VAT is

	R [●]

	
	(In words) [●]


This Offer may be accepted by the Employer by signing the Acceptance part of this Form of Offer and Acceptance and returning one copy of this document including the Schedule of Deviations (if any) to the tenderer before the end of the period of validity stated in the Tender Data, or other period as agreed, whereupon the tenderer becomes the party named as the Contractor in the conditions of contract identified in the Contract Data. 
	Signature(s)


	
	
	

	Name(s)


	
	
	

	Capacity


	
	
	

	For the tenderer:

	

	Name & signature of witness
	(Insert name and address of organisation)
	
	Date
	

	Tenderer’s CIDB registration number (if applicable) 
	


Acceptance

By signing this part of this Form of Offer and Acceptance, the Employer identified below accepts the tenderer’s Offer.  In consideration thereof, the Employer shall pay the Contractor the amount due in accordance with the conditions of contract identified in the Contract Data.  Acceptance of the tenderer’s Offer shall form an agreement between the Employer and the tenderer upon the terms and conditions contained in this agreement and in the contract that is the subject of this agreement.

The terms of the contract, are contained in: 

Part C1

Agreements and Contract Data, (which includes this Form of Offer and Acceptance)

Part C2

Pricing Data

Part C3

Scope of Work: Works Information

Part C4

Site Information

and drawings and documents (or parts thereof), which may be incorporated by reference into the above listed Parts.

Deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Returnable Schedules as well as any changes to the terms of the Offer agreed by the tenderer and the Employer during this process of offer and acceptance, are contained in the Schedule of Deviations attached to and forming part of this Form of Offer and Acceptance.  No amendments to or deviations from said documents are valid unless contained in this Schedule.

The tenderer shall within two weeks of receiving a completed copy of this agreement, including the Schedule of Deviations (if any), contact the Employer’s agent (whose details are given in the Contract Data) to arrange the delivery of any securities, bonds, guarantees, proof of insurance and any other documentation to be provided in terms of the conditions of contract identified in the Contract Data at, or just after, the date this agreement comes into effect.  Failure to fulfil any of these obligations in accordance with those terms shall constitute a repudiation of this agreement.

Notwithstanding anything contained herein, this agreement comes into effect on the date when the tenderer receives one fully completed original copy signed between them of this document, including the Schedule of Deviations (if any).  

Unless the tenderer (now Contractor) within five working days of the date of such receipt notifies the Employer in writing of any reason why he cannot accept the contents of this agreement, this agreement shall constitute a binding contract between the Parties.

	Signature(s)


	
	
	

	Name(s)
	
	
	

	Capacity


	
	
	

	for the Employer

	

	Name & signature of witness
	(Insert name and address of organisation)
	
	Date
	


Note: If a tenderer wishes to submit alternative tenders, use another copy of this Form of Offer and Acceptance. 
Schedule of Deviations to be completed by the Employer prior to contract award.
Note:

1. This part of the Offer & Acceptance would not be required if the contract has been developed by negotiation between the Parties and is not the result of a process of competitive tendering.
2. The extent of deviations from the tender documents issued by the Employer prior to the tender closing date is limited to those permitted in terms of the Conditions of Tender.

3. A tenderer’s covering letter shall not be included in the final contract document.  Should any matter in such letter, which constitutes a deviation as aforesaid be the subject of agreement reached during the process of Offer and Acceptance, the outcome of such agreement shall be recorded here, and the final draft of the contract documents shall be revised to incorporate the effect of it.

	No.
	Subject
	Details

	1
	[●]
	[●]

	2
	[●]
	[●]

	3
	[●]
	[●]

	
	
	


By the duly authorised representatives signing this Schedule of Deviations below, the Employer and the tenderer agree to and accept this Schedule of Deviations as the only deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules, as well as any confirmation, clarification or changes to the terms of the Offer agreed by the tenderer and the Employer during this process of Offer and Acceptance.  

It is expressly agreed that no other matter whether in writing, oral communication or implied during the period between the issue of the tender documents and the receipt by the tenderer of a completed signed copy of this Form shall have any meaning or effect in the contract between the parties arising from this Agreement. 

	
	For the tenderer:


	
	For the Employer


	Signature


	
	
	

	Name
	
	
	

	Capacity


	
	
	

	On behalf of
	(Insert name and address of organisation)


	
	(Insert name and address of organisation)



	Name & signature of witness
	
	
	

	Date
	
	
	


C1.2 ECC3 Contract Data

Part one - Data provided by the Employer.
	Clause
	Statement
	Data

	1
	General
	

	
	The conditions of contract are the core clauses and the clauses for main Option 
	

	
	
	A:

Priced contract with activity schedule

	
	dispute resolution Option
	W1:
Dispute resolution procedure

	
	and secondary Options 
	

	
	
	X1:

Price adjustment for inflation

	
	
	X2

Changes in the law

	
	
	X5:

Sectional Completion

	
	
	X7:

Delay damages

	
	
	X13:
Performance Bond

	
	
	X16:
Retention

	
	
	X17:
Low performance damages

	
	
	X18:
Limitation of liability 

	
	
	Z:

Additional conditions of contract

	
	of the NEC3 Engineering and Construction Contract, April 2013 (ECC3)
	If 2005 Edition is to be used delete “April 2013” and replace with “June 2005 with amendments June 2006”. Always delete this note before finalising this Data

	10.1
	The Employer is :
	Eskom Holdings SOC Ltd (reg no: 2002/015527/30), a state-owned company incorporated in terms of the company laws of the Republic of South Africa

	
	Address
	Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg

	10.1
	The Project Manager is:
	[●]

	
	Address
	[●]

	
	Tel
	[●]

	
	Fax
	[●]

	
	e-mail
	[●]

	10.1
	The Supervisor is:
	[●]

	
	Address
	[●]

	
	Tel No.
	[●]

	
	Fax No.
	[●]

	
	e-mail
	[●]

	11.2(13)
	The works are 
	· Design, Supply, Install, Testing and Commissioning, Storage, and optimisation of the Emergency Preparedness Public Address System at Medupi Power Station. Refer to the scope of work for details of the works.

	11.2(14)
	The following matters will be included in the Risk Register
	· Adverse Weather (Rain, Wind, Hailstorm, Heatwave)

· Earthworks planning needs to take into consideration the rain.

· Normal construction hazards working with machinery. 
· Covid 19, cold, flue
· Industrial Action

· Labour Strike, and Community Unrest  

· Security of equipment, materials, and      resources

· Disease outbreak impact on labour force

· Access to existing areas

· Unavailability of Generation plant due to electricity demand (plant not made available to work on) 

· Non-compliance to approved Environmental Management Programme

· Working at heights

· Hazardous gas

· Electrocution  

· Power supply interruptions or failure

· Interface and Integration of the works with the running plant and other Contractors

· Non-Compliance to the Permit to Work System 

· Dehydration (Hot Weather Conditions) 

· Fire and Smoke

· Snakes

· Normal construction hazards for Mechanical work

· Delay in project execution resulting in time and cost overruns. 
· Project delays due to access constraints. 

· Inadequate supervision. 
· External Risk: Strikes and community unrest. 
· Scope creep

· Environment: Environmental violations 

· Non-compliance to Occupational Health and Safety

· Non-compliance to legal and other requirements

· Quality: Insufficient quality control during execution
· Fly ash dust airborne, and existing plant and material contaminated with Fly ash and dust.

	11.2(15)
	The boundaries of the site are 
	Medupi Power Station and various Zone areas as listed in the Technical Specification Document. 

	11.2(16)
	The Site Information is in 
	Part 4: Site Information

	11.2(19)
	The Works Information is in  
	Part 3: Scope of Work and all documents and drawings to which it refers. 

	12.2
	The law of the contract is the law of 
	the Republic of South Africa

	13.1
	The language of this contract is 
	English

	13.3
	The period for reply is
	Within 14 (fourteen) calendar days

	2
	The Contractor's main responsibilities
	Data required by this section of the core clauses is provided by the Contractor in Part 2 and terms in italics used in this section are identified elsewhere in this Contract Data. 

	3
	Time
	

	11.2(3)
	The completion date for the whole of the works is
	31 March 2026


	11.2(9)
	The key dates and the conditions to be met are:
	Condition to be met
	key date

	
	
	1
	Safety file submitted and accepted. 
	Two (2) weeks of the Contract Date

	
	
	2
	Environmental file submitted and accepted
	Two (2) weeks of the Contract Date

	
	
	3
	Programme submitted (If a programme is not identified in the Contract Data)
	Two (2) weeks of the Contract Date

	
	
	4
	Project Quality Plan (PQP) submitted and accepted.
	Two (2) weeks of the Contract Date

	
	
	5
	Competency File (refer to 348-389557 rev 5)
	Two (2) weeks of the Contract Date

	
	
	6
	Method Statements submitted and accepted
	14 days before starting the installation on works on site

	
	
	7
	Inspection and Test Plans (ITP)/ Quality Control Plan submitted and accepted
	14 days before starting off-site inspections

	
	
	8
	Submit Operating and Maintenance Manuals (for each section) 
	14 days prior to commissioning of each section of the works

	
	
	9
	Delivery of VDSS items
	As per line items set out in the VDSS

	
	
	
	
	

	30.1
	The access dates are:
	Part of the Site
	Date

	
	
	1
	Medupi Power Station Site (Mobilisation to Medupi Site)
	01 November 2024

	
	
	2
	All sections of the works (Contractor is to adhere to  Permit To Work system)  
	01 November 2024

	
	
	
	
	

	31.1
	The first programme is to be identified in 

If a programme is not identified in the Contract Data, the Contractor is to submit a first programme for acceptance within 
	the Contract Data provided by the Contractor. Refer to section 2.6 of the Works Information. 

two (2) weeks of the Contract Date. 

	31.2
	The starting date is
	01 November 2024

	32.2
	The Contractor submits revised programmes at intervals no longer than 
	One (1) week. 

	35.1
	The Employer is not willing to take over the works before the Completion Date.
	Sectional Completion Clause X5 refers. 

	4
	Testing and Defects
	

	42.2
	The defects date is 
	Fifty-Two (52) weeks after Completion of the Section (Clause X5) of the Works as per the Accepted Programme. 

	43.2
	The defect correction period is 
	Twenty-four (24) hours for emergencies or breakdowns and seven (7) working days for other defects including those requiring material to be obtained.  

	5
	Payment
	

	50.1
	The assessment interval is 
	Between the 20th day of each successive month and 27th of each month. 

	51.1
	The currency of this contract is the 
	South African Rand. 

	51.2
	The period within which payments are made is 
	Sixty (60) Calendar days after receipt of a Valid Tax invoices. A Valid Tax invoice is to be submitted to the email address stated in the Works Information.

	51.4
	The interest rate is 
	the publicly quoted prime rate of interest (calculated on a 365day year) charged from time to time by the Standard Bank of South Africa Limited (as certified, in the event of any dispute, by any manager of such bank, whose appointment it shall not be necessary to prove) for amounts due in Rands and 

(ii) the LIBOR rate applicable at the time for amounts due in other currencies.  LIBOR is the 6 month London Interbank Offered Rate quoted under the caption “Money Rates” in The Wall Street Journal for the applicable currency or if no rate is quoted for the currency in question then the rate for United States Dollars, and if no such rate appears in The Wall Street Journal then the rate as quoted by the Reuters Monitor Money Rates Service (or such service as may replace the Reuters Monitor Money Rates Service) on the due date for the payment in question, adjusted mutatis mutandis every 6 months thereafter and as certified, in the event of any dispute, by any manager employed in the foreign exchange department of The Standard Bank of South Africa Limited, whose appointment it shall not be necessary to prove.

	6
	Compensation events
	

	60.1(13)
	The place where weather is to be recorded is:
	Medupi Power Station

	
	The weather measurements to be recorded for each calendar month are, 
	the cumulative rainfall (mm)

	
	
	the number of days with rainfall more than 10 mm

	
	
	the number of days with minimum air temperature less than 0 degrees Celsius

	
	
	the number of days with snow lying at 09:00 hours South African Time

	
	
	and these measurements:

	
	The weather measurements are supplied by
	The South African Weather Services

	
	The weather data are the records of past weather measurements for each calendar month which were recorded at: 
	Medupi Power Station 

	
	and which are available from: 
	the South African Weather Bureau and included in Annexure A to this Contract Data provided by the Employer

	7
	Title
	There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data.

	8
	Risks and insurance
	

	80.1
	These are additional Employer's risks  
	1. Loss of or damage to Plant and Materials supplied to the Contractor by the Employer, or by Others on the Employer’s behalf, until the Contractor has received and accepted them.
2. Loss of or damage to the Works, Plant and Material due to strikes, riots and civil commotion not confined to the Contractor’s employees. 

3. Loss of or wear or damage to the Works and any Equipment, Plant and Materials retained on the Site by the Employer after a termination, except loss, wear or damage due to the activities of the Contractor on the Site after termination.
4. Theft and vandalism to the works after taking over.
5. Damage to the works after taking over but before the Defects Certificate. 

	9
	Termination
	There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data.

	10
	Data for main Option clause
	

	A
	Priced contract with activity schedule
	There is no reference to Contract Data in this Option and terms in italics are identified elsewhere in this Contract Data.

	11
	Data for Option W1
	

	W1.1
	The Adjudicator is 
	the person selected from the ICE-SA Division (or its successor body) of the South African Institution of Civil Engineering Panel of Adjudicators by the Party intending to refer a dispute to him.  (see www.ice-sa.org.za). If the Parties do not agree on an Adjudicator the Adjudicator will be appointed by the Arbitration Foundation of Southern Africa (AFSA).

	W1.2(3)
	The Adjudicator nominating body is:
	the Chairman of ICE-SA a joint Division of the South African Institution of Civil Engineering and the London Institution of Civil Engineers. (See www.ice-sa.org.za ) or its successor body.

	W1.4(2)
	The tribunal is: 
	arbitration. 

	W1.4(5)
	The arbitration procedure is 
	the latest edition of Rules for the Conduct of Arbitrations published by The Association of Arbitrators (Southern Africa) or its successor body.

	
	The place where arbitration is to be held is
	Johannesburg, South Africa

	
	The person or organisation who will choose an arbitrator.

· if the Parties cannot agree a choice or
· if the arbitration procedure does not state who selects an arbitrator, is
	the Chairman for the time being or his nominee of the Association of Arbitrators (Southern Africa) or its successor body.

	12
	Data for secondary Option clauses
	

	X1
	Price adjustment for inflation
	

	X1.1(a)
	The base date for indices is 
	The Price will be fixed for the first year from Close of tender and subject to escalation at the end of the first year. 

	X1.1(c)
	The proportions used to calculate the Price Adjustment Factor are:
	proportion
	linked to index for
	Index prepared by

	
	
	0.15

0.50

0.35
	Non-adjustable

Labour

Material
	SEIFSA table C3

SEIFSA table G2



	
	Total
	1.00


	
	

	X2
	Changes in the law
	There is no reference to Contract Data in this Option and terms in italics are identified elsewhere in this Contract Data.

	X5
	Sectional Completion
	

	X5.1
	The completion date for each section of the works is:
	section
	Description
	Amount per day

	
	
	1
	Zone 1 Unit 1
	As per Accepted Schedule

	
	
	2
	Zone 2 Unit 2
	As per Accepted Schedule

	
	
	3
	Zone 3 Unit 3
	As per Accepted Schedule

	
	
	4
	Zone 4 Unit 4
	As per Accepted Schedule

	
	
	5
	Zone 5 Unit 5
	As per Accepted Schedule

	
	
	6
	Zone 6 Unit 6
	As per Accepted Schedule

	
	
	7
	Zone 7 BOP South
	As per Accepted Schedule

	
	
	8
	Zone 8 H-Block
	As per Accepted Schedule

	
	
	9
	Zone 9 Admin Building
	As per Accepted Schedule

	
	
	10
	Zone 10 Access control
	As per Accepted Schedule

	
	
	11
	Zone 11 10 000 Silo
	As per Accepted Schedule

	
	
	12
	Zone 12 Plant West
	As per Accepted Schedule

	
	
	13
	Zone 13 Coal stockyard
	As per Accepted Schedule

	
	
	14
	Zone 14 Ash Plant (out of perimeter fence)
	As per Accepted Schedule

	
	
	15
	Zone 15 Raw water dams (Outside perimeter fence)
	As per Accepted Schedule

	
	
	16
	Zone 16 HV Yard (part of outside zone)
	As per Accepted Schedule

	
	
	
	
	

	
	
	17 
	Remainder of the works
	As per Accepted Schedule

	X5 & X7
	Sectional Completion and delay damages used together
	

	X7.1

X5.1
	Delay damages for late Completion of the sections of the works are: 
	section
	Description
	Amount per day

	
	
	1
	Zone 1 Unit 1
	R10 000.00

	
	
	2
	Zone 2 Unit 2
	R10 000.00

	
	
	3
	Zone 3 Unit 3
	R10 000.00

	
	
	4
	Zone 4 Unit 4
	R10 000.00

	
	
	5
	Zone 5 Unit 5
	R10 000.00

	
	
	6
	Zone 6 Unit 6
	R10 000.00

	
	
	7
	Zone 7 BOP South
	R10 000.00

	
	
	8
	Zone 8 H-Block
	R10 000.00

	
	
	9
	Zone 9 Admin Building
	R10 000.00

	
	
	10
	Zone 10 Access control
	R10 000.00

	
	
	11
	Zone 11 10 000 Silo
	R10 000.00

	
	
	12
	Zone 12 Plant West
	R10 000.00

	
	
	13
	Zone 13 Coal stockyard
	R10 000.00

	
	
	14
	Zone 14 Ash Plant (out of perimeter fence)
	R10 000.00

	
	
	15
	Zone 15 Raw water dams (Outside perimeter fence)
	R10 000.00

	
	
	16
	Zone 16 HV Yard (part of outside zone)
	R10 000.00

	
	
	17
	Remainder of the works
	R10 000.00

	
	The total delay damages payable by the Contractor does not exceed:
	the amount payable is 10% of the Contract Value, once the amount is exceeded the Employer may terminate the Contractor’s obligations to provide the works in accordance with Core Clause 93 and the amount due is to be A1 and A3 as stated in Core Clause 93. 

	X13
	Performance bond
	

	X13.1
	The amount of the performance bond is

The performance bond in the form set out
The performance bond is given to the

Employer within
	10% of the Contract Price at Contract Date
in the Works Information (Pro forma documents for these bonds and guarantees are provided here for convenience but are to be treated as part of the Works Information)
four weeks of the Contract Date

	X16
	Retention
	

	X16.1
	The retention free amount is 
	R 0.00 

	
	The retention percentage is
	5% of the total of the Prices (deducted on each Payment Certificate) 

	X17
	Low performance damages
	

	X17.1
	The amounts for low performance damages are:
	Amount
2.5% per section of the works (not exceeding 2.5% of the total of the Prices)
2.5%  
	Performance level
The sound pressure level shall be at least 10dB above the ambient SPL of each area as stipulated in SANS 7420-19. (Charged at completion of the Subzone if 90% to 99% of the required level is achieved. Anything less than 90% is considered unacceptable)  
The microphone console shall provide for a selection of up to 80 Zones or Subzone. (Charged at completion of commissioning of the Microphone Consoles if the microphone console provides for a selection of between 60 and 72 Zones or Subzone. Anything less than 60 selectable Zones or Subzone is considered unacceptable)  


	X18
	Limitation of liability
	

	X18.1
	The Contractor’s liability to the Employer for indirect or consequential loss is limited to:
	R0.0 (zero Rand)

	X18.2
	For any one event, the Contractor’s liability to the Employer for loss of or damage to the Employer’s property is limited to:
	the amount of the deductibles relevant to the event 

	X18.3
	The Contractor’s liability for Defects due to his design which are not listed on the Defects Certificate is limited to
	The greater of 

· the total of the Prices at the Contract Date 

and 

· the amounts excluded and unrecoverable from the Employer’s assets policy for correcting the Defect (other than the resulting physical damage which is not excluded) plus the applicable deductible as at contract date.

	X18.4
	The Contractor’s total liability to the Employer for all matters arising under or in connection with this contract, other than excluded matters, is limited to:
	the total of the Prices other than for the additional excluded matters.

The Contractor’s total liability for the additional excluded matters is not limited. 

The additional excluded matters are amounts for which the Contractor is liable under this contract for

· Defects due to his design which arise before the Defects Certificate is issued,

· Defects due to manufacture and fabrication outside the Site,

· loss of or damage to property (other than the works, Plant and Materials),

· death of or injury to a person and 

· infringement of an intellectual property right.

	X18.5
	The end of liability date is 
	(i) Two (2) years after the defects date for latent Defects and  

(ii) the date on which the liability in question prescribes in accordance with the Prescription Act No. 68 of 1969 (as amended or in terms of any replacement legislation) for any other matter.

A latent Defect is a Defect which would not have been discovered on reasonable inspection by the Employer or the Supervisor before the defects date, without requiring any inspection not ordinarily carried out by the Employer or the Supervisor during that period. 

If the Employer or the Supervisor do undertake any inspection over and above the reasonable inspection, this does not place a greater responsibility on the Employer or the Supervisor to have discovered the Defect.



	Z
	The Additional conditions of contract are
	Z1 to Z15 always apply.

	
	

	Z1
	Cession delegation and assignment

	Z1.1
	The Contractor does not cede, delegate, or assign any of its rights or obligations to any person without the written consent of the Employer.

	Z1.2
	Notwithstanding the above, the Employer may on written notice to the Contractor cede and delegate its rights and obligations under this contract to any of its subsidiaries or any of its present divisions or operations which may be converted into separate legal entities as a result of the restructuring of the Electricity Supply Industry. 

	
	

	Z2
	Joint ventures

	Z2.1
	If the Contractor constitutes a joint venture, consortium or other unincorporated grouping of two or more persons or organisations then these persons or organisations are deemed to be jointly and severally liable to the Employer for the performance of this contract.

	Z2.2
	Unless already notified to the Employer, the persons or organisations notify the Project Manager within two weeks of the Contract Date of the key person who has the authority to bind the Contractor on their behalf.

	Z2.3
	The Contractor does not alter the composition of the joint venture, consortium or other unincorporated grouping of two or more persons without the consent of the Employer having been given to the Contractor in writing.

	
	

	Z3
	Change of Broad Based Black Economic Empowerment (B-BBEE) status

	Z3.1
	Where a change in the Contractor’s legal status, ownership or any other change to his business composition or business dealings results in a change to the Contractor’s B-BBEE status, the Contractor notifies the Employer within seven days of the change.

	Z3.2
	The Contractor is required to submit an updated verification certificate and necessary supporting documentation confirming the change in his B-BBEE status to the Project Manager within thirty days of the notification or as otherwise instructed by the Project Manager.

	Z3.3
	Where, as a result, the Contractor’s B-BBEE status has decreased since the Contract Date the Employer may either re-negotiate this contract or alternatively, terminate the Contractor’s obligation to Provide the Works.

	Z3.4
	Failure by the Contractor to notify the Employer of a change in its B-BBEE status may constitute a reason for termination. If the Employer terminates in terms of this clause, the procedures on termination are P1, P2 and P3 as stated in clause 92, and the amount due is A1 and A3 as stated in clause 93.

	
	

	Z4
	Confidentiality

	Z4.1
	The Contractor does not disclose or make any information arising from or in connection with this contract available to Others. This undertaking does not, however, apply to information which at the time of disclosure or thereafter, without default on the part of the Contractor, enters the public domain or to information which was already in the possession of the Contractor at the time of disclosure (evidenced by written records in existence at that time).  Should the Contractor disclose information to Others in terms of clause 25.1, the Contractor ensures that the provisions of this clause are complied with by the recipient.

	Z4.2
	If the Contractor is uncertain about whether any such information is confidential, it is to be regarded as such until notified otherwise by the Project Manager.

	Z4.3
	In the event that the Contractor is, at any time, required by law to disclose any such information which is required to be kept confidential, the Contractor, to the extent permitted by law prior to disclosure, notifies the Employer so that an appropriate protection order and/or any other action can be taken if possible, prior to any disclosure.  In the event that such protective order is not, or cannot, be obtained, then the Contractor may disclose that portion of the information which it is required to be disclosed by law and uses reasonable efforts to obtain assurances that confidential treatment will be afforded to the information so disclosed.

	Z4.4
	The taking of images (whether photographs, video footage or otherwise) of the works or any portion thereof, in the course of Providing the Works and after Completion, requires the prior written consent of the Project Manager.  All rights in and to all such images vests exclusively in the Employer.  

	Z4.5
	The Contractor ensures that all his Subcontractors abide by the undertakings in this clause.

	
	

	Z5
	Waiver and estoppel: Add to core clause 12.3:

	Z5.1
	Any extension, concession, waiver or relaxation of any action stated in this contract by the Parties, the Project Manager, the Supervisor, or the Adjudicator does not constitute a waiver of rights, and does not give rise to an estoppel unless the Parties agree otherwise and confirm such agreement in writing.

	
	

	Z6
	Health, safety and the environment:  Add to core clause 27.4

	Z6.1
	The Contractor undertakes to take all reasonable precautions to maintain the health and safety of persons in and about the execution of the works. Without limitation the Contractor:

· accepts that the Employer may appoint him as the “Principal Contractor” (as defined and provided for under the Construction Regulations 2014 (promulgated under the Occupational Health & Safety Act 85 of 1993) (“the Construction Regulations”) for the Site;

· warrants that the total of the Prices as at the Contract Date includes a sufficient amount for proper compliance with the Construction Regulations, all applicable health & safety laws and regulations and the health and safety rules, guidelines and procedures provided for in this contract and generally for the proper maintenance of health & safety in and about the execution of works; and

· undertakes, in and about the execution of the works, to comply with the Construction Regulations and with all applicable health & safety laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing.

	Z6.2
	The Contractor, in and about the execution of the works, complies with all applicable environmental laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing.

	
	

	Z7
	Provision of a Tax Invoice and interest.  Add to core clause 51

	Z7.1
	Within one week of receiving a payment certificate from the Project Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice in accordance with the Employer's procedures stated in the Works Information, showing the amount due for payment equal to that stated in the payment certificate.

	Z7.2
	If the Contractor does not provide a tax invoice in the form and by the time required by this contract, the time by when the Employer is to make a payment is extended by a period equal in time to the delayed submission of the correct tax invoice.  Interest due by the Employer in terms of core clause 51.2 is then calculated from the delayed date by when payment is to be made.

	Z7.3
	The Contractor (if registered in South Africa in terms of the companies Act) is required to comply with the requirements of the Value Added Tax Act, no 89 of 1991 (as amended) and to include the Employer’s VAT number 4740101508 on each invoice he submits for payment.

	
	

	Z8
	Notifying compensation events

	Z8.1
	Delete from the last sentence in core clause 61.3, “unless the Project Manager should have notified the event to the Contractor but did not”.

	
	

	Z9
	Employer’s limitation of liability

	Z9.1
	The Employer’s liability to the Contractor for the Contractor’s indirect or consequential loss is limited to R0.00 (zero Rand)

	Z9.2
	The Contractor’s entitlement under the indemnity in 83.1 is provided for in 60.1(14) and the Employer’s liability under the indemnity is limited.

	
	

	Z10
	Termination: Add to core clause 91.1, at the second main bullet point, fourth sub-bullet point, after the words "against it":  

	Z10.1
	   or had a business rescue order granted against it.

	
	

	Z11
	Addition to secondary Option X7 Delay damages (if applicable in this contract)

	Z11.1
	If the amount due for the Contractor’s payment of delay damages reaches the limits stated in this Contract Data for Option X7 or Options X5 and X7 used together, the Employer may terminate the Contractor’s obligation to Provide the Works using the same procedures and payment on termination as those applied for reasons R1 to R15 or R18 stated in the Termination Table. 

	
	


	Z12
	Ethics

	For the purposes of this Z-clause, the following definitions apply:

	Affected Party
	means, as the context requires, any party, irrespective of whether it is the Contractor or a third party, such party’s employees, agents, or Subcontractors or Subcontractor’s employees, or any one or more of all of these parties’ relatives or friends,

	Coercive Action
	means to harm or threaten to harm, directly or indirectly, an Affected Party or the property of an Affected Party, or to otherwise influence or attempt to influence an Affected Party to act unlawfully or illegally,

	Collusive Action
	means where two or more parties co-operate to achieve an unlawful or illegal purpose, including to influence an Affected Party to act unlawfully or illegally,

	Committing Party
	means, as the context requires, the Contractor, or any member thereof in the case of a joint venture, or its employees, agents, or Subcontractor or the Subcontractor’s employees,

	Corrupt Action
	means the offering, giving, taking, or soliciting, directly or indirectly, of a good or service to unlawfully or illegally influence the actions of an Affected Party,

	Fraudulent Action
	means any unlawfully or illegally intentional act or omission that misleads, or attempts to mislead, an Affected Party, in order to obtain a financial or other benefit or to avoid an obligation or incurring an obligation,

	Obstructive Action
	means a Committing Party unlawfully or illegally destroying, falsifying, altering or concealing information or making false statements to materially impede an investigation into allegations of Prohibited Action, and

	Prohibited Action
	means any one or more of a Coercive Action, Collusive Action Corrupt Action, Fraudulent Action or Obstructive Action.

	Z12.1
	A Committing Party may not take any Prohibited Action during the course of the procurement of this contract or in execution thereof.

	Z12.2
	The Employer may terminate the Contractor’s obligation to Provide the Services if a Committing Party has taken such Prohibited Action and the Contractor did not take timely and appropriate action to prevent or remedy the situation, without limiting any other rights or remedies the Employer has. It is not required that the Committing Party had to have been found guilty, in court or in any other similar process, of such Prohibited Action before the Employer can terminate the Contractor’s obligation to Provide the Services for this reason.

	Z12.3
	If the Employer terminates the Contractor’s obligation to Provide the Services for this reason, the amounts due on termination are those intended in core clauses 92.1 and 92.2.

	Z12.4
	A Committing Party co-operates fully with any investigation pursuant to alleged Prohibited Action. Where the Employer does not have a contractual bond with the Committing Party, the Contractor ensures that the Committing Party co-operates fully with an investigation.

	
	

	Z13
	Insurance

	Z 13.1
	Replace core clause 84 with the following:


	Insurance cover
	84
	

	
	
	

	
	84.1
	When requested by a Party, the other Party provides certificates from his insurer or broker stating that the insurances required by this contract are in force.

	
	
	

	
	84.2
	The Contractor provides the insurances stated in the Insurance Table A.

	
	
	

	
	84.3
	The insurances provide cover for events which are at the Contractor’s risk from the starting date until the earlier of Completion and the date of the termination certificate.

	
	
	

	
	
	INSURANCE TABLE A
Insurance against
Minimum amount of cover or minimum limit of indemnity
Loss of or damage to the works, Plant and Materials
The replacement cost where not covered by the Employer’s insurance. 
The Employer’s policy deductible, as at Contract Date, where covered by the Employer’s insurance
Loss of or damage to Equipment
The replacement cost
Liability for loss of or damage to property (except the works, Plant and Materials and Equipment) and liability for bodily injury to or death of a person (not an employee of the Contractor) caused by activity in connection with this Contract. 
Loss of or damage to property

Employer’s property

The replacement cost where not covered by the Employer’s insurance. 
The Employer’s policy deductible, as at Contract Date, where covered by the Employer’s insurance. 
Other property

The replacement cost. 
Bodily injury to or death of a person 

The amount required by applicable law
Liability for death of or bodily injury to employees of the Contractor arising out of and in the course of their employment in connection with this contract
The amount required by the applicable law


	
	
	

	Z 13.2
	
	Replace core clause 87 with the following:
The Employer provides the insurances stated in the Insurance Table B.

	
	
	

	
	
	

	
	
	

	
	
	INSURANCE TABLE B
Insurance against or name of policy
Minimum amount of cover or minimum limit of indemnity

Assets All Risk

Per the insurance policy document

Contract Works insurance

Per the insurance policy document

Environmental Liability

Per the insurance policy document
General and Public Liability

Per the insurance policy document
Transportation (Marine)

Per the insurance policy document
Motor Fleet and Mobile Plant

Per the insurance policy document
Terrorism

Per the insurance policy document
Cyber Liability

Per the insurance policy document

Nuclear Material Damage and Business Interruption
Per the insurance policy document
Nuclear Material Damage Terrorism
Per the insurance policy document



	Z14
	Nuclear Liability

	Z14.1
	The Employer is the operator of the Koeberg Nuclear Power Station (KNPS), a nuclear installation, as designated by the National Nuclear Regulator of the Republic of South Africa and is the holder of a nuclear licence in respect of the KNPS.

	Z14.2
	The Employer is solely responsible for and indemnifies the Contractor or any other person against any and all liabilities which the Contractor or any person may incur arising out of or resulting from nuclear damage, as defined in Act 47 of 1999, save to the extent that any liabilities are incurred due to the unlawful intent of the Contractor or any other person or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS site, without the permission of the Employer or of a person acting on behalf of the Employer.

	Z14.3
	Subject to clause Z14.4 below, the Employer waives all rights of recourse, arising from the aforesaid, save to the extent that any claims arise or liability is incurred due or attributable to the unlawful intent of the Contractor or any other person, or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS site, without the permission of the Employer or of a person acting on behalf of the Employer.

	Z14.4
	The Employer does not waive its rights provided for in section 30 (7) of Act 47 of 1999, or any replacement section dealing with the same subject matter.

	Z14.5
	The protection afforded by the provisions hereof shall be in effect until the KNPS is decommissioned.

	
	

	Z15
	Asbestos

	For the purposes of this Z-clause, the following definitions apply:

	AAIA
	means approved asbestos inspection authority.

	ACM
	means asbestos containing materials.

	AL
	means action level, i.e. a level of 50% of the OEL, i.e. 0.1 regulated asbestos fibres per ml of air measured over a 4 hour period. The value at which proactive actions is required in order to control asbestos exposure to prevent exceeding the OEL.

	Ambient Air
	means breathable air in area of work with specific reference to breathing zone, which is defined to be a virtual area within a radius of approximately 30cm from the nose inlet.

	Compliance Monitoring
	means compliance sampling used to assess whether or not the personal exposure of workers to regulated asbestos fibres is in compliance with the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles.

	OEL
	means occupational exposure limit.

	Parallel Measurements
	means measurements performed in parallel, yet separately, to existing measurements to verify validity of results.

	Safe Levels
	means airborne asbestos exposure levels conforming to the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment, and articles.

	Standard
	means the Employer’s Asbestos Standard 32-303: Requirements for Safe Processing, Handling, Storing, Disposal and Phase-out of Asbestos and Asbestos Containing Material, Equipment and Articles.

	SANAS
	means the South African National Accreditation System.

	TWA
	means the average exposure, within a given workplace, to airborne asbestos fibres, normalized to the baseline of a 4 hour continuous period, also applicable to short term exposures, i.e. 10-minute TWA.

	Z15.1
	The Employer ensures that the Ambient Air in the area where the Contractor will Provide the Services conforms to the acceptable prescribed South African standard for asbestos, as per the regulations published in GNR 155 of 10 February 2002, under the Occupational Health and Safety Act, 1993 (Act 85 of 1993) (“Asbestos Regulations”). The OEL for asbestos is 0.2 regulated asbestos fibres per millilitre of air as a 4-hour TWA, averaged over any continuous period of four hours, and the short term exposure limit of 0.6 regulated asbestos fibres per millilitre of air as a 10-minute TWA, averaged over any 10 minutes, measured in accordance with HSG248 and monitored according to HSG173 and OESSM.

	Z15.2
	Upon written request by the Contractor, the Employer certifies that these conditions prevail. All measurements and reporting are effected by an independent, competent, and certified occupational hygiene inspection body, i.e. a SANAS accredited and Department of Employment and Labour approved AAIA. The Contractor may perform Parallel Measurements and related control measures at the Contractor’s expense. For the purposes of compliance the results generated from Parallel Measurements are evaluated only against South African statutory limits as detailed in clause Z15.1. Control measures conform to the requirements stipulated in the AAIA-approved asbestos work plan.

	Z15.3
	The Employer manages asbestos and ACM according to the Standard.

	Z15.4
	In the event that any asbestos is identified while Providing the Services, a risk assessment is conducted and if so required, with reference to possible exposure to an airborne concentration of above the AL for asbestos, immediate control measures are implemented, and relevant air monitoring conducted in order to declare the area safe.

	Z15.5
	The Contractor’s personnel are entitled to stop working and leave the contaminated area forthwith until such time that the area of concern is declared safe by either Compliance Monitoring or an AAIA approved control measure intervention, for example, per the emergency asbestos work plan, if applicable.

	Z15.6
	The Contractor continues to Provide the Services, without additional control measures presented, on presentation of Safe Levels. The contractually agreed dates to Provide the Services, including the Completion Date, are adjusted accordingly. The contractually agreed dates are extended by the notification periods required by regulations 3 and 21 of the Asbestos Regulations, 2001.

	Z15.7
	Any removal and disposal of asbestos, asbestos containing materials and waste, is done by a registered asbestos Contractor, instructed by the Employer at the Employer’s expense, and conducted in line with South African legislation.


Annexure A:
 One-in-ten-year-return weather data obtained from SA Weather Bureau for [weather station]

If any one of these weather measurements recorded within a calendar month, before the Completion Date for the whole of the works and at the place stated in this Contract Data is shown to be more adverse than the amount stated below then the Contractor may notify a compensation event.

Only the difference between the more adverse recorded weather and the equivalent measurement given above is taken into account in assessing a compensation event. 

[image: image1.png]Lephalale (One-in-Ten-Year)

Lephalale- (1983-2022)
Comp No: 7888

One-in-t —return
cumulative | Number of days | Number of days :;s"mf
Month " with rain more !
rainall (mm) | %t 12 m snow lying at
08:00 AT
AN 1558 2 No Data
FeB 1204 s No Data
MAR 108.5 3 No Data
aPR 56.0 2 No Data
mAY 244 1 No Data
JuN 121 o No Data
oL 5.0 o No Data
aue 32 o No Data
S 67 1 No Data
oct 663 2 No Data
Nov 1237 2 No Data
DEC 152.4 s No Data





C1.2 Contract Data

Part two - Data provided by the Contractor.
Notes to a tendering Contractor:

1. Please read both the NEC3 Engineering and Construction Contract (April 2013) and the relevant parts of its Guidance Notes (ECC3-GN)
 in order to understand the implications of this Data which the tenderer is required to complete.  An example of the completed Data is provided on pages 156 to 158 of the ECC3 (April 2013) Guidance Notes.

2. The number of the clause which requires the data is shown in the left-hand column for each statement however other clauses may also use the same data

3. Where a form field like this [     ] appears, data is required to be inserted relevant to the option selected. Click on the form field once and type in the data.  Otherwise, complete by hand and in ink.

Completion of the data in full, according to Options chosen, is essential to create a complete contract.

	Clause
	Statement
	Data

	10.1
	The Contractor is (Name):
	     

	
	Address
	     

	
	Tel No.
	     

	
	Fax No.
	     

	11.2(8)
	The direct fee percentage is
	     %

	
	The subcontracted fee percentage is
	     %

	11.2(18)
	The working areas are the Site and
	     

	24.1
	The Contractor's key persons are:
	

	
	1
Name:
	     

	
	
Job:
	     

	
	
Responsibilities:
	     


	
	
Qualifications:
	     

	
	
Experience:
	     

	
	2
Name:
	     

	
	
Job
	     

	
	
Responsibilities:
	     

	
	
Qualifications:
	     

	
	
Experience:
	     

	
	
	CV's (and further key persons data including CVs) are appended to Tender Schedule entitled     .

	11.2(3)
	The completion date for the whole of the works is
	     

	11.2(14)
	The following matters will be included in the Risk Register
	     

	11.2(19)
	The Works Information for the Contractor’s design is in:
	     

	31.1
	The programme identified in the Contract Data is
	     

	A
	Priced contract with activity schedule
	

	11.2(20) 
	The activity schedule is in
	     

	11.2(30)
	The tendered total of the Prices is 
	      (in figures) 

      (in words), excluding VAT 

	
	Data for Schedules of Cost Components
	Note “SCC” means Schedule of Cost Components starting on page 60, and “SSCC” means Shorter Schedule of Cost Components starting on page 63 of ECC3 (April 2013).

	A
	Priced contract with activity schedule
	Data for the Shorter Schedule of Cost Components

	41 in SSCC
	The percentage for people overheads is:
	     %

	21 in SSCC
	The published list of Equipment is the last edition of the list published by
	     

	
	The percentage for adjustment for Equipment in the published list is
	Minus      %

	22 in SSCC
	The rates of other Equipment are:
	Equipment
	Size or capacity
	Rate

	
	
	     
	     
	     

	
	
	     
	     
	     

	
	
	     
	     
	     

	
	
	     
	     
	     

	
	
	     
	     
	     

	61 in SSCC
	The hourly rates for Defined Cost of design outside the Working Areas are
	Category of employee
	Hourly rate

	
	Note:  Hourly rates are estimated ‘cost to company of the employee’ and not selling rates.  
	     
	     

	
	Please insert another schedule if foreign resources may also be used
	     
	     

	
	
	     
	     

	
	
	     
	     

	62 in SSCC
	The percentage for design overheads is
	     %

	63 in SSCC
	The categories of design employees whose travelling expenses to and from the Working Areas are included in Defined Cost are:
	     

	
	Refer to the SHORTER SCHEDULE OF COST COMPONENTS under ECC NEC 3 document  of April 2013 and provide the full list of the components of the costs under the following headings,
	

	
	People 1:
	     

	
	Equipment 2:
	     

	
	Plant and Materials 3:
	     

	
	Charges 4:
	     

	
	Manufacture and fabrication 5:
	     

	
	Design 6:
	     

	
	Insurance 7:
	     


C1.3 Forms of Securities 

Pro formas for Bonds & Guarantees

For use with the NEC3 Engineering & Construction Contract 

The conditions of contract stated in the Contract Data Part 1 include the following Secondary Options:

Option X13:
Performance Bond

Each of these secondary Options requires a bond or guarantee “in the form set out in the Works Information”.    Pro forma documents for these bonds and guarantees are provided here for convenience but are to be treated as part of the Works Information.

Option X16:
Retention

The Contractor may provide a Retention Money Guarantee in the form stated here.  When the Employer receives and accepts a Retention Money Guarantee exactly in the form stated he will instruct the Project Manager not to assess any amount be retained in terms of secondary Option X16.
The organisation providing the bond / guarantee does so by copying the pro forma document onto his letterhead without any change to the text or format and completing the required details.  The completed document is then given to the Employer within the time stated in the contract.  

Pro forma Performance Bond – Demand Guarantee (for use with Option X13)

(to be reproduced exactly as shown below on the letterhead of the Contractor’s Parent Company)
	Eskom Holdings SOC Ltd

Megawatt Park

Maxwell Drive

Sandton

Johannesburg
	Date:
	


Dear Sirs

Reference No. [●] [Drafting Note: Bank reference number to be inserted]
Performance Bond – Demand Guarantee: [Drafting Note: Name of Contractor to be inserted]
Project [  ] Contract Reference: …… [Drafting Note: Contractor contract reference number to be inserted]
1. In this Guarantee the following words and expressions shall have the following meanings: -

1.1 “Bank” - means [●], [●] Branch, (Registration No. [●]); [Drafting Note: Name of Bank to be inserted]

1.2 “Bank’s Address” - means [●]; [Drafting Note: Bank’s physical address to be inserted]

1.3 “Contract” – means the written agreement relating to the Project, entered into between Eskom and the Contractor, on or about the [●] day of [●] 200[●] (Contract Reference No. [.]as amended, varied, restated, novated or substituted from time to time; [Drafting Note: Signature Date and Contract reference number to be inserted]

1.4 “Contractor” – means [●] a company registered in accordance with the laws of [●] under Registration Number [●]. [Drafting Note: Name and details of Contractor to be inserted]

1.5 “Eskom” - means Eskom Holdings SOC Ltd, a company registered in accordance with the laws of the Republic of South Africa under Registration Number 2002/015527/30].

1.6 “Expiry Date” - means the date on which the Defects Certificate is issued in terms of the Contract.

1.7 “Guaranteed Sum” - means the sum of R [●] ([●] Rand); 

1.8 “Project” - means [insert if applicable.].

2. At the instance of the Contractor, we the undersigned ______________ and ______________, in our respective capacities as _____________ and ___________ of the Bank, and duly authorized thereto, confirm that we hold the Guaranteed Sum at the disposal of Eskom, as security for the proper performance by the Contractor of all of its obligations in terms of and arising from the Contract and hereby undertake to pay to Eskom, on written demand from Eskom received prior to the Expiry Date, any sum or sums not exceeding in total the Guaranteed Sum.

3. A demand for payment under this guarantee shall be made in writing at the Bank’s address and shall:

3.1 be signed on behalf of Eskom by a Group Executive, Divisional Executive, Senior General Manager, General Manager or its delegate;

3.2 state the amount claimed (“the Demand Amount’);

3.3 state that the Demand Amount is payable to Eskom in the circumstances contemplated in the Contract.

4. Notwithstanding the reference herein to the Contract the liability of the Bank in terms hereof is as principal and not as surety and the Bank’s obligation/s to make payment:

4.1 is and shall be absolute provided demand is made in terms of this bond in all circumstances; and

4.2 is not, and shall not be construed to be, accessory or collateral on any basis whatsoever. 

5. The Bank’s obligations in terms of this Guarantee:

5.1 shall be restricted to the payment of money only and shall be limited to the maximum of the Guaranteed Sum; and

5.2 shall not be discharged and compliance with any demand for payment received by the Bank in terms hereof shall not be delayed, by the fact that a dispute may exist between Eskom and the Contractor.

6. Eskom shall be entitled to arrange its affairs with the Contractor in any manner which it sees fit, without advising us and without affecting our liability under this Guarantee. This includes, without limitation, any extensions, indulgences, release or compromise granted to the Contractor or any variation under or to the Contract. 

7. Should Eskom cede its rights against the Contractor to a third party where such cession is permitted under the Contract, then Eskom shall be entitled to cede to such third party the rights of Eskom under this Guarantee on written notification to the Bank of such cession.

8. This Guarantee:

8.1 shall expire on the Expiry Date until which time it is irrevocable;

8.2 is, save as provided for in 7 above, personal to Eskom and is neither negotiable nor transferable;

8.3 shall be returned to the Bank upon the earlier of payment of the full Guaranteed Sum or expiry hereof;

8.4 shall be regarded as a liquid document for the purpose of obtaining a court order; and

8.5 shall be governed by and construed in accordance with the law of the Republic of South Africa and shall be subject to the jurisdiction of the Courts of the Republic of South Africa. 

8.6 Any claim which arises or demand for payment received after expiry date will be invalid and unenforceable.

9. The Bank chooses domicilium citandi et executandi for all purposes in connection with this Guarantee at the Bank’s Address.

Signed at _____________________

Date ____________________________

For and behalf of the Bank

Bank Signatory: ___________________

Bank Signatory: ___________________

Witness: ________________________

Witness: _________________________

Bank’s seal or stamp

Pro forma Retention Money Guarantee (may be used when Option X16 applies)

(to be reproduced exactly as shown below on the letterhead of the Bank providing the Guarantee)
	Eskom Holdings SOC Limited

Megawatt Park

Maxwell Drive

Sandton

Johannesburg 
	Date:
	


Dear Sirs

Reference No. [●] [Drafting Note: Bank reference number to be inserted]
Retention Money Guarantee: [Drafting Note: Name of Contractor to be inserted]
Project [  ] : Contract Reference:  [Drafting Note: Contractor contract reference number to be inserted]
1. In this Guarantee the following words and expressions shall have the following meanings:-

1.1 “Bank” - means [●], [●] Branch, (Registration No. [●]); [Drafting Note: Name of Bank to be inserted]

1.2 “Bank’s Address” - means [●]; [Drafting Note: Bank’s physical address to be inserted]

1.3 “Contract” – means the written agreement relating to the Project, entered into between Eskom and the Contractor, on or about the [●] day of [●] 200[●] (Contract Reference No. ………. as amended, varied, restated, novated or substituted from time to time; [Drafting Note: Signature Date and Contract reference number to be inserted]

1.4 “Contractor” – means [●] a company registered in accordance with the laws of [●] under Registration Number [●]. [Drafting Note: Name and details of Contractor to be inserted]

1.5 “Eskom” - means Eskom Holdings SOC Limited, a company registered in accordance with the laws of the Republic of South Africa under Registration Number 2002/015527/30

1.6 “Expiry Date” - means the date on which the Defects Certificate is issued in terms of the Contract.

1.7 “Guaranteed Sum” - means the sum of R [●] ([●] Rand); [Drafting Note: Insert amount of Retention Money Guarantee.].

1.8 “Project” - means the…………………………………..

2. At the instance of the Contractor, we the undersigned ______________ and ______________, in our respective capacities as _____________ and ___________ of the Bank, and duly authorized thereto, confirm that we hold the Guaranteed Sum at the disposal of Eskom, as security for the proper performance by the Contractor of all of its obligations in terms of and arising from the Contract and hereby undertake to pay to Eskom, on written demand from Eskom received prior to the Expiry Date, any sum or sums not exceeding in total the Guaranteed Sum.

3. A demand for payment under this guarantee shall be made in writing at the Bank’s address and shall:

3.1 be signed on behalf of Eskom by a director of Eskom or his authorised delegate.

3.2 state the amount claimed (“the Demand Amount’);

3.3 state that the Contractor has failed to carry out his obligation(s) to rectify certain defect(s) for which he is responsible under the Contract (and the nature of such defect(s)) alternatively that the Demand Amount is payable to Eskom in the circumstances contemplated in the Contract.

4. Notwithstanding the reference herein to the Contract the liability of the Bank in terms hereof is as principal and not as surety and the Bank’s obligation/s to make payment:

4.1 is and shall be absolute provided demand is made in terms of this bond in all circumstances; and

4.2 is not, and shall not be construed to be, accessory or collateral on any basis whatsoever. 

5. The Bank’s obligations in terms of this Guarantee:

5.1 shall be restricted to the payment of money only and shall be limited to the maximum of the Guaranteed Sum; and

5.2 shall not be discharged and compliance with any demand for payment received by the Bank in terms hereof shall not be delayed by the fact that a dispute may exist between Eskom and the Contractor.

6. Eskom shall be entitled to arrange its affairs with the Contractor in any manner which it sees fit, without advising us and without affecting our liability under this Guarantee. This includes, without limitation, any extensions, indulgences, release or compromise granted to the Contractor or any variation under or to the Contract. 

7. Should Eskom cede its rights against the Contractor to a third party where such cession is permitted under the Contract, then Eskom shall be entitled to cede to such third party the rights of Eskom under this Guarantee on written notification to the Bank of such cession.

8. This Guarantee:

8.1 shall expire on the Expiry Date until which time it is irrevocable.
8.2 is, save as provided for in 7 above, personal to Eskom and is neither negotiable nor transferable.
8.3 shall be returned to the Bank upon the earlier of payment of the full Guaranteed Sum or expiry hereof.
8.4 shall be regarded as a liquid document for the purpose of obtaining a court order; and

8.5 shall be governed by and construed in accordance with the law of the Republic of South Africa and shall be subject to the jurisdiction of the Courts of the Republic of South Africa.

8.6 Any claim which arises or demand for payment received after expiry date will be invalid and unenforceable.

9. The Bank chooses domicilium citandi et executandi for all purposes in connection with this Guarantee at the Bank’s Address.

Signed at _____________________

Date ____________  Bank’s seal or stamp

For and behalf of the Bank

Bank Signatory: ___________________

Bank Signatory: ___________________

Witness: ________________________

Witness: _________________________

Part 2: Pricing Data

ECC3 Option A

	Document reference
	Title
	No of pages

	C2.1
	Pricing assumptions: Option A
	     

	C2.2
	The activity schedule  
	     


C2.1 Pricing assumptions: Option A

1. How work is priced and assessed for payment

Clause 11 in NEC3 Engineering and Construction Contract, (ECC3) Option A states:

	Identified and defined terms
	11

11.2
	(20) The Activity Schedule is the activity schedule unless later changed in accordance with this contract.



	
	
	(27) The Price for Work Done to Date is the total of the Prices for 

· each group of completed activities and

· each completed activity which is not in a group.

A completed activity is one which is without Defects which would either delay or be covered by immediately following work.



	
	
	(30) The Prices are the lump sum prices for each of the activities on the Activity Schedule unless later changed in accordance with this contract.




This confirms that Option A is a lump sum form of contract where the work is broken down into activities, each of which is priced by the tendering Contractor as a lump sum.   
Only completed activities are assessed for payment at each assessment date; no part payment is made if the activity is not completed by the assessment date. 

2. Function of the Activity Schedule

Clause 54.1 in Option A states: “Information in the Activity Schedule is not Works Information or Site Information”.  This confirms that specifications and descriptions of the work or any constraints on how it is to be done are not included in the Activity Schedule but in the Works Information.  This is further confirmed by Clause 20.1 which states, “The Contractor Provides the Works in accordance with the Works Information”. Hence the Contractor does not Provide the works in accordance with the Activity Schedule.  The Activity Schedule is only a pricing document.  

3. Link to the programme

Clause 31.4 states that “The Contractor provides information which shows how each activity on the Activity Schedule relates to the operations on each programme which he submits for acceptance”.  
The tendering Contractor is to develop a high-level programme first then resource each activity and thus arrive at the lump sum price for that activity both of which can be entered into the activity schedule.  

4. Preparing the activity schedule
Generally, it is the tendering Contractor who prepares the activity schedule by breaking down the works described within the Works Information into suitable activities which can be well defined, shown on a programme and priced as a lump sum.

The Employer, in his Instructions to Tenderers or in a Tender Schedule, may have listed some items that he requires the Contractor to include in his activity schedule and be priced accordingly. 
It is assumed that in preparing his activity schedule the Contractor:
· Has taken account of the guidance given in the ECC3 Guidance Notes pages 19 and 20;

· Understands the function of the Activity Schedule and how work is priced and paid for;

· Is aware of the need to link the Activity Schedule to activities shown on his programme;

· Has listed and priced activities in the activity schedule which are inclusive of everything necessary and incidental to Providing the works in accordance with the Works Information, as it was at the time of tender, as well as correct any Defects not caused by an Employer’s risk;
· Has priced work he decides not to show as a separate activity within the Prices of other listed activities in order to fulfil the obligation to complete the works for the tendered total of the Prices; 
· Understands there is no adjustment to the lump sum Activity Schedule price if the amount, or quantity, of work within that activity later turns out to be different to that which the Contractor estimated at time of tender. The only basis for a change to the Prices is as a result of a compensation event. 
In preparing the activity schedule, the Contractor is further required to: 

· Take note that the Employer has specified some high-level activities as listed in the activity schedule for the purpose of comparing tenders, however; it remains the responsibility of the Contractor to identify and price all activities as stated in the Works Information and/or in the scope of work documents.  
· Insert prices into the high-level activity schedule as lump sums. 

· Ensure that all activities (which are inclusive of everything necessary and incidental to providing the works in accordance with the Works Information) are priced.  
· Include cost for labour under the sums for works activities (under “THE WORKS”) and not under the Preliminaries and General (P&G) items. 

· Take note that all Preliminaries and General items (Time-related items, Fixed charge and Value-Related items)  will be spread within the works activities (under “THE WORKS”)  once a successful tender is identified. 
C2.2 the activity schedule
	ITEM NO.
	HIGH-LEVEL ACTIVITY DESCRIPTION 
	UNIT
	AMOUNT

	 
	 
	 
	 

	1
	PRELIMINARIES AND GENERAL

	1.1
	Fixed charge and Value-Related items
	Sum
	 

	1.2
	Time-related items 
	Sum
	

	1.3
	Site Establishment completed and accepted
	Sum
	 

	 
	 
	 
	 

	 
	[A] TOTAL:
	Sum
	 

	 
	 
	 
	 

	2
	THE WORKS

	2.1
	PROJECT INITIATION PHASE ACTIVITIES 

	2.1.1
	Safety file submitted and accepted
	Sum
	 

	2.1.2
	Environmental file submitted and accepted
	Sum
	 

	2.1.3
	Project Quality Plan (PQP) submitted and accepted
	Sum
	 

	2.1.4
	Quality Competency File submitted and accepted
	Sum
	 

	 
	 
	 
	 

	 
	[B] TOTAL:
	Sum
	 

	2.2
	EXISTING INFRASTRUCTURE ACTIVITIES 

	2.2.1
	Existing Basic Design review, evaluation, design, updating and acceptance of existing design documents
	Sum
	 

	2.2.2
	Removal of Existing  Installations after assessing re-usability
	Sum
	 

	2.2.3
	Additional fibre optic cables and fibre optic patch leads and related consumables
	Sum
	 

	2.2.4
	Noise level assessments in each zone and sub-zones
	Sum
	 

	 
	 
	 
	 

	 
	[C] TOTAL:
	Sum
	 

	2.3
	GEOTECHNICAL ACTIVITIES 

	2.3.1
	Geotechnical investigation, geotechnical report, test pits and reinstatement of test pits
	Sum
	 

	 
	 
	 
	 

	 
	[D] TOTAL:
	Sum
	 

	2.4
	SECTIONS OF THE WORKS HIGH-LEVEL ACTIVITIES

	2.4.1
	Zone 1 Unit 1

	2.4.1.1
	Basic Engineering
	Sum
	 

	2.4.1.2
	Detailed Engineering
	Sum
	 

	2.4.1.3
	KKS codification
	Sum
	 

	2.4.1.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.1.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.1.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.1.7
	Quality inspections and testing 
	Sum
	 

	2.4.1.8
	Sectional Commissioning
	Sum
	 

	2.4.1.9
	Professional Engineering Certification
	Sum
	 

	2.4.1.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.2
	Zone 2 Unit 2

	2.4.2.1
	Basic Engineering
	Sum
	 

	2.4.2.2
	Detailed Engineering
	Sum
	 

	2.4.2.3
	KKS codification
	Sum
	 

	2.4.2.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.2.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.2.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.2.7
	Quality inspections and testing 
	Sum
	 

	2.4.2.8
	Sectional Commissioning
	Sum
	 

	2.4.2.9
	Professional Engineering Certification
	Sum
	 

	2.4.2.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.3
	Zone 3 Unit 3

	2.4.3.1
	Basic Engineering
	Sum
	 

	2.4.3.2
	Detailed Engineering
	Sum
	 

	2.4.3.3
	KKS codification
	Sum
	 

	2.4.3.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.3.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.3.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.3.7
	Quality inspections and testing 
	Sum
	 

	2.4.3.8
	Sectional Commissioning
	Sum
	 

	2.4.3.9
	Professional Engineering Certification
	Sum
	 

	2.4.3.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.4
	Zone 4 Unit 4

	2.4.4.1
	Basic Engineering
	Sum
	 

	2.4.4.2
	Detailed Engineering
	Sum
	 

	2.4.4.3
	KKS codification
	Sum
	 

	2.4.4.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.4.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.4.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.4.7
	Quality inspections and testing 
	Sum
	 

	2.4.4.8
	Sectional Commissioning
	Sum
	 

	2.4.4.9
	Professional Engineering Certification
	Sum
	 

	2.4.4.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.5
	Zone 5 Unit 5

	2.4.5.1
	Basic Engineering
	Sum
	 

	2.4.5.2
	Detailed Engineering
	Sum
	 

	2.4.5.3
	KKS codification
	Sum
	 

	2.4.5.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.5.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.5.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.5.7
	Quality inspections and testing 
	Sum
	 

	2.4.5.8
	Sectional Commissioning
	Sum
	 

	2.4.5.9
	Professional Engineering Certification
	Sum
	 

	2.4.5.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.6
	Zone 6 Unit 6

	2.4.6.1
	Basic Engineering
	Sum
	 

	2.4.6.2
	Detailed Engineering
	Sum
	 

	2.4.6.3
	KKS codification
	Sum
	 

	2.4.6.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.6.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.6.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.6.7
	Quality inspections and testing 
	Sum
	 

	2.4.6.8
	Sectional Commissioning
	Sum
	 

	2.4.6.9
	Professional Engineering Certification
	Sum
	 

	2.4.6.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.7
	Zone 7 BOP South

	2.4.7.1
	Basic Engineering
	Sum
	 

	2.4.7.2
	Detailed Engineering
	Sum
	 

	2.4.7.3
	KKS codification
	Sum
	 

	2.4.7.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.7.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.7.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.7.7
	Quality inspections and testing 
	Sum
	 

	2.4.7.8
	Sectional Commissioning
	Sum
	 

	2.4.7.9
	Professional Engineering Certification
	Sum
	 

	2.4.7.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.8
	Zone 8 H-Block

	2.4.8.1
	Basic Engineering
	Sum
	 

	2.4.8.2
	Detailed Engineering
	Sum
	 

	2.4.8.3
	KKS codification
	Sum
	 

	2.4.8.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.8.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.8.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.8.7
	Quality inspections and testing 
	Sum
	 

	2.4.8.8
	Sectional Commissioning
	Sum
	 

	2.4.8.9
	Professional Engineering Certification
	Sum
	 

	2.4.8.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.9
	Zone 9 Admin Building

	2.4.9.1
	Basic Engineering
	Sum
	 

	2.4.9.2
	Detailed Engineering
	Sum
	 

	2.4.9.3
	KKS codification
	Sum
	 

	2.4.9.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.9.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.9.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.9.7
	Quality inspections and testing 
	Sum
	 

	2.4.9.8
	Sectional Commissioning
	Sum
	 

	2.4.9.9
	Professional Engineering Certification
	Sum
	 

	2.4.9.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.10
	Zone 10 Access control

	2.4.10.1
	Basic Engineering
	Sum
	 

	2.4.10.2
	Detailed Engineering
	Sum
	 

	2.4.10.3
	KKS codification
	Sum
	 

	2.4.10.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.10.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.10.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.10.7
	Quality inspections and testing 
	Sum
	 

	2.4.10.8
	Sectional Commissioning
	Sum
	 

	2.4.10.9
	Professional Engineering Certification
	Sum
	 

	2.4.10.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.11
	Zone 11 10 000 Silo

	2.4.11.1
	Basic Engineering
	Sum
	 

	2.4.11.2
	Detailed Engineering
	Sum
	 

	2.4.11.3
	KKS codification
	Sum
	 

	2.4.11.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.11.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.11.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.11.7
	Quality inspections and testing 
	Sum
	 

	2.4.11.8
	Sectional Commissioning
	Sum
	 

	2.4.11.9
	Professional Engineering Certification
	Sum
	 

	2.4.11.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.12
	Zone 12 Plant West

	2.4.12.1
	Basic Engineering
	Sum
	 

	2.4.12.2
	Detailed Engineering
	Sum
	 

	2.4.12.3
	KKS codification
	Sum
	 

	2.4.12.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.12.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.12.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.12.7
	Quality inspections and testing 
	Sum
	 

	2.4.12.8
	Sectional Commissioning
	Sum
	 

	2.4.12.9
	Professional Engineering Certification
	Sum
	 

	2.4.12.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.13
	Zone 13 Coal stockyard

	2.4.13.1
	Basic Engineering
	Sum
	 

	2.4.13.2
	Detailed Engineering
	Sum
	 

	2.4.13.3
	KKS codification
	Sum
	 

	2.4.13.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.13.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.13.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.13.7
	Quality inspections and testing 
	Sum
	 

	2.4.13.8
	Sectional Commissioning
	Sum
	 

	2.4.13.9
	Professional Engineering Certification
	Sum
	 

	2.4.13.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.14
	Zone 14 Ash Plant (out of perimeter fence)

	2.4.14.1
	Basic Engineering
	Sum
	 

	2.4.14.2
	Detailed Engineering
	Sum
	 

	2.4.14.3
	KKS codification
	Sum
	 

	2.4.14.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.14.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.14.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.14.7
	Quality inspections and testing 
	Sum
	 

	2.4.14.8
	Sectional Commissioning
	Sum
	 

	2.4.14.9
	Professional Engineering Certification
	Sum
	 

	2.4.14.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.15
	Zone 15 Raw water dams (Outside perimeter fence)

	2.4.15.1
	Basic Engineering
	Sum
	 

	2.4.15.2
	Detailed Engineering
	Sum
	 

	2.4.15.3
	KKS codification
	Sum
	 

	2.4.15.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.15.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.15.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.15.7
	Quality inspections and testing 
	Sum
	 

	2.4.15.8
	Sectional Commissioning
	Sum
	 

	2.4.15.9
	Professional Engineering Certification
	Sum
	 

	2.4.15.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	2.4.16
	Zone 16 HV Yard (part of outside zone)

	2.4.16.1
	Basic Engineering
	Sum
	 

	2.4.16.2
	Detailed Engineering
	Sum
	 

	2.4.16.3
	KKS codification
	Sum
	 

	2.4.16.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.4.16.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.4.16.6
	Supply, Erection & Installation 
	Sum
	 

	2.4.16.7
	Quality inspections and testing 
	Sum
	 

	2.4.16.8
	Sectional Commissioning
	Sum
	 

	2.4.16.9
	Professional Engineering Certification
	Sum
	 

	2.4.16.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	 
	 
	 
	 

	 
	[E] Total:
	Sum
	 

	2.5
	CIVIL INFRASTRUCTURE AND BUILDINGS  (OUTSIDE ZONE SIREN TOWERS) ACTIVITIES 

	2.5.1
	Basic Engineering
	Sum
	 

	2.5.2
	Detailed Engineering
	Sum
	 

	2.5.3
	KKS codification
	Sum
	 

	2.5.4
	Pre-Factory Acceptance Testing (Pre-FAT)
	Sum
	 

	2.5.5
	Factory Acceptance Testing (FAT) 
	Sum
	 

	2.5.6
	Supply, Erection, Installation & Excavation works 
	Sum
	 

	2.5.7
	Quality inspections and testing 
	Sum
	 

	2.5.8
	Commissioning works
	Sum
	 

	2.5.9
	Professional Engineering Certification
	Sum
	 

	2.5.10
	Sectional Handover including Data Books 
	Sum
	 

	 
	Sub-total:
	Sum
	 

	 
	 
	 
	 

	 
	[F] Total:
	Sum
	 

	2.6
	TRAINING ACTIVITIES 

	2.6.1
	Provide training
	sum
	 

	 
	 
	 
	 

	 
	 [G] Total:
	Sum
	 

	2.7
	PROJECT CLOSE-OUT  ACTIVITIES 

	2.7.1
	Operational Acceptance Test (OAT) 
	sum
	 

	2.7.2
	Site Clearance and De-Establishment completed and accepted
	sum
	 

	 
	 
	 
	 

	 
	 [H] Total:
	Sum
	 

	 
	 
	 
	 

	SUMMARY

	 
	DESCRIPTION 
	CODE
	 AMOUNT  

	1
	PRELIMINARIES AND GENERAL
	[A]
	 

	2.1
	PROJECT INITIATION PHASE ACTIVITIES 
	[B]
	 

	2.2
	EXISTING INFRASTRUCTURE ACTIVITIES 
	[C]
	 

	2.3
	GEOTECHNICAL ACTIVITIES 
	[D]
	 

	2.4
	SECTION OF THE WORKS HIGH-LEVEL ACTIVITIES
	[E]
	 

	2.5
	CIVIL INFRASTRUCTURE AND BUILDINGS  (OUTSIDE ZONE SIREN TOWERS) ACTIVITIES 
	[F]
	 

	2.6
	TRAINING ACTIVITIES 
	[G]
	 

	2.7
	PROJECT CLOSE-OUT  ACTIVITIES 
	[H]
	 

	 
	 
	 
	 

	
	GRAND TOTAL:
	
	


Part 3: Scope of Work

	Document reference
	Title
	No of pages

	
	This cover page
	1

	C3.1
	Employer’s Works Information
	

	C3.2
	Contractor’s Works Information

(insert at award stage or delete if not applicable)
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	Total number of pages
	


C3.1: Employer’s works Information

Contents

Part 3: Scope of Work
44
C3.1: Employer’s works Information
45
1
Description of the Works
48
1.1
Executive overview
48
1.2
Employer’s objectives and purpose of the works
49
1.3
Interpretation and terminology
50
2
Management and start up.
51
2.1
Management meetings
51
2.2
Documentation control
53
2.3
Health and Safety Risk Management
59
2.4
Environmental constraints and management
71
2.4.1
Environmental Management
71
2.4.2
Spillage of Hazardous Chemical Agents
72
2.4.3
Herbicide usage
72
2.4.4
Fire hazard
72
2.4.5
Waste
73
2.4.6
Material requirement
73
2.4.7
Dust and Noise
73
2.4.8
Environmental Incidents
74
2.4.9
Water
74
2.4.10
Environmental file
74
2.4.11
Environmental legislations and other requirements
75
2.5
Quality assurance requirements
75
2.6
Programming constraints
78
2.6.1
General Programme Requirements
78
2.6.2
Commissioning Plan
80
2.6.3
Computerised Planning
80
2.6.4
Planning Methodology and Programme Levels
80
2.6.5
Time Reporting
81
2.6.6
Reporting on Remaining Duration
81
2.6.7
Actual Dates
81
2.6.8
Progress Reporting during Provision of the Works
81
2.6.9
Progress Report
81
2.6.10
Weekly Progress Report
82
2.6.11
Monthly Progress Report
82
2.6.12
Planner Requirements
82
2.7
Contractor’s management, supervision, and key people
83
2.8
Invoicing and payment
83
2.9
Insurance provided by the Employer.
84
2.10
Contract change management.
85
2.10.1
Contract changes and contract Scope
85
2.10.2
Administrative changes
85
2.10.3
Substantive changes
85
2.10.4
General Principles of contract change management.
85
2.10.5
Costs
86
2.10.6
Impact Assessment
86
2.10.7
Project Manager’s right of acceptance of contract changes
87
2.10.8
Contractor’s right of acceptance of proposed changes
87
2.10.9
Emergency Instruction contract changes
88
2.10.10
Authorisation of Contract Change
88
2.10.11
Communications
88
2.11
Provision of bonds and guarantees.
89
2.12
Records of Defined Cost, payments & assessments of compensation events to be kept by the Contractor.
89
2.13
Training workshops and technology transfer
89
3
Engineering and the Contractor’s design
90
3.2
Parts of the works which the Contractor is to design.
90
3.3
Procedure for submission and acceptance of Contractor’s design
91
3.3.1
Submission and Acceptance of Contractor’s design
91
3.3.2
Engineering Changes
95
3.3.3
Engineering Change Procedure
95
3.3.4
Design Change Procedure
95
3.3.5
Procedure for Submission of Change Documents
95
3.4
Other requirements of the Contractor’s design
96
3.4.1
General
96
3.4.2
Other requirements
97
3.4.3
Power Supply interruptions
98
3.4.4
Certificate of Compliance
99
3.5
Use of Contractor’s design
99
3.6
Design of Equipment
99
3.7
Equipment required to be included in the works.
99
3.8
As-built drawings, operating manuals, and maintenance schedules
99
5
Construction
110
5.1
Temporary works, Site services & construction constraints
110
5.1.1
Employer’s Site entry and security control, permits, and Site regulations.
110
5.1.2
Restrictions to access on Site, roads, walkways, and barricades.
110
5.1.3
People restrictions on Site; hours of work, conduct and records.
111
5.1.4
Health and safety facilities on Site
111
5.1.5
Environmental controls, fauna & flora, dealing with objects of historical interest.
111
5.1.6
Title to materials from demolition and excavation
111
5.1.7
Cooperating with and obtaining acceptance of Others
112
5.1.8
Publicity and progress photographs
112
5.1.9
Contractor’s equipment
112
5.1.10
Equipment provided by the Employer.
113
5.1.11
Site services and facilities
113
5.1.12
Supply of Electricity
114
5.1.13
Lighting
114
5.1.14
Water
114
5.1.15
Roads
115
5.1.16
Setting-Out Beacons
115
5.1.17
Facilities provided by the Contractor.
115
5.1.18
Existing premises, inspection of adjoining properties and checking work of Others
116
5.1.19
Survey control and setting out of the works.
116
5.1.20
Excavations and associated water control
117
5.1.21
Underground services, other existing services, cable, and pipe trenches and covers.
117
5.1.22
Control of noise, dust, water, and waste
117
5.1.23
Sequences of construction or installation
118
5.1.24
Giving notice of work to be covered up
119
5.1.25
Hook ups to existing works
119
5.1.26
Communication and Correspondence
120
5.2
Completion, testing, commissioning, and correction of Defects
120
5.2.1
Work to be done by the Completion Date of each section of the works.
120
5.2.2
Use of the works before Completion has been certified.
121
5.2.3
Materials facilities and samples for tests and inspections
121
5.2.4
Commissioning
121
5.2.5
Start-up procedures required to put the works into operation.
123
5.2.6
Take over procedures.
124
5.2.7
Access given by the Employer for correction of Defects.
124
5.2.8
Performance tests after Completion
124
5.2.9
Training and technology transfer
124
5.2.10
Operational maintenance after Completion
125
6
Plant and Materials standards and workmanship
125
6.1
Investigation, survey, and Site clearance
125
6.2
Building works
125
6.3
Civil engineering and structural works
125
6.4
Electrical & mechanical engineering works
125
6.5
Process control and IT works
125
6.6
Other [as required]
126
7
List of drawings
126
7.1
Drawings issued by the Employer.
126
Part 4: Site Information
127
Part 4: Site Information
128
8
Site Information
128
8.1
General description
128
8.2
Existing buildings, structures, and plant & machinery on the Site
129
8.3
Subsoil information
130
8.3.1
Hidden services
130
8.4
Other reports and publicly available information
130


1 Description of the Works
1.1 Executive overview 

Medupi power Station requires the design, supply, erection (and / or installation) and commissioning of a station wide public address (PA) system as part of the emergency preparedness and response plan.

The PA system will primarily be used to broadcast informative and guidance voice instructions during an emergency to ensure correct implementation of the emergency response plan. Also, the PA system can be used to make normal announcements and play background music when required.

The main function of the PA system is to ensure effective communication for all employees, contractors, and visitors during emergency evacuation. System shall be primarily used to provide clear one-way voice communication and audio alarm tones as well as visual indications during an emergency to effect a rapid and orderly evacuation of everyone in response to the emergency.

The system shall be comprised typically of the following sub-systems: 

· Call Stations – consisting of input devices, microphones, etc.

· Redundant network equipment – such as network switches, linking the call stations with the decentralized amplifiers.

· Redundant Amplifiers

· Terminal Units such as horns and loudspeakers. 
· Supporting redundant UPS Power supplies.

Approximately 75% of the Basic Design documentation have been submitted by the previous EPPA supplier and have been accepted by the Employer. The Contractor shall be responsible for the review, evaluation, design, updating and acceptance of existing design documentation. The Contractor shall confirm that its review, evaluation, design, update, and acceptance of the existing and new design assures that the design is in full compliance with the Generic Public Address System Technical Specification Standard (240-161708025) and the technical specification document (348-9971909: Technical Specification for Medupi Power Station Emergency Preparedness Public Address System Project). Any updates and changes to the design documents shall be submitted to Project Manager for acceptance. Once the Contractor has accepted these designs, the Contractor shall take full accountability of these designs.
The redundant backbone fibre optic ring topology network infrastructure required for the EPPA system has been installed already as part of the consolidated building management system (CBMS); however, there might be requirements to install additional fibre optic cables and fibre optic patch leads and related consumables for areas where the installation has not been completed by the CBMS Contractor or in areas where the installed capacity does not meet requirements as set out in this design. An assessment of the then installed capacity and the required additional capacity would need to be completed prior commencement of the detailed design.

There are 16 zones and 60 sub-zones to be designed for which are areas that shall be covered by the PA system as per Table 1: Defined Zones Tables. Also refer to Appendix D of the Specification document 348 -9971909 – Project Drawings – for location drawings of these zones.

Microphones consoles are to be located at the EOC, EOD and Administration Reception desk.

The best suited type of speaker for the location shall be installed at the respective zone or sub-zone.

Power amplifiers shall be available in various modules, e.g. 60, 120, 240, 360, etc. watt RMS, as may be dictated by the loudspeaker load. Amplifiers shall be sized for maximum 80% of rated load, to allow for future additional loudspeakers.

Some network infrastructure and equipment used during the construction phase of Medupi Power Station shall be re-used to the maximum extent possible during the permanent phase. An assessment of the existing infrastructure/equipment and its re- usability needs to be completed before commencement of detailed design; this also should ensure that the re-used infrastructure/equipment can be fully integrated with permanent designed equipment/infrastructure without unnecessary duplication of equipment.

The electrical system design will include interfaces to currently installed electrical systems at interface points or at zonal points as defined in Table 1: Defined Zones Tables also in accordance to provided Limit of Supply and Services (LOSS) Diagrams.

The Battery Backup System – the system shall be equipped with EN54 compliant stand-by batteries to cater for a minimum stand-by period of 24 hours and a continuous broadcast of 30 minutes at full power. The Contractor shall be responsible for sizing, installing and commissioning of the Charger as per the Eskom standard 240-108614750. The technology for the Stand-by batteries shall be Stationary Vented Nickel Cadmium.

Training should be provided as per following training requirements:

· The Provision of detailed training manuals incorporating all aspects of the training that will be provided.

· Formal theoretical training to personnel in the operation, maintenance and general running of the system and equipment before commencing testing and commissioning is required, including training on all required software to operation, maintenance and to perform general running of the system and equipment before commencing testing and commissioning. Software licences are to be handed-over to the Employer as specified in Appendix_A _VDSS of the technical specification document (348-9971909: Technical Specification for Medupi Power Station Emergency Preparedness Public Address System Project). 

· The disciplines to be trained are operating (All shifts=10 personnel, including emergency personnel, reception personnel and security officers), control and instrumentation(C&I) maintenance (6 x personnel) and C&I engineering (4 x personnel).

The overall scope of the Works shall include engineering, design, procurement, manufacturing, factory acceptance testing, and delivery, off-loading at site, storage, installation, testing, commissioning, optimisation, and as-built documentation for the Medupi Power Station’s EPPA systems, to fulfil all the requirements of the Contract and as stated in the specification document (including all appendices) – 348-9971909: Technical Specification for Medupi Power Station Emergency Preparedness Public Address System Project.

1.2 Employer’s objectives and purpose of the works
The purpose of the works is primarily to broadcast informative and guidance voice instructions during the course of an emergency to ensure correct implementation of the emergency response plan. The PA system is to be make normal announcements and play background music when required.

To ensure effective communication for all employees, contractors and visitors during emergency evacuation. System shall be primarily used to provide clear one way voice communication and audio alarm tones as well as visual indications during an emergency so as to effect a rapid and orderly evacuation of everyone in response to the emergency

1.3 Interpretation and terminology

1.3.1 Abbreviations

	Abbreviation & Acronyms
	Description

	BGM
	Background Music

	CBMS
	Centralized Building Management System

	C&I
	Control and Instrumentation

	CMD
	Construction Management Department

	DVC
	Digital Voice Command

	EDWL
	Engineering Design Work Lead

	ECM
	Engineering Change Management

	ECSA
	Engineering Council of South Africa

	EN
	European Norm

	EOC
	Emergency Operations Centre

	EOD
	Electrical Operating Desk

	EPPA
	Emergency Preparedness Public Address System

	FAT
	Factory Acceptance Test

	GenTLC
	Generation Technical Life Cycle

	HMI
	Human Machine Interface

	ISO
	International Standard

	IP
	Ingress Protection

	PA
	Public Address

	PEC
	Professional Engineering Certificate

	PEIC
	Production, Engineering, Integration, Coal

	PS
	Power Station

	PSM
	Power Station Manager

	ROC
	Required Operational Capability

	RTS
	Return To Service

	OHSAct
	Occupational, Health and Safety Act

	SANAS
	South African National Accreditation System

	SANS
	South African National Standard

	SHE
	Safety, Health & Environmental

	SIT
	Site Integration Test

	SRD
	Stakeholders Requirements Definition

	SPL
	Sound Pressure Level

	UPS
	Uninterrupted Power Supply

	mV
	Mill-Volts

	µV
	Micro Volts

	VDSS
	Vendor Documentation Submittal Schedule


1.3.2 Interpretation
	Definition
	Description

	Amplifier
	A device which raises the voltage or current generated by a low-level device such as a microphone to the level necessary to operate the loudspeaker(s). Amplifiers normally have an output voltage of 100 volts

	Background Music
	Refers to the playing of music at a low level to produce a comfortable working ambiance. The volume level at which BGM should be played is important to its effectiveness and should ideally be adjusted so that should the music stop it is not immediately noticeable.

	Controlled disclosure
	Controlled disclosure to external parties (either enforced by law, or discretionary).

	Loudspeaker
	A device which converts electrical energy produced by the amplifier into sound energy. For paging and evacuation purposes they mostly fall into two categories:
· Ceiling type loudspeakers are usually built into wall mounting cabinets and baffles designed for ceiling mounting. This type of loudspeaker is typically used in indoor environments such as offices, passage-ways, shops and waiting rooms.
· Horn type loudspeakers are typically used in industrial environments such as workshops, factories, warehouses and also for outdoor installations.
· Bidirectional speakers
· Cabinet Speakers- Wall/surface mount speakers typically used escape stairs, store rooms and kitchens

	Microphone
	A device which converts sound energy into electrical energy. The output voltage is very low and typically ranges between 0.0001 volts and 0.005 volts (100µV and 5.0mV).


2 Management and start up.

2.1 Management meetings

Meetings will be held monthly between the Project Manager and the Contractor, and any person instructed by the Project Manager to attend. The Contractor is represented at each meeting by the appropriate member of the staff. Additional ad hoc meetings may also be called to address urgent issues.

The Project Manager will, as and when necessary, require the Contractor to attend meetings with Other Contractors on the project. This requirement does not constitute a compensation event.  

The venue for these meetings is as determined by the Project Manager. The Project Manager writes the minutes of meetings and circulates to attendees within five (5) working days.

Any action of the Project Manager and the Contractor implied in the minutes of meetings is confirmed by a separate formal communication between the Project Manager and the Contractor.

The Contractor reports the overall progress and as a minimum requirement, the following is addressed:

a) Contractor’s current activity progress and planned finish dates

b) Contractor’s planned start and finish dates for the works 

c) Contractor and Project Manager’s programme agenda current and projected manpower by class

d) Health, Safety and Quality issues

e) The progress of any other relevant activities

f) Discussion on any technical and commercial issues

g) Problem areas or concerns

Regular meetings of a general nature may be convened and chaired by the Project Manager as follows:

Table 1: Meetings Schedule

	Title and purpose
	Approximate time & interval
	Location
	Attendance by:

	Risk registers and compensation events
	Weekly on Wednesday at Medupi Employer Offices
	Venue determined by the Project Manager 


	Relevant appointed members of a Risk or and Compensation event committee that will include Contractor’s Project Manager,

Construction Manager, Engineering Manager, Quality Manager, Safety Manager, Environmental Manager

	Overall contract progress and feedback
	Monthly 
	Venue determined by the Project Manager
	Employer, Contractor, Supervisor, 

	Overall contract progress and feedback during execution
	Weekly
	Venue determined By the Project Manager
	Employer, Contractor, Supervisor
as determined by the Project Manager

	Planning Meetings
	Weekly 
	Venue determined By the Project Manager
	Employer, Contractor, Supervisor,

Planner and Others as determined by the Project Manager

	Integration meetings with Others 
	Weekly
	Venue determined By the Project Manager
	Employer, Contractor, Supervisor, 

Planners and Others as determined by the Project Manager

	Safety Meetings 
	Monthly
	Venue determined By the Project Manager
	Employer, Contractor, Supervisor
Safety Officers and  

Others as determined by the Project Manager


Meetings of a specialist nature may be convened as specified elsewhere in this Works Information or if not so specified by persons and at times and locations to suit the Parties, the nature and the progress of the works.  Records of these meetings shall be submitted to the Project Manager by the person convening the meeting within five days of the meeting.  

All meetings shall be recorded using minutes or a register prepared and circulated by the person who convened the meeting.   Such minutes or register shall not be used for the purpose of confirming actions or instructions under the contract as these shall be done separately by the person identified in the conditions of contract to carry out such actions or instructions.  

2.2 Documentation control

2.2.1 Submission
All submissions to the Employer, the language of all documentation is to be in English. Documentation submissions shall be through either email or walk-in to documentation centre with CD and/or hard copies. In case submission of documentation is through email, take note of the following:

a)
Email submissions shall be directed to the proxy email and copy all recipient(s) as per the distribution matrix, which will be provided by the Project Manager. 

b)
Use emails strictly as a channel for submitting documentation. 

c)
All information required and intended for use by the Employer, may not be part of the body of the email, one shall document it. 

d)
Email shall not be used as a transmittal; all submissions shall be accompanied by a transmittal slip.

e)
The email subject shall always include the package number/contract number and transmittal number.

Large file transfer: Documentation submission with the file size that exceeds the outlook maximum size of 10MB, Contractor shall submit via the Employer’s large file transfer portal called ZendTo, CD/DVD, and/or hard drives to the Employer project documentation centre. The contractor shall submit data books together with the CD/DVD/USB. Data books shall be split into multiple volumes, to avoid arch lever file overloading . The Contractor shall notify the Employer in advance via email, with the transmittal note attached, to confirm the date, time, and method of submitting large files. Method option may be Datebooks with CD/DVD and/or hard drives, which is a walk into documentation centre or large file transfer portal. 

All submissions, the receiver shall acknowledge by sending back a signed transmittal to the sender within two (2) working days upon receipt. Every submission shall have the pdf version and the native (Editable) version. The file name for both the pdf and the native shall be the same, and as minimum contain documentation number and revision. One shall list all items intended for submission, on the transmittal. 

If the pack contains 10 documentations, therefore the transmittal shall contain 10 items on the list. The listing shall include as minimum item number, documentation number, title, and revision. The example of 10 items, will equate to a pack of 10 pdf files and 10 native files, because each pdf files shall have a native file. 

2.2.2 Identification

Documentation shall have a unique documentation identifier for audit trail. The transmittal shall also have the unique identifier. All other documentation properties shall be on the document; to supplement the document number. Minimum properties that shall be on the document is the package number, contract, revision number, KKS code, functional area (example Unit 1), document type, document status, compiler, reviewer(s), approver, and approval date (Refer to 348-883860 Medupi Format and Layout Specification).

The primary documentation identifier is the Employer documentation management system generated number, except for the drawings. The primary number for the drawing is the Employer drawing number with a prefix of 0.84. Prior submission the Contractor shall request for Eskom drawings number(s), data books and application for inspection numbers from the Employer, to populate on the documentation before submission. The secondary or alternative documentation number is the Contractor documentation identifier. The Contractor shall request pre-allocation of numbers via the pre-allocation form (348-684677). 

All letters exchanged between the Employer and Contractor will contain a secondary numbering system which is sequential, to account for the audit trail. Example, Employer compiled letters shall use this format P00-ESK-MED-0001,

a)
P00 = package number

b)
ESK = Eskom

c)
MED = Medupi

d)
0001 = sequential number.

Contractor format shall be P00-XXX-MED-0001, which is as follows:

a)
P00 = Package number

b)
XXX = Contractor name abbreviation

c)
MED = Medupi

d)
0001 = sequential number.

The Employer will allocate the Employer documentation number upon submission from the Contractor. 
2.2.3 Revision control

Contractor shall use only numeric revision control, and not use alpha or alphanumeric. Contractor may not skip revisions, track internal changes via version control, but submission to the Employer shall maintain a sequential revision control, without skipping numbers. First submission shall be revision 0.

Do not revise a record. A document shall contain revision history. Design/drawing composed of multiple sheets (example sheet 1 to 10); Contractor shall revise all sheets as a batch, even if changes are made to one sheet. The Contractor shall always maintain revision control on the entire batch and submit the entire batch. 

2.2.4 Drawing Management

Use the Employer’s drawing template and ensure that all the fields on the title block are populated and all signatures are completed. Maintain the revision audit trail on the title block. The drawing shall not be submitted as a batch, the contractor shall split the drawing according to their sheet numbers  The last submission of the drawing shall be the final as-built drawing with As-Built Stamp, Professional Engineer’s number and signature. The creation, issuing and control of engineering drawings are in accordance with Employer’s Drawing Standard and Common requirements 240-86973501. The Contractor shall submit as minimum one hardcopy and an electronic copy to the Employer.
The Contractor shall submit editable electronic drawings in Micro Station (DGN) format, and scanned drawings in pdf format. Drawings issued to the Employer shall not be right protected or encrypted as the Employer has to do the necessary configuration management on these documents upon receipt. Electronic drawings shall have a water mark indicating the approval phase of a drawing and hardcopies shall be stamped to indicate the phase. 

Any additional drawings requested by the Employer do not constitute a compensation event. All drawing types including but not limited to the following (General arrangement, Isometrics, P&IDs, detail drawings) are submitted in the following formats:

a)
One (1) hard copy.

b)
One (1) electronic copy in pdf format

c)
One (1) electronic copy in the native CAD format, preferably dwg format

Drawings are submitted in sufficient time to permit reviews, comments and/or modifications being made, if such are considered necessary by the Project Manager, without delaying the Contract Delivery and Completion Dates.

2.2.5 Reports
The Contractor shall submit the vendor documentation submission schedule for review to the Employer within thirty (30) days after the contract is awarded. After being informed of the decision to accept or reject the schedule, the Contractor revises and submits the updated schedule within forty-eight (48) hours. The VDSS is revisable, and one shall discuss any change to reach agreement between all parties, and then properly document the changes. If there is a change in the previously approved and/or issued VDSS, a Change Procedure shall be followed as all times. Changes in the VDSS may include additional documentation for submission; submission dates; documentation descriptions and document numbers; etc. The Contractor shall be responsible for the management of the schedule. 

The Contractor shall compile a documentation register, to track the documentation submission progress, in line with Contractor-committed dates on the VDSS. The register for tracking submission progress is the master documentation list (MDL); Contractor shall submit it monthly to the Employer. The MDL shall contain an audit trail of all submitted documentation, all historic documentation revisions, and current revision.

2.2.6 Retention of Documentation 

The Contractor shall retain all documentation which are specified on the VDSS, this includes data books, for a minimum of ten (10) years post contract close out in line with the Rules of Conduct for Registered Persons, Engineering Professional Act, paragraph 4(a): “Registered Persons, may not without satisfactory reasons destroy or dispose of, or knowingly allow any other person to destroy or dispose of, any information within a period of ten (10) years after completion of the work concerned.”

The retained documentation shall be kept electronically in the Contractor’s documentation management system. The Contractor shall also keep the original ink signed hard copies for the minimum of ten (10) years post contract close out.  

When the ten (10) years comes to an end, the Contractor shall inform the Employer in writing prior to disposal, to confirm if the Employer is not in need of any documentation. The correspondence shall include the master documentation register which outlines all retained documentation. It is the Contractor’s responsibility to ensure that the correspondence has reached the Employer, by requesting acknowledgement of receipt. The Employer has the maximum of six (6) months to respond in writing to the Contractor, failure to do so, the Contractor may proceed and dispose the documentation after the six (6) months has passed. 

2.2.7 Governance

Contractor shall comply with the following governance documentation: 348-883860: Medupi Format and Layout Specification; 348-883808 Medupi Document and Records Management Work Instruction; 348-883753 Project Data Capturing Guideline ; 240-86973501 Engineering Drawing Standard; 348-885429 Engineering Change Management Work Instruction; 36-943 Engineering Drawings Office and Engineering Documentation Standard; 240-53114186 Eskom Project/Plant Specific Technical Document and Records Management Procedure, 240-83561037 Reporting and Data Requirements Specification for Contractors, 240-53113685 Generation Design Review Procedure, 474-1325-Design Review Procedure_Rev_1,348-942820 Transmittal Template, 200-616427 Data Book Checklist.

2.2.8 Configuration Management 

The Contractor to prepare a configuration management (CM) plan utilizing ISO 10007 as a reference guide for the technical specification document. The CM plan shall include the following:

The process of managing documentation for the works will be supported by the following.

a)
According to process functions: All plant shall be coded to KKS Breakdown Level 3.  

b)
According to points of installations: Electrical and instrumentation devices installation units (e.g. cabinets, panels, consoles) shall be coded to KKS Breakdown Level 3. 

c)
Location codes: Plant structures shall be coded to KKS Breakdown Level 2. 

d)
Cables coding: Cables shall be coded with either source or destination equipment KKS code followed by sequential four-digit number and optional four alpha numeric characters. 

The Contractor to codify all equipment, and any components which are required to be codified as per the guidelines and standards referenced in this document. The Contractor to indicate equipment and component codification in drawings and documents indicating or referencing such plant.

The Contractor to submit all KKS codes designated by the Contractor in an equipment list format with equipment descriptions, the documents in which they were originally designated, to the Employer for review. Any description abbreviations shall be done according to the List of Abbreviations (200-24473). 

The Contractor will remain responsible for ensuring that the codes designated are unique, not duplicated and meet the requirements established by the various standards applicable to the project. Where any ambiguities or doubts with regards to KKS codification exist, the Contractor shall engage the Employer for resolution.

2.2.9 Plant Labelling and KKS Classification

The KKS system is used by the Contractor for classification and designation of both plant and associated documents. The Contractor uses Employer-specific interpretations of the KKS standards, which will be reviewed and agreed upon after Contract Date.

The Contractor shall manufacture and install labels according to the Medupi Label specification 2003340.

Any abbreviations to plant descriptions shall be prepared in accordance with the Employer’s abbreviation standard 200-24473. 

Detailed name plate or label lists with the service legends and including the KKS code shall be prepared by the Contractor and submitted to the Employer for review and comment before commencing the manufacture of the labels. On plant areas where labels do not make ergonomically sense please consult site configuration management for guidance.

2.2.10 Data

The Contractor supplies the descriptive data including the following but not limited to equipment list, price schedules, and speciality item lists in Microsoft Excel compatible to the Employer’s latest version.  Compliance to this requirement does not constitute compensation event. The lists contain the following fields for each item as a minimum:

a)
Functional location

b)
Tag ID (consistent with the Employer Specification) 

c)
Description

d)
Associated drawing and document names (that contain references to this item)

2.2.11 Documentation to be supplied by the Contractor. 
The following documentation and including documentation stated in the VDSS shall be supplied to the Employer by the Contractor as a minimum where applicable:

a)
All engineering clearance charts.
b)
Technical specifications for the spares, part numbers and the stock levels required

c)
Commissioning procedures

d)
Performance test procedures

e)
Installation reports 

f)
Supply of end of manufacturing reports for all components

g)
Documentation for new/modified auxiliaries

h)
List with new components KKS numbering 

i)
As-built drawings:

i.
Single line drawings

ii.
Works Information 
iii.
Schematic drawings

iv.
Operating philosophy

j)
Quality control plan

k)
Installation procedure

l)
Maintenance manual

m)
Operating manual

n)
Technical manual

o)
Instruction manuals and/or catalogues 

p)
List of recommended spares

q)
Test procedure, certificates and/or report

r)
Test instruments calibration certificates

s)
Design review packages

At the end of the process design phase, the Contractor is expected to deliver the following updated documentation specific to the works:

a)
Piping and instrumentation diagrams (P&ID’s)

b)
Valve lists

c)
Instrument schedule

d)
Control narrative

e)
Operating philosophy

f)
Design calculations (i.e., NPSH, velocity, pressure drop/ 100m etc.)

g)
Hydraulic model input file, results, and report

h)
HAZOP study report

i)
FMECA study report

j)
Reliability, availability and maintainability (RAM) study Report

k)
Equipment data sheets

l)
Loading calculation

At the end of the mechanical design phase, the Contractor is expected to deliver the following updated documentation specific to the works:

a)
Plot plans and GA drawings showing the positions of all pipes supports, and details of the supports

b)
Isometric drawings for the pipeline, and piping accessories

c)
Mechanical design calculations and any model input file, and reports

On completion of the C&I design the Contractor shall submit the following documentation to the Employer for approval.

a)
Instrument location diagram 

b)
Signal list

c)
I/O block diagram

d)
Control narrative or detailed functional description

e)
Alarm list and rationalization 

f)
Functional block diagram (FBD)

g)
Instrument data sheets

The Contractor is also required to submit steel grade certificates, fabrication drawings, welder’s certificates and quality and test plans for review prior to fabrication.

Once the construction work is completed, the Contractor’s designer will issue the necessary certificates (inclusive of geotechnical and structural PE certificates) and as-built documentation (drawings, native files as well as structural and foundation design reports that includes all calculations).
2.3 Health and Safety Risk Management
The Contractor shall comply with the health and safety requirements contained on the Occupational Health and Safety Act (OHSA Act 85 of 1993) and its Regulations, Employer policies and procedures as well as contract requirements. It is essential that the Contractor is conversant with Employer safety procedures training prior commencing any work on site. Failure to comply shall result in the Employer suspending execution of services and removing the Contractor from site until compliance is achieved. The Employer may terminate the contract depending on the situation and risks to people, plant and equipment, reputation and the Employer’s business of electricity supply. 

The Contractor, shall always, consider itself to be the “Employer” for the purposes of the OHSA and shall not consider itself under the supervision or management of the Employer regarding compliance with the SHEQ requirements. The Contractor shall furthermore not consider itself to be a subordinate or under the supervision of the Employer in respect of these matters. The Contractor is always responsible for the supervision of its employees, agents, suppliers, Contractors, and mandataries and takes full responsibility and accountability for ensuring they are competent and aware of the SHEQ requirements and execute the works in accordance with the SHEQ requirements.

Should the Contractor appoint Contractors the Subcontractors shall carry responsibilities of a client as per Construction Regulation 2014.

The Contractor shall ensure that all statutory appointments and appointments required by the management system are in place, and that all appointees fully understand their responsibilities and are trained and competent to execute their duties. The Contractor supervises the execution of their duties by all such appointees.

The Contractor shall appoint a safety officer who will be responsible for the premises relevant to this contract and liaise with the Employer safety department accordingly to ensure compliance to health and safety requirements. As a minimum the appointed safety officer should have a National Diploma – Safety management or environmental health and be registered with SACPCMP. 

The Employer, or person appointed by the Employer, may at any stage during the period of this contract:

a)
Conduct health and safety audits regarding all aspects of compliance with the SHEQ requirements, at any off-site place of work, or the site establishment of the Contractor.

b)
Refuse any employee, Subcontractors or agent of the Contractor access to the premises if such person has been found to commit an unsafe act or any unsafe working practice or is found not to be qualified or authorised in terms of the SHEQ requirements.

c)
Issue the Contractor with a stop order should the Employer become aware of any unsafe working procedure or condition or any non-compliance with any provision of the SHEQ requirements.

The Employer expects the Contractor to engage in safety culture initiatives in line with the Employers SHEQ policy and value, Zero Harm.

The Contractor shall implement their OHS management system and requirements and incorporate the applicable Employer requirements into their system.

2.3.1
Compliance with Legislation and other requirements

It is required that all contractors on the project comply with the relevant applicable legislation and any other changes in legislation, specifications, and standards in accordance with the scope of the project. 
It is the duty of the Contractor to ensure that they are familiar with the necessary OHS legislation required. Applicable acts/regulations should be displayed or available for employees, client and inspector when required. 

When there is an amendment to acts and/or to the regulations, the OHS plan shall be reviewed, updated accordingly, and send through to the client. Changes shall be communicated to all relevant employees.

2.3.2
SHE Induction and Access to Site

All the employees of the Contractor shall attend the Employers SHEQ induction course provided by the Employer before commencement of the works will be allowed on the Site. It is the responsibility of the Contractor to ensure that all employees have attended the safety induction. Contractor shall further develop and train all its employees on company specific SHEQ induction. Proof of yearly induction should be always easily identifiable/available. Only once this induction has been received, will each employee receive a site access permit. 

2.3.3
Designer: Roles, Accountabilities and Responsibilities

A designer is the person responsible for the overall management of the project design as well as ensuring the management of the compliance of the completed works to the design during and after construction on site. 
Designers should ensure compliance with the Occupational Health and Safety Act in terms of Construction Regulations of 2014, Regulations 6, and all other applicable regulations, standards and legislations. 

The designer shall consider the hazards associated with the future maintenance of the designed structure(s) and make provision in the design(s) for the necessary maintenance work to be performed such that the associated risks are minimised. 

Designers should ensure that when they design for construction work they consider foreseeable health and safety risks during construction and eventual maintenance and cleaning of the structure in the balance with other design considerations, such as aesthetics and cost.

Inform the Employer in writing of any known or anticipated dangers or hazards relating to the works and make available all relevant information required for the safe execution of the works upon being designed or when the design is subsequently altered.

The designer should apply the hierarchy of risk control. This means designers need to identify the hazards inherent in carrying out the works and where possible alter the design to avoid them. If the hazards cannot be removed by design changes, the designer should minimize the risks and provide information about the risks that remain.

Make available in a report to the Employer all relevant health and safety information about the design of the relevant structure, geotechnical science aspects where appropriate and the loading structure is designed to withstand.

Designer should describe any matters that require particular attention by a Contractor. Enough information should be provided to alert Contractors and Others to matters which they could not be reasonably expected to know about.

Take into consideration and ensure compliance of health and safety specification. 

In cases where the Employer uses offshore designers, the appointed designers shall indicate and submit to the Employer the legislative requirements/documentation with which they comply to verify whether they meet the South African SHE legislative requirements.

An offshore designer can appoint a local designer to conduct the inspections required by the construction regulations.

Designers shall communicate changes with the Project Manager on designs that affect environmental authorisations/approval issued. Final designs and layout maps shall be approved by relevant authorities before the commencement of the works.

2.3.4
Contractor: Details, Accountabilities and Responsibilities

The Contractor carries primary accountability and responsibility for the health and safety of his/her employees within his/her working area, as contemplated by Section 37(2) of the OHS Act No. 85 of 1993 and Regulations. None of the additional safety requirements specified by the Employer reduces the Contractor’s accountability and responsibility for the health and safety of his employees within his working area.


The Contractor shall have a disciplinary process and an organisational structured procedure to deal with employees who have transgressed organisational and legal requirements.

The Contractor shall provide a list of names and contact telephone numbers of all his employees on site. This list shall be updated as and when new employees commence on site.

The Contractor shall keep a record of all employees, including date of induction, relevant skills, and licenses, and be able to produce this list at the request of the relevant officials. These records shall be filed in the OHS file.

Employees are responsible for their own health, safety, and that of their co-workers in their respective areas of work on the project. 

Employees shall be made aware of their responsibilities during induction and awareness sessions some of which are:

a)
Familiarising themselves with their workplaces and health and safety procedures.

b)
Working in a manner that does not endanger them or cause harm to Others.

c)
Keeping their work area tidy.

d)
Reporting all incidents/accidents and near misses. 

e)
Protecting fellow workers from injury.

f)
Reporting unsafe acts and unsafe conditions.

g)
Reporting any situation that may become dangerous.

h)
Carrying out lawful orders and obeying health and safety rules.

i)
Declaring to the Employer if taking medication, which may have intoxicating effects. 

j)
If an employee has a reasonable belief that the work to be undertaken is likely to endanger him/her or any other person/s due to sub-standard acts or conditions, inadequate precautions or a lack of protective equipment or clothing, he/she has the right to refuse to work and shall report such situation to the Employer.

k)
An employee does have the right not to work in any area or perform any task where that employee has reasonable justification to believe that the work situation presents a danger to his/her health and safety, organizational assets or the environment.

It shall be highlighted to all employees, that anyone who becomes aware of any person disregarding a health & safety notice, instruction or regulation shall immediately report this to the person concerned. If the person persists, stop the person from working and report the matter to the Project Manager immediately.

The Contractor appointed personnel shall be registered in their respective levels as professionals in terms of the legislative requirements (SACPCMP).

OHS professionals (which include safety officers) are required to register as professionals with the SACPCMP.

2.3.5
SHE Competency and organogram

The Contractor is required to compile their company organogram for the contract, highlighting the reporting structure from their senior management down to their project employees. This diagram shall be kept up to date, a copy of which shall be given to the Employer and copy filled in the relevant project SHE files.

The Contractor shall appoint a safety practitioner(s)/officer(s) with a minimum of a national diploma in safety management or environmental related courses and be registered with the SACPCMP.

2.3.6
COID and UIF requirements

The Contractor shall be registered with an appropriate employment compensation commissioner and submit proof of good standing with the commissioner. The Contractor shall, before the commencement with work on site, furnish the Employer with proof of a valid registration through a certificate of good standing in terms of the Compensation for Occupational Injuries and Diseases Act, (COID Act), 130 of 1993 and that all payments due to the commissioner are discharged. This cover shall remain in force during the contract and shall be the responsibility of the Contractor to ensure validity. The letter of good standing shall reflect the name of the Contractor. 
2.3.7
Occupational health and safety policy

The Contractor shall have an OHS/SHEQ policy authorised by their chief executive (OHS Act Section 16(1) appointee) that clearly states overall SHEQ objectives and commitment to improving safety and health of its employees. The policy should outline the arrangements for carrying out and reviewing that policy.

The Employer has a SHEQ Policy (32-727) that clearly states the policy principles by which the Employer operates and the commitment to SHEQ excellence and is authorised by the chief executive. 

Contractors shall support the Employer SHEQ policy. 
2.3.8
Mandatory agreements

A Section 37(2) agreement shall be signed between the Employer and the Contractor at the time of awarding the contract. A signed copy of this agreement is submitted to the Employer prior to commencement of any activity on site. The Contractor shall ensure that a section 37(2) agreement is signed between them and all their appointed Subcontractors for the contract.

Copies of all agreements shall form part of the Contractor’s OHS file.

2.3.9
Annexure B: Eskom SHE Rules and Requirements

Annexure B is the acknowledgement of the Employers SHE rules, and requirements form signed and submitted by the Contractor.

2.3.10
Health and safety (SHE) file 

The Contractor shall compile a SHE (Safety, Health and Environmental) file as per Employer’s safety file requirements. The Contractor shall also ensure that the health and safety file; which shall include all documentation required in terms of the provisions of act and these regulations; is opened and kept on site and made available to an inspector and/or the Employer upon request. 
The Contractor at the end of the project shall submit health and safety file to the Employer. 

2.3.11
Health and safety management plan

The Contractor shall provide and demonstrate to the Employer a suitable and sufficiently documented health and safety plan, based on the Employer’s health and safety specification contemplated in regulation 5(1)(b) provided by the client.

The Contractor shall use the applicable OHS information to develop a suitable and sufficient OHS plan, submitted with the tender documents, which will indicate to the Employer the level of compliance to the OHS Act 85 of 1993 and its Regulations and other requirements. The occupational health and safety plan shall identify each activity to be undertaken by the Contractor, the foreseeable internal and external hazards, the specific precautions, and controls that shall be necessary to ensure that the works proceeds safely and without risks to health or adjacent operations.

Upon discussions with the Contractor, a final accepted OHS plan would be signed and approved. 

The plan shall demonstrate the Contractors management commitment to OHS.

The safety plan shall be reviewed to ensure that it fully addresses all the issues and complies with the requirements of the OHS specifications and contract. If necessary, the Contractor shall amend the OHS plan as required by the Employer.

2.3.12
Hazard identification and Risk assessment

It is a legal requirement in terms of Section 8 (2)(d) of the OHS Act for an Employer to continuously carry out risk assessments, to establish which risks and hazards are attached to the health and safety of persons due to any work which is performed, any article or substance which is, handled, stored, transported.

The Contractor shall prepare and provide to the Employer a baseline risk assessment as well as activity-based risk assessment for an intended work. 

2.3.13
Provision for Cost of Health and Safety measures

The Contractor shall ensure that there is provision for the cost of occupational health and safety measures.

Note: the costing for OHS shall be detailed, that is itemised based on the overall scope of the project (i.e., medical surveillance (Medicals), training, provision of PPE, Disaster, and communicable diseases (COVID-19) compliance, safety equipment purchases, resources, occupational health, and occupational hygiene   stressors surveys and etc). 
2.3.14
Medical programs

The Contractor shall ensure that the employees are registered on a medical surveillance programme and are in possession of a valid medical fitness certificate, completed in South Africa. The certificate of fitness should be relevant to the type of work (risk based) that the employee will be exposed to. This will require each employee to have a risk-based person job specification that will be used as a basis for medical examination.

The Contractor shall ensure that his employees have undergone pre-entry medical examination before starting work on site. No employee will access site without a valid medical fitness certificate. Periodic medical examination shall be done for all employees as work progresses. Upon completion or as and when employees’ leave the project, an exit medical examination shall be done for all employees involved in the project. No employee shall leave the project without having completed and submitted exit medical certificate to the Employer. 
2.3.15
Emergency Care

The Contractor shall develop emergency procedure in line with the Employers emergency protocols. Contractor shall further ensure that emergency response service is always available to attend to any emergency cases that may arise during the duration of the contract. 

The Contractor shall be responsible to familiarise himself with local municipal disaster management portfolios. 
A list of emergency numbers shall be displayed at notice boards and public areas for ease of access to all employees and visitors. The Contractor shall ensure that his employees are familiar with the emergency numbers. Emergency numbers will also be part of the OHS induction.

Contractor shall have one first aid box for the first five (5) persons and thereafter one for every fifty (50) or team of workers on site or part thereof. There should be a trained and appointed person to render first aid service when required. The first aider(s) shall be in possession of a first aid level two (2) training as minimum requirement as per Employer’s emergency planning procedure 32-123.

More first aid boxes shall be provided if the risks, distance between work teams or workplace requirements require it (it should be available and accessible for the treatment of injured persons at that workplace).

Minimum contents of a first aid box: (Refer to GSR 3 Annexure of the OHS Act).

A prominent notice or sign shall be erected in a conspicuous place at a workplace (SANS1186 approved signs to indicate location of first aid boxes), indicating where the first aid box or boxes are kept as well as the name and contact details of the first aider of such first aid box or boxes.

The Contractor shall ensure that alternative arrangements shall be made for possible incidents occurring after normal working hours.

2.3.16
Employers’ Lifesaving Rules

The Contractor shall comply with the Employers lifesaving rules. Violation of these rules will be viewed in a serious light and the consequences will be dealt with via the respective disciplinary processes. 
Five (5) lifesaving rules have been developed that will apply to all Employer employees, agents, Contractors, consultants, suppliers, and visitors. Failure to adhere to these rules will be considered a serious transgression. These rules are being implemented to prevent serious injury or death of any employee, labour broker or Contractor working in any area within the Employer.
Employer lifesaving rules are non-negotiable health and safety rules which shall not be broken under any circumstances.  It shall be highlighted that the Employer takes a ZERO TOLERANCE stance to violation of these rules. These rules are applicable to any person entering the Employers sites.
The rules are as follows: 

	Rule 1
	OPEN, ISOLATE, TEST, EARTH, BOND AND/OR INSULATE BEFORE TOUCH

Any person who performs work on an electrical installation shall ensure that it is isolated, tested and earthed before starting any work. Contractor is to provide the Responsible Person (RP) as required.  
(That is plant, any plant operating above 1000 V)

No person may work on any electrical network unless:

· He / she is trained and authorised as competent for the task to be done.

· A pre-task risk assessment to identify all risks and hazards shall be conducted prior to any work commencing. 

· An equipotential zone is created for each worker on the job site by earthling, bonding and/or insulating according to approved divisional procedures.

· All conducting material is connected, all staff onsite wear electrical safety shoes and insulating techniques are applied according to standards. 

· The authorised person (Team leader) has certified and shown all team members that the apparatus is safe to work on. He / she is trained and authorised as competent

	Rule 2
	HOOK UP AT HEIGHTS

Working at Height is defined as any work performed above a stable work surface or where a person puts himself/herself in a position where he/she exposes himself/herself to a fall from or into. A pre-task risk assessment to identify all risks and hazards shall be conducted prior to any work at height commencing.

	Rule 3
	BUCKLE UP

Seatbelts shall be always used whilst driving. No person may drive any vehicle on Eskom business and/or on Eskom premises: Unless the driver and all passengers are wearing seat belts.

	Rule 4
	BE SOBER

No person is allowed to be under the influence of intoxicating liquor or drugs while on duty.

Under-the-influence’ means the use of alcohol, drugs and /or a controlled substance to the extent that:

·  the individuals’ faculties are in any way impaired by the consumption or use of the substances or.

·  the individual is unable to perform in a safe, productive manner or.

·  the individual has a level of any such substance in his body that corresponds with or exceeds accepted medical/legal standards or.

·  the individual has a level of alcohol in his body that is greater than 0,00 % blood alcohol concentration.

·  Any level of an illegal substance in the body irrespective of when the substance was used

	Rule 5
	PERMIT TO WORK

Where an authorisation limitation exists, no person shall work without the required Permit to Work (PTW).

· Work is as defined in the Plant Safety Regulations (OHS) and Operating Regulations for High Voltage Systems (ORHVS) of Eskom.

· A Risk Assessment shall be carried out jointly by the Authorised (AP) and Responsible Person (RP) on all work before it commences.

· The PTW shall be issued by an AP, in accordance with the PSR.

· The PTW shall be accepted in writing by an authorised RP.

· The PTW shall be shown to everyone working on the job and the risks explained.

· The RP shall ensure that all staff working on that job are entered on a Workers’ Register and the risks explained to each one.

· The RP shall ensure that the conditions of the PTW are enforced for the duration of the work.


2.3.17
Personal Protective Equipment (PPE)

In terms of Section 8 of the OHS Act, the duty of the Employer is to take steps to eliminate or mitigate (hierarchy of control measures) any hazard or potential hazard to the safety or health of employees before resorting to PPE.

Contractor’s employees on site, including visitors, shall use SANS always approved risk-based PPE, as a minimum: 

a)
Head protection hard hat (with chin straps).

b)
Steel toe capped safety boots.

c)
Eye protection. Wearing of impact Safety Spectacles with side shields. Prescription glasses shall comply with the same standard or cover impact safety spectacles shall be worn over them. 

d)
Long sleeved and long pants protective clothing.

e)
High visibility vests.

f)
Dust mask and/or cloth masks.

g)
Refer to General Safety Regulation 2 of the OHS Act.

The Contractor shall ensure that his employees understand why the personal protective equipment is necessary and that they use them correctly. Training should be provided to employees on the use, care, replacement, and limitation of the provided PPE. Records of training to be kept and made available to the Employer or inspector upon request.

Strict non-compliance measures shall be administered to any employee not complying with the use of PPE and that employee shall be removed from the Site.

Note: Certain areas will be subjected to specific/extra PPE requirement.

2.3.18
Health Pandemics and Disaster Management

The Contractor shall ensure proper management and control of any disaster and or pandemics that may come forth during the contract.   

2.3.19
BBSO Behavioural Based Safety Observation (BBSO)

Contractor shall incorporate BBSO or VFL (Visible Felt Leadership) programmes within their health and safety management system.

The objective of behavioural safety observations is to assess and address the actual safe and unsafe behaviours of people in the workplace; as well as workplace conditions - which are caused by the actions or non-actions of employees, Contractor, or their workers. 
2.3.20
Employees’ Right of refusal to work in an unsafe situation.
Employees have a duty to take reasonable care of their own as well as other person’s health and safety at work and to cooperate with the Employer, carry out lawful orders, including reporting unsafe situations and incidents.

Refer to Employer’s procedure 240-43848327- Employees’ right of refusal to work in an unsafe situation. The aim of the procedure is to ensure that an environment is created that promotes zero harm by empowering employees and Contractors to take responsibility for their own safety and that of Others.

2.3.21
OHS Audits

During this contract, the Contractor shall be subjected to scheduled or monthly audits by the client to monitor compliance.

The Employer reserves the right to monitor and conduct unannounced audits to ensure compliance and provide assurance to the Employer’s representatives and their key stakeholders.

2.3.22
Incident management

The Contractor shall report and investigate all incidents/accidents as required in terms of the legislation.

All incidents reporting, recording, classification and investigation will be done according to the requirements set out in the Employer’s document 32-95 (latest revision).

2.3.23
OHS Performance Status Reports

The Contractor shall provide OHS statistical and non-statistical reports, dashboards, presentations on weekly and monthly basis.

2.3.24
Meetings

The Contractor shall attend the monthly safety meeting scheduled by the Employer. Ad-hoc meetings shall be scheduled to address any health and safety related issue.

2.3.25
Work Co-ordination/interface Process

Work coordination process is designed for monitoring and coordination of activities for Contractors working within the same area. It allows work to proceed without risk to the health and safety of Contractor personnel, visitors, principal Contractors, and client personnel.  

The following shall be taken into consideration:

a)
Whenever there is more than one Contractor working in one area there shall be a documented interface process.

b)
Where there are agreements between different Contractors, those agreements shall be written and signed off by the client and site/plant owner.

c)
It is crucial that there is link between the risk assessment required for the permit to work in terms of PSR (Plant Safety Regulations) and the task risk assessment, as these risk assessments identifies critical controls required to execute the work.

2.3.26
Housekeeping

The Contractor shall maintain a high standard of housekeeping within the site. Prompt disposal of waste materials, scrap and rubbish is essential.

The Employer requires the Contractor to conduct housekeeping daily and perform housekeeping inspections (at least weekly) to ensure maintenance of satisfactory standards. The Contractor shall document the results of each inspection and shall maintain records for viewing.

Housekeeping shall be done before and after every shift. After completion of every task, the Contractor shall conduct a proper housekeeping and keep evidence of housekeeping in that area.

Note: Nails protruding through timber shall be bent over or removed so as not to cause injury.

In cases where an inadequate standard of housekeeping has developed, compromising the health, safety and cleanliness, all employees have the responsibility to bring it to the attention of the Employer. The Employer will have the authority to instruct the suspension of relevant works until the area has been tidied up and made safe. Neither additional cost nor extension of time to the Contract shall be allowed because of work stoppage.

Emphasis on housekeeping and general safeguarding on construction site CR 27 and stacking and storage on construction site CR 28 is mandatory and shall be always complied with.

2.3.27
Inspection Colour Codes

The below table should be used for colour coding on site for monthly and quarterly inspections on tools and equipment. Material to be used on colour coding should be cable ties. The colour coding should be implemented as soon as on the first day of the respective month. Previous month colour coding should be removed and replaced with new ones for the present month. Wrong colour coding on tools and equipment shall be deemed as proof that inspection was not conducted for the month on that item. Colour coding does not replace the need of daily inspection checklist being conducted daily and kept in the file on site.

	Monthly Inspection Colour lode
	Quarterly Inspection Colour Code 

	January
	Blue
	Blue
	January
	Green

	February
	
	White
	February
	

	March
	
	Black
	March
	

	April
	Grey
	Grey
	April
	Red

	May
	
	White
	May
	

	June
	
	Black
	June
	

	July
	Pink
	Pink
	July
	Blue

	August
	
	White
	August
	

	September
	
	Black
	September
	

	October
	Brown
	Brown
	October
	Yellow

	November
	
	White
	November
	

	December
	
	Black
	December
	


2.3.28
Work Stoppage

The temporary stoppage of an activity/activities or task(s) may be because SHE concerns, including the following circumstances which shall not warrant any financial compensation:

a)
Ad hoc safety intervention (safety stand-down/work stoppage) by Employers management: All work of a similar nature may be stopped as the result of an occurrence of a serious incident.  The Contractor shall be required to comply with, and/or verify, the conditions stipulated in the work stoppage instruction pack.

b)
Ad hoc safety intervention by any person, especially SHE functionaries, may be due to unsafe work or unsafe behaviour by the Contractor. The conditions that gave rise to the work stoppage will determine the corrective measures to be taken urgently to protect the health and safety of employees and protect the environment and plant or equipment, etc.

NOTE: Work stoppages that are initiated because of SHE related incidents shall not warrant any financial compensation claim lodged against the Employer.

Further note the Employer do have two (2) compulsory work stoppages per annum. Safety discussions will be held on those days and no financial compensation claim lodged against the Employer. This is in line to support the Employers safety culture of Zero Harm.

2.3.29
Hours of Work

All work conducted on site shall fall within the legal requirements in accordance with the Basic Conditions of Employment Act. 

The Contractor will notify the Employer of any work that needs to be performed after hours according to the agreed arrangements. (The application needs to be submitted timeously). Where applicable, the notification should include proof of application, for overtime, to the Department of Employment and Labour and/or the letter of approval from the Department of Employment and Labour.

2.3.30
Project Close-out

On completion of the project or service rendered, the Contractor shall close out their project documentation and OHS files and handover to the Project Manager. All required documentation shall be submitted and handed over to the Employer using relevant medium as per the procedure (Project Closeout and H&S documentation, 348-9942695). A checklist shall accompany the submission to verify that all documents are submitted/or handed in to the Employer.

2.4 Environmental constraints and management

2.4.1 Environmental Management
The Contractor shall comply with the Projects’ Environmental Management Plan (EMPr), Environmental Authorisations, Licences, permits and other related requirements.

Minimum requirements for compliance by Contractors:

· Ensure that the Method Statements are submitted to the TM/ECO for approval/acceptance before any work is undertaken. Any lack of adherence to this shall be considered as non-compliance to the specifications.

· Ensure that any instructions issued by the Engineer, on the advice of the ECO, are adhered to.

· Contractor shall maintain the environmental legal register.

· Ensure that there shall be communication tabled in the form of a report at each site meeting, which shall document all incidents that have occurred during the period before the site meeting.

· Ensure that a register is kept at the site office, which lists all the transgressions issued by the ECO.

· Ensure that a register of all public complaints is maintained. 

· Ensure that all employees, including those of sub-Contractors receive training before the commencement of construction in order that they can constructively contribute towards the successful implementation of the environmental requirements of the Contract.

· Ensure compliance with the environmental requirements, relating to the provision of adequate resources for the implementation and monitoring of the requisite environmental controls.

· Compile an Environmental monitoring plan outlining all the construction activities, associated environmental impacts and how they shall be mitigated.

· Ensure that the project pricing makes provision for environmental costs.

· Contractor shall attach a company waste management plan including the typical waste inventory and templates used for keeping waste records.

· Include environmental considerations as an item on the agenda of the monthly site meetings.

· Compile and implement the necessary Method Statements; and undertake environmental awareness training of all site staff during the commencement of each Contract, with regular refreshers for the duration of the Contract.

· Appropriate measures shall be undertaken to minimise the generation of dust from work activities. 
· The work area is kept clean, tidy, and free of waster/rubbish. Waste shall be disposed of in designated bins. 
· Adherence to current and amended Water Use License and Regulation 704 of the National Water Act (Act 36 of 1998).

· Plant and machinery shall be equipped with drip trays. Oil refills for plant and machinery shall take place in designated areas.

Ensure that the environmental authorizations required in terms of National Environmental Management Act, 1998 (section 24) are sought prior to storage of dangerous goods, including petrol, diesel, liquid petroleum gas or paraffin.

2.4.2  Spillage of Hazardous Chemical Agents

· Any spillages that occur shall be managed using project procedures and legal requirements and as indicated on the SDS. 

· Identify appropriate storage areas for stockpiling of materials, storage of hydrocarbons and storage of hazardous substances and ensure that these areas are appropriately prepared for their purpose.

· Disposal of hazardous substances shall be done in terms of the relevant legal requirements.

· Limit spillage of hazardous substances or substances with the potential to cause contamination of the environment.

· Develop emergency protocols for dealing with spillages particularly where these pose a pollution risk or involve hazardous substances.

· Compile and implement the necessary Method Statements; and undertake environmental awareness training of all staff.

2.4.3 Herbicide usage

Only registered pest control operators shall apply herbicides on a commercial basis. All staff applying herbicides shall be trained in the application thereof and shall be provided with suitable PPE.

The application of herbicides shall be in accordance with the Fertilizers, Farm Feeds, Agricultural Remedies and Stock Remedies Act No. 36 of 1947. Only approved and tested herbicides with a low environmental risk shall be used.

A herbicide register for usage shall be compiled and maintained, and a copy handed to the project leader / environmental advisor on completion of the project / contract.

2.4.4 Fire hazard

The Contractor shall develop emergency protocols for dealing with fires, which may include a Fire Management Plan in accordance with the National Veld and Forest Fire Act (No 101 of 1998) and ensure that all staff is educated in fire prevention and shall be held responsible to avoid the risk of fire. Firebreaks shall be created to prevent fires from spreading. No open fires are allowed on site. The Contractor shall ensure that operations always comply with statutory requirements. The Contractor Environmental Officer shall ensure that in areas with a high fire danger rating, staff are made aware thereof. Smoking shall be restricted to designated areas or shall not be allowed, particularly in areas that have a high fire danger rating. 

Contractor shall ensure that adequate Fire Fighting equipment is available on site, particularly near hot work.
2.4.5 Waste

All waste generated shall be disposed of at a licensed facility.  A waste inventory of all waste streams generated or handled shall be developed and kept. A waste management plan shall be compiled before commencement of work. Records of waste disposal shall be submitted to TM as required in terms of Medupi Waste Management Work Instruction. No waste, be it biodegradable or not, shall be left on site once work has ended.

Industrial general waste and hazardous waste generated shall not be burned, buried, or disposed of on Eskom or Landowner property, but instead be controlled and removed to a licensed waste site on a regular basis. The Principal Contractor and Contractor working on site shall ensure that oil, fuel, and chemicals are confined to specific and secure areas throughout the construction period. These materials shall be stored in a bund/secondary containment with adequate containment for potential spills and leaks.

Waste shall be collected by the registered service provider or alternatively taken by the Contractor to a registered landfill site. Of most important legal requirements pertaining to transportation of waste shall be adhered to. 

Contractors shall ensure that sufficient waste bins / containers, with lids are made available for waste control. The Contractor shall comply with the requirements of NEM: Waste Act 59 of 2008.

Quantities of disposed waste shall be recorded and reported monthly. Set up system for regular waste removal to an approved facility and minimize waste by sorting wastes into recyclable and non-recyclable wastes.

Equipment maintenance and storage:

· Ensure that all plant is in good working order.

· Undertake maintenance within specified area (workshop); and use drip trays for all stationary or parked plant and when servicing equipment away from designated areas.
2.4.6 Material requirement

The use of any material or property belonging to any landowner shall not be permitted prior to arrangements with the relevant landowner. Written proof of such agreement shall be handed to project leader / co-coordinator for record keeping.

2.4.7 Dust and Noise

The Contractor shall monitor dust and noise caused by mobile equipment, generators, and other equipment during construction. Factors such as wind can often affect the intensity to which these impacts are experienced.

To ensure that noise does not constitute a disturbance during construction activities, all construction works shall occur between specific working hours. This shall be stipulated in the contract. 

Mitigation measures to be implemented as required / agreed upon with the project leader / environmental advisor.

Dust suppression measures shall be in place to reduce the dust caused by the movement of heavy vehicles and other Contractor activities.

2.4.8 Environmental Incidents

All environmental incidents such as pollution (air, water, land, noise, etc.), bird kills, and animals killed, plants destroyed, public complaints etc. shall be reported to TM and/or ECO before the end of the shift. 

All environmental incidents occurring on site shall be recorded according to current Eskom Environmental Incident Management Procedure detailing how each incident was dealt with.  Proof thereof shall be kept in an incident register.

The Contractor shall be held liable for any infringement of any Environmental statutory requirements.

2.4.9 Water

Always implement the current project Water Use Licence

No construction shall be allowed within the 1:100-year flood lines. Shall any pollution of the watercourse occur, the Department of Water and Sanitation shall be notified immediately. 

Water usage on site shall be verified with the substations/power stations responsible person, the project leader / environmental advisor to ensure compliance with legislation. Borehole water shall be verified as suitable for human consumption. All incidents related to water contamination shall be reported as per the requirements stipulated under Eskom Environmental Incident Management Procedure. Records of water quantities abstracted shall be kept and submitted on the 25th of every month as part of the Contract Environmental Compliance Report.

Chemical toilets shall not be within proximity of the drainage lines / ways and shall be serviced on regular basis. Service records shall be submitted on the 25th of every month as part of the Contract Environmental Compliance Report.
2.4.10 Environmental file

Environmental file including the following but not limited to shall be approved by the client. Ensure the files is updated regularly. 

· Comprehensive aspect and Impact register specific to the scope of works. 

· SHE policy recently signed. 

· Environmental management plan that addresses all the potential environmental risks as per aspect and impact register. 

· Environmental Legal Register. 

· Declaration Letter of Compliance to Eskom Environmental Requirements.

· Environmental procedures or plans which include, Waste Management Plan, Hazardous Chemical Agents Management Plan, Water Management Plan, Non-Conformance and Incident Management Plans and Internal Auditing Procedure etc.

· Method statements that include environmental impact and mitigations measures. Include all activities in sequence as per the project scope and aspect and impact register. 

2.4.11  Environmental legislations and other requirements 

Ensure compliance to all relevant environmental legislations and other requirements. 
Ensure compliance to the project available licences, authorisations and permits.

Ensure that the environmental legal register is updated continuously and maintained.  
2.5 Quality assurance requirements
2.5.1 Quality Requirements 

The Contractor shall demonstrate, provide, and maintain a Quality Management System (QMS) that is ISO 9001:2015 certified or compliant thereto as well as the Supplier Quality Management Specification (240-105658000) and Medupi Contractor Quality Specification (348-389557). Compliance with the provisions of this clause in no way relieves the Contractor of the final responsibility to furnish acceptable services. Contractors QMS that includes: 

a) Ensuring that processes, plans and procedures needed for the QMS are established and maintained and the integrity of the QMS is maintained when changes are implemented.
b) Ensuring that Quality Assurance and Quality Control Depts. are sufficiently manned with competent resources to effectively implement quality requirements.

c) Reporting to top management on the performance of the quality management system and any need for improvement.

d) Ensuring the awareness of customer requirements throughout Contractors organization. 

The Contractor shall ensure that the Employer's requirements as specified in the Contract are met in full and verified as such to Employer satisfaction. Quality management shall be in accordance with ISO 9001:2015 and related ISO 9000 series of Standards and is to provide full documentary and Objective evidence that the Works have been designed, manufactured, executed, completed and maintained in accordance with the Contract.

The quality management system shall apply to the Contractor and all persons real or juristic working for

or on behalf of the Contractor on or in connection with the Works and regardless of the form of employment

contract.
The Contractor shall ensure that the Quality Control Plans, Inspection and Test Plans and procedures/instructions/method statements/ECNs/FCNs developed or adopted provide stages at which the Employer may witness what is being done or require what is being done to be subject to inspection before the execution continues. 
· Inspection activities during manufacturing shall be managed according to the Medupi Manufacturing Inspection and Testing Procedure (348-860842).

· Inspection activities during construction shall be managed according to the Medupi Site Quality Assurance Control and Verification Procedure (348-106670).

· The Contractor shall be required to maintain inspection databases where all records of inspection are maintained as required in the Medupi Quality Specification (348-389557).

The Contractor shall list all documentation needed for the effective implementation of the project quality management system (QMS) and shall, as a minimum, prepare, maintain and implement throughout the

life cycle of the project, as part of the project quality management system. The project specific

documentation are as follows:

a) Project Quality Policy

b) Project Quality Strategy

c) Project Quality Objectives

d) Project Quality Management Plan

e) Project Organisation Chart.

f) Project RACI Matrix – may be split by Dept. /Phase/Discipline as required.

g) Job Descriptions including performance requirements and measurements.

h) Equipment and Process Criticality Ratings,

i) Project Quality Assurance Plans – per project phase:

(i) Design

(ii) Manufacturing, Inspection and Testing

(iii) Construction, Inspection and Testing

(iv) Commissioning and Taking-Over

(j) 
Project Quality Control Procedures - per discipline:


(i) Civil and Structural works.


(ii) Mechanical, Piping, Painting and Insulation works.


(iii) Electrical works.


(iv) Control and Instrumentation works.

Project Quality Control Procedures per individual activity identifying specific inspection and test methods and

acceptance criteria.

Project Inspection and Test Plans (ITP’s) per individual activity that plan, assure quality, and define inspection intervention levels.

Project Quality Verification Records per individual activity - as referenced in ITP’s.

Manufacturing, Construction and Commissioning Record Books

Except where otherwise stated, all documents that constitute the Quality Management System,

including proforma Quality Verification Records, shall be complete, in accordance with the Contract,

and ready for use and submitted to Engineer not less than 30 days before the work governed by the

documents are planned to start.

Throughout the lifecycle of the project, on a monthly basis, the Contractor shall maintain and submit a

MDL (Master Documentation List), to the Project Manager for review and approval. Each document on the Master Document List shall have the following marked against it:

a) 
The planned and actual date of submittal to the Project Manager 

b) 
The classification of documentation (for approval, for review, or for reference) based upon the

       classification guidelines of Quality specification document.


(i) 
Class 1 - for the Engineer’s approval - where the Contractor may not proceed with the Works 

            that are the subject of the document until it has been approved by the Engineer.


(ii) 
Class 2 - for the Project Manager’s Review - where the Contractor may proceed with the works 

             that are the subject of the documentation if the Project Manager’s has made no comment after 
             seven (7) days from the receipt by the Project Manager 

(iii) 
Class 3 - for the Engineer’s Reference - where the Project Manager reserves the right to comment, 

            but the Contractor may proceed with the works that are the subject of the documentation. 

Where there is an ambiguity or where a document is produced that is not referenced

therein clarification as to classification shall be sought from the Project Manager.

The Master Document List shall be submitted to the Project Manager electronically via email in native file format on a monthly basis.

The Contractor submits as a minimum the following documents, as required by the Employer, which requirement does not constitute a compensation event, during the execution of the Works:-

a) Updated QCP register.

b) Inspection notifications accompanied by their inspection report.

c) Non-conformance and Defects registers and reports

d) Updated Site and off-site inspection schedules.

e) Inspection and or FAT dates.

f) Inspections completed/outstanding.

g) Inspection and test reports

h) Monthly contract quality progress report

· Data books for the completed Works, before commissioning can commence (refer to the Record books section 2.5.2 and data books hand over timelines)

· The Contractor agrees to control and professionally preserve and store appropriate documents, records and recordings for a period of 5 years after termination of the agreement to guarantee the traceability of the services rendered and inspection thereof.

· The Contractor agrees to regularly update and implement all the latest technology available as well as the necessary improvements for the installation, production and organisation deemed necessary to meet the requirements of the agreement and in order to enhance capabilities and effectiveness to deliver high quality, cost-effective security services.

· The delivered or services shall be uniform in Quality and condition, consistent with good industry practices and adhere to requested Eskom requirements, without deviation.

· The Employer shall have the right to regularly conduct inspections, assessments, audits and surveys and perform surveillance of the Contractor and/or Sub-contractor facilities, sites, premises, records and documentation (including but not limited to data books) to evaluate their capability to comply with the requirements necessary to conform to contractual and QMS requirements.

· The Employer reserves the right to inspect, at reasonable times, any or all of the services performed at the Contractor’s or Sub-contractor premises or elsewhere. Verification by Eskom shall not absolve the Contractor of the responsibility to provide acceptable product and / or services, nor shall it preclude subsequent rejection by Eskom. 
· The services shall comply with the agreed specifications and requirements and the applicable directives and standards set out in the Contract. Defects notified by the Employer shall be remedied by the Contractor upon demand by the Employer without undue delay and at no extra cost. The Contractor shall continuously monitor and identify non-conformances, both internal and external, as signals of opportunities for improvement making process and other relevant changes to prevent recurrence.

· The Contractor shall further identify potential problems before they occur by identifying deviations in patterns or trends in product, service or process performance.

· Nothing contained in the Contract and/or purchase order and/or scope of work and /or works information shall relieve in any way the Contractor from the obligation of Quality control thereof.

· The Contractor guarantees that the Quality of the delivered services will comply with the requirements of the contract and/or relevant specifications. 
· The Contractor shall, on request, prove its ability to relate to the proposed scope of work which establishes the manner in which the Contractor intends to perform the Contract.

· The Contractor shall, on request, prove its organisational, logistics and support resources to ensure the requirements of the contract can and will be achieved.

· The Employer reserves the right to assess and measure, during the existence of the agreement the qualifications, capability and competence of the key staff (assigned personnel) in relation to the scope of work and to interview any / all of them to confirm the Quality evaluation.

· The identified professional personnel who will be managing the service will be available and accessible on a continuous basis until the conclusion of the project.

· The Contractor shall demonstrate experience in comparable projects or specific aspects of the project and / or performance in similar projects, on request.

· The Quality of the services and the contents thereof will always be in accordance with professional standards.

·  For the duration of the Contract, the professional staff managing the service, shall be and remain a member of his/her Professional Society 

· The Contractor shall, at all relevant times, scrutinise and be aware of Eskom’s requirements with specific focus on, inter alia, its philosophy, principles, strategies, practises, mission, vision, models, policies and practises. 
· The Contractor shall exercise reasonable professional skill, care and diligence in the performance of his obligations in terms of this agreement.

· On awarding of the Contract to the successful Contractor, such Contractor shall present to the Employer an acceptable Quality Control Plan (QCP). The QCP shall comply with the requirements of ISO 10005. 
The Contractor shall employ sufficient qualified and knowledgeable quality assurance and quality control and inspection staff. These staff members shall be independent from those responsible for construction and commissioning activities and report directly to the Site Quality Department Manager and not the production team as referenced on Medupi Quality Specification (348-389557 sub-clause 3.4.1).
2.5.2 Quality Payment Schedule

1) The Contractor shall ensure that Quality Assurance is performed at all levels and phases of work carried out for the Employer. 

2) The Contractor shall use processes to ensure that quality is built into their products/services i.e. its business processes are organized such that quality is built into the process of producing goods and rendering services. The Contractor shall work according to processes.

3) The Contractor shall ensure that it can be relied on to deliver quality goods and services without the need for the Employer to have to inspect all the time.

The Contractor shall keep the Quality Table of Payments (Quality Payment Schedule) updated with progressive Employer sign-off (as the work is done and Contractor Payments Application are submitted). This means that as the Contractor completes an activity and has the related ITP/QCP signed by the Employer, the Contractor shall bring the Quality Table of Payments to the Employer’s Quality representative to sign off for that activity. 

The updated Quality Table of Payments shall accompany each Contractor payment application. The Contractor shall attach the signed (or partially signed if applicable) ITPs/QCPs to the Contractor Payments Application. Payment will only be made if the ITPs/QCPs are signed by the Employer. 
2.6 Programming constraints 
2.6.1 General Programme Requirements

The Contractor shall submit Programmes in Primavera P6 format and shall be submitted weekly in electronic format (XER) with copies in PDF. 
The Employer provides the Key Dates as set out in clause 11.2.9 of the Contract Data of the Employer, the access dates in clause 30.1 of the Contract Data by the Employer; the interface points shall be identified by the Contractor as per the Scope of Work and the requirements set out in the Works Information. 

The Contractor submits as part of its tender response a P6 Level 4 programme, in XER format together with copies in PDF, which becomes the First Accepted Programme that contains the following as a minimum: 
a) Show all activities as per the Scope Document No. 348-9971909, Works Information, and any other activities required to deliver the project successfully at P6 Level 4,
b) All activities shall be resource loaded and shall be aligned with the costing report (Activity Schedule),
c) Show activity durations taking into account the Completion Date stated in the Contract Data by Employer,
d) Show late and early start dates, late and early finish dates and total float, 
e) Include activities codes and XER export of layout used by the Contractor. Activity ID’s/codes will not change during the contract period,
f) The access dates from clause 30.1 of the Contract Data by the Employer,
g) Interface with Others, 
h) Interface with the Employer.
i) The date of Site establishments activities and Site De-establishments activities,
j) Any addition or deletion of activities to be clearly reported on with reasons,
k) The Contractor shall ensure that his programme contains sufficient float in order for the Contractor to add interface and alignment with the Employer’s requirements, and
l) Other factors, information, methodologies, details and dates which the Contractor believes are necessary for the achievement of the interface with Others, Key Dates, Completion Dates and access dates.

The Contractor submits a revised programme during the Contract in accordance with time provided in clause 32.2.  This revised programme shall contain the following: All information required as [stated above],
a) Activities exceeding thirty (30) days in duration shall be broken down into detailed sub-tasks,
b) the services and work (programs) of all his Subcontractors and suppliers,
c) Clearly identify and indicate milestones, Key Dates, and critical path, 
d) the design schedule,
e) the construction schedule,
f) the planning schedule,
g) the construction and manufacturing schedule,
h) Commissioning activities shall be scaled in days, 
i) Any addition or deletion of activities to be clearly reported with reasons in a separate letter as per the Change Procedure.

The Contractor submits an updated programme every 2 weeks during execution. The updated programme is not a revised programme submitted in terms of clause 32 of the Contract.  Notwithstanding anything to the contrary in the Contract, Works Information or expressed at any meeting or in any minute of a meeting, the Accepted Programme is not altered by the Employer’s involvement in discussing the updated programme. All references to the requirements for a revised programme will be inferred as references to the requirements for an updated programme.

Where project execution date periods fall during or after public holidays or the annual builders’ holidays, festive season, Easter, or any Other public holiday recognised by the Public Holidays Act number 36 of 1994, the Contractor plans his schedule, work force and resources to ensure the Key Dates and Completion Date are met.  
Together with the first programme, the Contractor shall submit a cash flow diagram (S-Curve) directly produced from the programme detailing the estimated financial expenditure over the Contract period based appropriate quantitative information.
2.6.2 Commissioning Plan 
To the extend the Contractor is responsible for the design of the works under the Contract, the Contractor shall prepare and submit to the Employer for his approval a detailed commissioning plan for such works, which commissioning plan shall:
a) Comply with the Employer’s Requirements and other applicable requirements of the Contract (the Contractor acknowledging that his commissioning plan will need to be integrated by the Employer into a detailed commissioning plan for the related works, which will include the works of Others).

b) Be amended and re-submitted at the expense of the Contractor until approved by the Employer.
c) Be amended, updated, and re-submitted for the approval of the Employer as necessary and when required by the Employer.

d) Compliance with the commissioning plan shall not relieve the Contractor of any responsibility, undertaking warranty or other obligation under the Contract.

Unless the Employer directs otherwise, the detailed commissioning plan shall be submitted at least six (6) months prior the scheduled start date of commissioning and a preliminary commissioning plan shall be submitted within fifty-six (56) days after commencement date.

2.6.3 Computerised Planning 

Primavera Project Planner (version 6) has been adopted by the Employer for all planning, progress monitoring and reporting on the Project. The Contractor applies it for the planning and control of the works in line with the accepted WBS.  The Employer does not accept any programmes, progress reports or Other required data and information in PDF or any Other form except Primavera Project Planner (version 6).

The Employer will have a Master Programme which incorporates the Contractor’s and Others programmes. The Contractor submits updated electronic progress reports as required by the Project Manager which requirement is not a compensation event. The updated progress report shows the logic and all filters and layouts used in the programme. 

2.6.4 Planning Methodology and Programme Levels

All planning is done based on the CPM. The Contractor’s planning methodology incorporates the compatibility, alignment and interface with Others on the Project.  This is clearly visible to the Employer. The Accepted Programme shows the actual critical path clearly. Unless the critical path is affected the Contractor does not get a change to the Completion Date [or increase to the Prices].

The Accepted Programme and progress reports layout takes into account the approved WBS, reflecting the manner the works are to be performed and how control data are to be summarised, reported and monitored.

The Contractor’s Accepted Programme and progress reports include sufficient detail and input to allow for dynamic integrated project control allowing the Employer to achieve the requirements of the Project.

2.6.5 Time Reporting

The Contractor extracts and provides a one-month “look ahead window” from the Accepted Programme, showing activities.  It furthermore shows Key Dates and the activities of the Employer and Others, which are scheduled for Completion within the next reporting period in a case where there are interfaces.
2.6.6 Reporting on Remaining Duration

The method for reporting on activities in progress is by remaining duration, i.e. the time, in working days, needed to complete the activity from the report date.  Once an activity has started, the remaining duration is assessed for each update.

Automatic reduction of remaining duration as the report date moves forward is not accepted.

2.6.7 Actual Dates

When completion of any activity is confirmed by quoting document numbers, these numbers are given in remarks and are appended, e.g. suborders, drawings, inspection certificates, delivery notes, etc.  The actual starting and completion date of all activities is reported.

2.6.8 Progress Reporting during Provision of the Works
The Contractor submits its progress reports on the last day of each month and if the last day is not a working day, the preceding working day or more often as required by the Project Manager.  This requirement does not constitute a compensation event.  

The Contractor submits, together with the progress reports, a written report containing the following:

Statement and report on work where delay against the Accepted Programme has occurred (if any), together with the reasons why delay has occurred and a plan denoting the action to be taken and the period of time necessary to recover such delay; any impact that the delay may have on Others or an indication of Others affected by the delay.

Statement and report on those Works that are currently ahead of programme, any impact on the progress of Others or an indication of Others affected by the delay.

The impact of any programming changes arising is reflected in revised forecast rate of payment schedules and resource schedules.

2.6.9 Progress Report

The Employer, the Contractor, and Others meet daily to report the overall progress of erection activities which identifies the following:

a) any SHE related incidents and remedial actions or plans;

b) progress of previous day’s work

c) resources,
d) any deliveries of Plant, Material and Equipment’

e) the scheduled date of delivery of Plant, Material and Equipment’

f) interface, alignment and compatibility with the Employer and Others;

g) Contractor’s current activities progress and planned finish dates

h) Contractor’s planned start and finish dates for work

i) Planned effort for activities.
j) Actual effort for activities.
k) Remaining duration for activities

l) Percentage progress for activities 

2.6.10 Weekly Progress Report

The Contractor submits weekly progress reports to the Project Manager.  This report is used as a tool for the day-to-day management of the Contract. Contents of a weekly report include the following items:

a) Programme summary narrative.

b) Progress and performance summaries.

c) Schedule rolling horizon.

d) Completion and Key Date status.
2.6.11 Monthly Progress Report

The Contractor submits to the Project Manager a written monthly report as provided for in paragraph 2.6.6 above. The report contains the following information as a minimum requirement:

a) Executive summary (narrative identifying major movement within the reporting period).

b) Revised Programme indicating, actual progress of work against last Accepted Programme.

c) A one-month look ahead work window.

d) Activities completed during current reporting period per discipline, including the activities of the Employer and Others.

e) Activities in progress during current reporting period per discipline, including the activities of the Employer and Others.

f) Activities undertaken during next reporting period per discipline, including the activities of the Employer and Others.

g) Status overview by unit, by plant area, by phase.

h) Key issues / Items of concern and corrective actions.

i) Progress curves and tabular progress reports.

j) Cost and Cash flow.

k) Cost curve 'S-curve'.

l) Early warning log.

m) Compensation event log.

n) General planning report (computer generated).

o) Critical activities report.

p) Key event report (computer generated).

q) Report selecting all of the activities of the Employer and Others - (computer generated).

r) Updated bar charts.

s) Updated resource schedule and histogram (If changed).

t) Updated activity schedule 

u) Forecast rate of payment schedule updated with actual progress.

v) Statement and report on Works ahead and behind progress.
w) Skills development progress report (if applicable)
2.6.12 Planner Requirements

The Contractor’s planner is experienced, qualified and shall be dedicated to the Contract to perform the planning and programming requirements in accordance with this section.  During execution, the Contractor shall provide a full-time planner at the Site.  

2.7 Contractor’s management, supervision, and key people
Proof of qualifications to be submitted to the Project Manager for approval and acceptance for the Contractor and Subcontractor’s key people, including appropriate registrations.

The Contractor to submit an operational plan, including organogram showing people and lines of authority / communication for approval and acceptance by the Project Manager. 

Below are the key persons referred to in clause 24 of the Contract. The Contractor should on his organogram include the below listed key persons.

The Contractor provides the following key people as a minimum:

a) Dedicated Project Manager 

b) Dedicated Project Planner 

c) Dedicated Site Manager 

d) Dedicated Quality Manager

e) Dedicated Quality Control Supervisors
f) Dedicated Site Safety Manager

g) Dedicated Site Safety Representatives 

h) Dedicated Engineering Manager /Technical Field Advisor / Specialist

i) Dedicated Engineer (as part of Labour resources).  
j) Dedicated Commissioning Engineers (as part of Labour resources). 

For the purposes of this Contract, “dedicated” means that the person is allocated only to this Contract, full time, shall not be working on any other contract, shall be available at Site as and when required, shall be available at Site full time during the construction phase, shall respond promptly to instructions.

In the Contractor’s tender response, the Contractor states how many of the key people are required for this Contract. The Contractor’s pricing for this provision of this activity shall be stated in such a way that the Employer is able to assess the number of dedicated persons, their job function, and the extent of their availability. If the Employer finds that the key people are not a “dedicated” resource, the Employer makes a pro rata deduction from the Prices. 
2.8 Invoicing and payment
2.8.1 Contractor Payment Application

The Contractor shall submit copies of the Contractor Payment Application to the Project Manager for assessment and certification, by the 20th of each Month, in a form approved by the Project Manager, showing in details the amount to which the Contractor considers himself to be entitled as per the value of work executed (completed activities as per the activity schedule), together with supporting documents which shall include all documents as stated under Section 2.5 (Quality assurance requirements) of this document, and any other document to substantiate the completed activities.  
Within one week of receiving a payment certificate from the Project Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoices showing the amount due for payment equal to that stated in the Project Manager’s payment certificate.  
The Contractor shall address the tax invoice to Eskom Holdings SOC Ltd and include on each invoice the following information:

	Eskom Holdings SOC Limited

Medupi Power Station

	P. Bag 7502

	ONVERWACHT

	0557


And, include on each invoice the following information:

Name and address of the Contractor and the Project Manager; 

The contract number and title;

Contractor’s VAT registration number;

The Employer’s VAT registration number 4740101508;

Description of the completed activity for each item invoiced based on the Activity Schedule;

Total amount invoiced excluding VAT, the VAT and the invoiced amount including VAT;

Procedures for invoice submission and payment (e. g. electronic payment instructions)
a) Submit Contractor Payment Application by 20th of each month to the Project Manager for assessment and certification.  
b) The Project Manager will verify and return the payment certificate to the Contractor around 27th of the month; however, the Contractor is required to substantiate each payment application using QC and/or QS verified and signed records. If the Contractor has not submitted the verified and signed records with the application the application submission date will then be calculated from the date on which the verified and signed records are submitted. 
c) Following receipt of the payment certificate the Contractor is required to submit a tax invoice to the Employer and the following email address invoicesgrpcapitalMHP@eskom.co.za.
d) Where the Contractor is also claiming for Cost Price Adjustment (CPA) and Deductions /Penalty release, the Contractor is required to issue a separate invoice for CPA and separate invoice Deductions /Penalty release.

e) The invoice date cannot be before the date on which the payment certificate was signed by all relevant people who are supposed to sign the payment certificate as the invoice is supposed to be issued after all parties had signed the payment certificate. 

f) Payment date would be calculated from the date on which the Contractor submits a valid invoice to the account payable email address.  If the Contractor submit an invalid invoice, it will be rejected / returned back to the Contractor and the Contractor will be required to resubmit a valid invoice and payment date will also be calculated from the date on which a new valid invoice is submitted. 

g) Payment will be concluded within 60 days of receipt of undisputed invoices.
2.9 Insurance provided by the Employer. 
As stated for in the Employer`s Construction All Risk Insurance Policy available on request from Eskom Group Insurance. 

To be dealt with in accordance with ECC3 Core Clause 80 and as also stipulated in Z Clauses.  

The insurance policies and procedures will form part of the Contract Data and any reference to this will be contained in the Contract Data.
2.10 Contract change management. 
Changes during a term of the Contract are inevitable and when they occur, they need to be managed within the policies and procedures of the Employer. Changes can be minor which are administrative or substantial which may affect the price and delivery.  There are two ways to change a contract: 

a) Bilateral

b) Unilateral

Bilateral is when both Parties (Contractor and Employer) agree that a change is necessary. The second one is the unilateral whereby the Employer may exercise a right to modify the contract without the Contractor’s consent. In case of latter one, the Employer’s procurement and supply chain management procedure 32-1034 shall be followed.
2.10.1 Contract changes and contract Scope

Employer’s commercial policy requires a competitive process, any change upon the type of goods or services needed shall be consistent with what was asked during the tender stage. A contract change needs to be within the scope of what was provided during tender stage. A significant difference will not be allowed because it had not been subjected to fair competition. Transparency is one of PPPFA requirements and as a government owned organisation had to comply with.
2.10.2 Administrative changes

These are the changes that are within the scope of contract and do not affect the originally signed contract. These changes are typically executed via a unilateral amendment. Examples include: 

a) Changes in address,
b) Correction of typographical errors not affecting the substance of the contract,
c) Changes as permitted by the language of the contract,
d) Changes in personnel assigned to the contract (exclusion of Key People, these are dealt with as per the contract). 
2.10.3 Substantive changes

These are the changes that affect both Parties. They require bilateral amendments. These changes may require one of the Parties to be compensated for such changes as stated in the contract clause 60.1 

2.10.4 General Principles of contract change management.
Engineering change will be dealt with as per 3.3 if either party is in doubt about whether a change fall within the definition of engineering change then it will be processed as a contract change.

Under this contract change management: 

a) Either party may request a contract change. All changes need to be formally communicated prior to the implementation of that change. 

b) Neither party makes a request that is not made in good faith or for good reasons

c) The Project Manager assesses and documents the potential impact of a proposed contract change before presenting it to Employers Compensation Events Committee

d) The Project Manager has the right to request reasonable amendments to a contract change request.

e) The Project Manager has the right to reject a change and specify his reasons. 

f) No proposed contract change will be implemented by the Contractor without prior approval of the Project Manager. 

g) If the proposed change is of emergency in nature, approval of emergency instructions will be followed as per paragraph 2.10.9, 

h) Any contract changes necessary to comply with a change in law will be implemented as set out in paragraph 2.10.3 & 2.10.4. 

i) Until a change is approved, signed, and issued to the Contractor, then 

i. Unless the Project Manager expressly agrees otherwise in writing, the Contractor continues to provide the works in accordance with the signed contract as if the proposed contract change does not apply.
ii. Any discussions, negotiations or other communications which may take place between the Project Manager and Contractor in connection with any proposed contract change, including submission of any change communications, is without prejudice to each party’s other rights under this Contract. 

j) The Project Manager notifies in writing the Contractor stating the reasons why the Contractor has not reasonably demonstrated the need or justification for the contract change in connection with the specified event. If the Contractor disputes the notice, then the matter is resolved in a risk reduction meeting. 

k) Where the Contractor does not approve a contract change in respect of a specified event, the Contractor notifies his decision within period of reply. 
2.10.5 Costs

a) Each party bears its own costs in relation to the preparation and agreement of each change request and impact assessment.

b) All contract changes are calculated in accordance with the principles set out in Price Schedule. Any cost savings resulting from the contract change will be passed on to the Project Manager by way of reduction in the charges.2.10.6 Contract Change Request.

c) Either party may issue a contract change request to the other party at any time during the term of the contract. The change request is substantially in the form of Appendix 10 and shall state a relevant clause and specify if it is categorised as an emergency change. 

d) If the Contractor provides a contract change request, he also needs to provide an impact assessment in terms of cost, schedule, and quality. 
2.10.6 Impact Assessment

a) Each impact assessment includes (without limitation): 

i. Details of the proposed contract change where the contract change is proposed by the Contractor including the reason for the contract change.
ii. Details of the impact of the proposed contract change on the contract and the Contractor’s ability to meet its other obligations under this contract, including without limitation changes to: 

· The Works Information 

· Accepted Programme

· Other works provided by Others to the Employer including any changes required by the proposed contract change to the Project Manager.

· Interface 

iii. Details of the estimated cost of implementing the proposed contract change

iv. A schedule for the implementation, together with any proposals for the testing of the contract change

v. Where applicable details of how the proposed contract change will ensure compliance with any applicable change in law.
vi. Such other information as the Project Manager may reasonably request in (or in response to) the change request.

b) The Project Manager reviews the impact assessment and responds within the period of reply or as agreed with the Contractor. 

c) If the Project Manager requires further information regarding the proposed contract change so that it may properly evaluate the change request and impact assessment, then with the period of reply or as agreed with the Contractor, the Project Manager notifies the Contractor of this fact and details the further information that is required. The Contractor provides the relevant Impact assessment within the period of reply or as agreed with the Project Manager of such notification. The parties may repeat the process described in this paragraph until the Project Manager is satisfied that it has sufficient information to properly evaluate the change request and impact assessment. 
2.10.7 Project Manager’s right of acceptance of contract changes

Within period of reply of receiving the impact assessment from the Contractor, or further information, the Project Manager evaluates the change request and the impact assessment in good faith and 

a) Submits all the details of the event to the secretariat of the Employers Compensation Events Committee (CEC) which meets on weekly basis. 

b) Presents the details of the event to Employer CEC 

c) Implements the recommendations of the CEC. 

d) Notifies the Contractor of the rejection of the proposed change. If the Project Manager rejects a proposed change, then he may explain his reasons in writing to the Contractor within period of reply or as agreed with the Contractor. 

e) Require further details on the change request and/or impact assessment in which the Contractor makes changes and respond within period of reply or as agreed with the Project Manager of such request. 

f) If the proposed contract change is recommended by the compensation events committee, the Project Manager notifies the Contractor in writing. The Project Manager signs off on all deviation to the contract (drawings, specifications, and other relevant documents) before the implementation of such deviations may take place 
2.10.8 Contractor’s right of acceptance of proposed changes

The Contractor has a right to reject a proposed change if he believes any proposed contract change which is requested by the Project Manager:
a) Would materially and adversely affect the risks to the health and safety of any person,
b) Would require the works to be performed in a way that infringes any law,
c) Is technically impossible to implement provided that:
i. The Contractor can demonstrate to the Project Manager that the proposed contract change is impossible to implement,
ii. Neither the Accepted Programme nor the Works Information state that the Contractor has technical capacity and flexibility required to implement the proposed change. 

d) Would materially and adversely affect the Contractor’s ability to deliver the works.

e) Would not be possible to implement before contract completion date,
f) Would cause the Contractor to breach any of the insurances, 
g) Would cause the Contractor to be in breach of any existing licence, consent, or permit,
h) Would require the consent of Others to enable the contract change to be implemented and the Contractor is unable to obtain the consent of the Others, and 
i) Would result in additional cost to the Contractor that is not proposed to be paid to the Contractor as part of change.
2.10.9 Emergency Instruction contract changes
a) The emergency instruction contract change may cover technical, financial, safety and strategic aspects.

b) The only person who can instruct the Contractor to implement such changes is the Project Manager. Such instructions need to be subsequently followed by a written formal communication. All changes shall be documented, and no payment will be made to undocumented change. 

c) The Project Manager is given restricted authority to cover instructions to the Contractor that are of an emergency in nature, and which will result in a contract change. Such contract changes are presented to the compensation events committee, by the Project Manager, for its retrospective recommendation and ratification by the Employer.
2.10.10 Authorisation of Contract Change

Any proposed contract changes are not authorised, and the Contractor does not implement any proposed contract change until the signed letter and other signed documents (e.g., drawings, specifications) are sent to the Contractor. 

2.10.11 Communications

a) For any contract change communication to be valid, it shall be sent to the Contractor as applicable.

b) All contracts change communications may be hand delivered or sent by first class post or facsimile. Contract change communications are deemed to have been received at the following times: 

i. If hand delivered, then at the time of delivery or, if delivered after 16.00 hours on the next working day

ii. If posted first class within South Africa at 10h00 on the second working day after it put into the post.

iii. If sent by facsimile, then at the expiration of four (4) hours after the time of despatch, if despatched before 15h00 on the next working day, and in any other case at 10h00 on the next working day following the date of despatch.

c) In proving delivery of a contract change communication, it will be sufficient to prove that the delivery was made, or that the envelope containing the contract change communication was properly addressed and posted (by prepaid first class recorded delivery post) or that the facsimile was properly addressed and despatched.
2.11 Provision of bonds and guarantees. 
The form in which a bond or guarantee required by the conditions of contract (if any) is to be provided by the Contractor is given in Part 1 Agreements and Contract Data, document C1.3, Sureties.  

The Employer may withhold payment of amounts due to the Contractor until the bond or guarantee required in terms of this contract has been received and accepted by the person notified to the Contractor by the Project Manager to receive and accept such bond or guarantee.  Such withholding of payment due to the Contractor does not affect the Employer’s right to termination stated in this contract. 

2.12 Records of Defined Cost, payments & assessments of compensation events to be kept by the Contractor. 
The Contractor submits the following for compensation event assessment:

a)
Quotation indicating current market rate if not included in the short schedule of cost components. 
b)
Labour time sheets

c)
Early warning to the Project Manager
d)
Project Manager ‘s Instruction

e)
Percentage fee applied. 
f)
CPA Calculation where short schedule of cost components rates was utilised 

g)
Signed record of decisions (ROD) or design change request form for engineering design changes

h)
Revised program where key date and completion date is affected. 
i)
Revised programs were instructed to accelerate by the Project Manager. 
j)
Invoice from Contractor and service providers. 
2.13 Training workshops and technology transfer

At completion of the installation and commissioning of the first Section of the Works, the Contractor is required to provide training and transfer system knowledge to the Employer by submitting documented design Intent, as-built drawings, operational and maintenance manual, commissioning records, commissioning report and by providing training on all the systems to the Employer’s personnel to ensure that they have all the information and understanding needed to operate and maintain the features and systems in the various areas. 
As each Section of the works is completed (after Commissioning of a section) the Contractor is required to provide training and transfer system knowledge to the Employer’s personal. 

Training requirements are detailed in the 348-9971909: Scope of Work document (Technical Specification: Medupi Power Station Emergency Preparedness Public Address System Project). 
3 Engineering and the Contractor’s design
The Contractor submits the Contractor’s Design Documents to the Project Manager for acceptance at the times and in the manner and format stated in the Works Information, and in the specification document 348-9971909. For the details of the acceptance of Contractor’s designs, refer to the document number 348-9971909. 

The Contractor grants to the Employer, with effect from the starting date, in the case of documents or other matters not yet in existence, with effect from the creation thereof (and notwithstanding the Completion or termination of this contract), an irrevocable royalty-free non-exclusive licence to use all of the documents provided to Provide the Works (including, but not limited to calculations, computer programmes (Software) and other software, drawings, manuals, models and other documents of a technical nature), for any purpose whatsoever, including for the purpose of operating, repairing, maintaining, dismantling, re-assembling and making adjustments to all parts of the Works. The Contractor ensures that each Subcontractor executes all and any further documents and takes all and any other actions as may be required in order to give effect to this licence. 

3.1 Employer’s design

The Employer provides the documentation/drawings to use as baseline for Contractor’s designs and the execution of the works as per the listed Appendices in the specification document number 348-348-9971909.
3.2 Parts of the works which the Contractor is to design. 
The Contractor is to provide designs as stated in the Scope document 348-348-9971909. The Contractor is to design, conduct design reviews, produce required drawings and provide plant and material which satisfies the following: 
a) The overall plant performance and efficiency specification.

b) The specified reliability; and keep maintenance costs to a minimum.

c) Local and statutory authorities. Each system and sub-system components are to be evaluated for compliance with PER of OHSACT of 1993 and be categorised (where applicable) according to SANS 347. 

d) Space constraints and construction requirements.

e) Local content.

f) The specified and applicable standards confirmed in the specification including all the legal requirements in respect of safety and the prevention of environmental pollution.
g) Facilitation of efficient manufacture, inspection, transportation, installation, maintenance, cleaning, and repairs.

h) Safe and satisfactory operation for a life expectancy of the chosen technology under the conditions prevailing at specific sites.

i) Prevention of undue stresses being produced by expansion and contraction due to temperature change and other local natural and manmade conditions.
j) Plant operation of 365 day per annum; and 24 hours a day (where applicable).
k) All material from which the equipment is manufactured from is compatible with the intended duty and service conditions. All equipment is suitable treated and protected from corrosion; and
l) All electrical equipment, forming part of the specified equipment shall be sealed against penetration by hose cleaning operations, and be also accessible for repair and maintenance.
The Contractor submits the following as part of his design:

a) Documents including equipment data sheets and specification for selected equipment, electrical cabling, and other associated equipment.

i. Mechanical equipment list

ii. Electrical load List

iii. Control philosophy

b) Manufacturer’s product data highlighting minimum efficiency reporting value (MERV) for filtration media.

c) Detailed electrical wiring diagrams including schematic and control circuits.

d) Detailed sequencing manner for installation procedure of works.

e) Technical literature for all items of equipment that forms part of the complete installation, including, evaporators, condensing units, refrigerant circuits, ventilation fans, electrical and control circuits etc.

f) Proposed corrosion protection systems, including data sheets for coating of proposed equipment.

g) List of recommended spares and technical specifications for the spares, part numbers and the stock levels required.

h) Basic Designs and Detail designs as required in the Scope document.  
3.3 Procedure for submission and acceptance of Contractor’s design
3.3.1 Submission and Acceptance of Contractor’s design
The Contractor submits his designs as stated in the Works information and as per the Scope document 348-348-9971909 and as stated in the VDSS to the Project Manager for acceptance. A reason for not accepting the Contractor’s design is that it does not comply with either the Works Information and/or the applicable law, and therefore the Contractor is to ensure that the first submissions (including design review reports as required) complies with the Works Information and/or the applicable law to avoid delays that may affect the completion dates (including sectional completion). In terms of the Contractor’s Programme (P6) it is expected that the design submission to be also sectional.   
As stated in the Contract the acceptance and/or not acceptance of the Contractor’s designs (including design review reports) can only be issued by the Project Manager using the official communication channels.  
Any acceptance and/or not acceptance, check, certificate, consent, examination, inspection, instruction, notice, proposal, request, test, or similar act by the Project Manager (including absence of acceptance and/or not acceptance) shall not relieve the Contractor from any responsibility he has under the Contract, including responsibility for errors, omissions, discrepancies, and non-compliances.
The Contractor is the Design Authority as defined in the Design Review Procedure (240-53113685). The Design Review Procedure shall take precedence in the review process. 

The Contractor is to submit an organogram with relevant experience and qualifications of the execution team. In addition to the above, project cost and schedule estimates related to the design is ton submitted to the Project Manager for acceptance. The Contractor shall submit procedures, method statement, Inspections and Test Plan prior commencement of works where design work is required. 

The Contractor submits all documents according to the templates that are referenced on the list of Standards. In order to expedite (improve) the review process as described herein below, the Project Manager may change the procedure stated below, and this change shall not constitute a compensation event. The process for the submission of documents is described below: 
a) The Contractor submits the documents/drawings to the Employer.

b) The Employer’s document controller registers the documents.

c) The Employer’s document controller will supply the documents/drawings to all relevant parties within the Employer’s project team.

d) The Employer’s project team reviews the documents/drawings and will submit all comments or inputs to the Employer and the Employer submits to the Contractor for consideration.

e) If the Employer finds major deficiencies in the submitted documents/drawings, the Contractor revises the documents/drawings and resubmits to the Employer. 
f) The Employer reviews the documents/drawings and if no major deficiencies are found, the Contractor organises a design review session. 
g) The Employer and the Contractor conduct a design review. 
h) If any fundamental errors were found in the designs or further actions are required, the Contractor record all concerns raised and revises the designs. 
i) The Contractor organises a design review session once all designs were revised according to the concerns raised by the Employer.

j) If no fundamental errors were found in the designs during the design review session, the Contractor compiles the design review minutes or report and submits it to the Employer.

k) The Employer’s document controller registers the report. 
l) The Employer’s project team reviews the Contractor’s report/minutes. If the report/minutes are not acceptable, the Contractor revises the report/minutes and resubmits to the Project Manager.

m) The Project Manager accepts the Contractor’s design once the report/minutes are accepted by the Employer’s project team. 
The Contractor is to implement the following activities for approval: 

a) The Contractor reviews, stamps, dates, and signs to signify his/her approval and submit in the manner required by the Employer in orderly sequence to cause no delay in the work, all Contractor’s drawings, equipment selections and/or samples required by the works or subsequently by the Employer. Contractor’s drawings, equipment selections and samples are to be properly identified as specified or as the Employer may require.
b) At the time of submission, the Contractor informs the Employer in writing of any deviation in the Contractor’s drawings, equipment selection or samples from the requirements of the works.

c) Each individual plant & material selection submission is to be accompanied by a copy of the applicable detailed technical specification. Each clause of this specification to be marked “Complies” or “Does not comply”, complete with reason stated, alternative offered and countersigned by the Contractor.
d) Plant & Material selection submissions are to be indexed like the index for plant & material part of the “Operating Instructions and Maintenance Manual”.
e) The Contractor is to submit two copies of drawings and Plant & Material selections along the channels agreed.
f) By submitting drawings, Plant & Material selections and/or samples, the Contractor represents that he/she has determined and verified all site measurements, site instruction criteria, materials, catalogue numbers and similar data, and that he/she has checked and co-ordinated each services drawing and sample with the requirements of the works.
g) The Employer reviews Contractor’s drawings, plant & material selections, and samples to cause no delay, but only for conformance with the design of the works. The Employer’s approval of a separate item does not indicate approval of an assembly in which the item functions.
h) The Contractor makes any corrections required by the Employer and re-submits the required number of corrected copies of the Contractor’s drawings, plant & material selections, or new samples until approved. The Contractor directs specific attention in writing on resubmitted drawings to revisions other than the corrections required by the Employer on previous submissions.

The following documents are supplied to the Employer by the Contractor as a minimum:

a) Documents, including detailed calculations such as hydraulic and pipe stress analysis (where required), pipe supports, handers and racks, 

b) Documents including equipment data sheets and specification for selected equipment, electrical cabling, and other associated equipment.

c) Dimensioned shop drawings showing the general arrangement of all plant and equipment including isometrics and P&ID’s or PFD’s where required. Sufficient views shall be given to ensure clarity and the drawings are to have at least a plan and two different elevations or sections giving overall dimensions.

d) Dimensioned shop drawings showing proposed method of fixing of all the plant and equipment

e) Detailed electrical wiring diagrams including schematic and control circuits.

f) Compliance and Electrical Certificates

g) Detailed sequencing manner for installation procedure of works
h) Detailed programme for the works in sufficient detail as to represent the units of work to enable the representative to assess the progress of the works
i) Technical specification and literature for all items of equipment that forms part of the complete installation. 
j) Proposed corrosion protection systems, including data sheets for coating proposed of equipment

k) List of recommended spares and technical specifications for the spares, part numbers and the stock levels required

l) Detailed building works for complete works
m) Detailed maintenance, reliability, control, and operating philosophies

n) Testing, balancing, and commissioning procedures
o) Plant and material acceptance testing
p) Detailed operation & maintenance manuals with As-Built drawings & Commissioning Results
q) Plant codification lists for each section of the works
r) Construction competition reviews

s) Acceptance testing reviews

t) Quality assurance reports

u) Close out reports 

3.3.2 Engineering Changes

Engineering change is any change to an established baseline related to the plant system, such as its configuration documentation, design requirements, technical operating documentation, operating margins and set points, replacement of alternative components with equivalents.

Any change on the Contract shall be recorded and correct procedure shall be used to implement the change on the project.

3.3.3 Engineering Change Procedure

The Contractor takes note of the Employer’s Engineering Change Procedure (240-53114026).  The Engineering change procedure applies to the Employer’s personnel or Contractors performing engineering or engineering related work where the quality of the engineering work performed is the direct responsibility of Eskom.

3.3.4 Design Change Procedure

The Contractor is the Design Authority as defined in the Design Review Procedure (240-53113685). The Contractor is responsible for following this design procedure and conducts all the design reviews as specified in this procedure. The Contractor is responsible for conducting the following design reviews where applicable:

a) Design Freeze Review

b) Integrated Design Review

c) Construction Completion Review

d) Acceptance Testing Review

3.3.5 Procedure for Submission of Change Documents

The Contractor shall complete the engineering/design change [report/request] within [5 days] or such other time period that the Project Manager and Contractor agree is reasonable in the circumstances, of the Project Manager’s instruction changing the Works Information.  

In completing the engineering change report, the Contractor:

a) Takes into account the impact of the Project Manager’s instruction on the Contractor’s works, in accordance with the Works Information and the Contract;

b) Provides the Project Manager with the impact on the Contractor’s detailed design, programme, costs, Completion Date, Key Dates, execution and methodologies;

This information from the Contractor will be sent to the Others on the Project in order to integrate the system and ensure that the Employer’s objectives in relation to the Project are achieved.  Likewise, the Contractor may during the Contract receive such information, via the Project Manager, from Others.  The Contractor assesses this information to:

a) Assess the impact of this on the Contractor’s works, in accordance with the Works Information and the Contract;

b) Provide the Project Manager with the impact on the Contractor’s detailed design, programme, costs, Completion Date, Key Dates, execution and methodologies;

Within [5 calendar days] or such Other time period that the Project Manager and Contractor agree is reasonable in the circumstances of the Contractor submitting (or receiving this information), the Contractor attends a meeting with the Employer and Others on the Project to align the Employer, Contractor and Others’ works and ensure compatibility and integration of the Project;

The Contractor submits its revised information within [5 calendar days], or such other time period that the Project Manager and Contractor agree is reasonable in the circumstances, taking into account all information received from the Employer and Others.

Where the Contractor is unable to comply with the Contract or Works Information, he promptly notifies the Project Manager of:

a) Details of the non-compliance;

b) Impact of non-compliance on his and Others;

c) Remedial steps to be taken.

3.4 Other requirements of the Contractor’s design

3.4.1 General

The Contractor provides all plant, equipment, materials and services and executes all work necessary to fulfil all requirements specified in this Works Information. The Works complies with Professional Engineering practices and standards for fossil fuel power plants and is designed for the environmental conditions prevailing at Medupi Power Station.

The Contractor liaises with the Employer and Other Contractors to ensure the successful completion of both contract requirements. This is a site activity and is coordinated by the Project Manager.

The contract includes the provision of the following:

a) KKS labels (Employer provides the KKS codes)

b) Contract management including site management and Subcontractors

c) Contract programming

d) Provision of draftsman (drawing) services

e) Cost control and progress reporting

f) Quantity surveying documentation

g) Quality assurance

h) Quality control

i) Acceptance testing and handing over to the Employer

j) Documentation

k) Maintenance support

The Contractor is required to guarantee the complete Emergency Preparedness Public Address System as per the requirements of the Contract.

3.4.2 Other requirements

The Contractor is to design, produce required drawings and select plant & material which satisfies the following:

· The overall plant performance and efficiency specification;

· The specified reliability; and keep maintenance costs to a minimum;

· Local and statutory authorities. Each system and sub-system components are to be evaluated for compliance with PER of OHSACT of 1993 and be categorised (where applicable) according to SANS 347.

· Space constraints and construction requirements;

· The specified and applicable standards confirmed in the specification including all the legal requirements in respect of safety and the prevention of environmental pollution.

· Facilitation of efficient manufacture, inspection, transportation, installation, maintenance, cleaning and repairs;

· Safe and satisfactory operation for a life expectancy of the chosen technology;

· Prevention of undue stresses being produced by expansion and contraction due to temperature change and other local natural and manmade conditions;

· All material from which the equipment is manufactured from is compatible with the intended duty and service conditions. All equipment is suitable treated and protected from corrosion; and

· All electrical equipment, forming part of the specified equipment shall be sealed against penetration by hose cleaning operations and be also accessible for repair and maintenance.

· The Contractor shall manage and execute the engineering, quality control, inspections, plant and material selection, preparation of installation drawings, testing, balancing, commissioning and preparation of operating and maintenance manuals. The Contractor’s submissions includes, but is limited to the following;

· Detailed design

· Plant and material selection;

· Installation drawings

· Codification and labelling of the plant

· Testing, balancing and commissioning Documentation

· Operating Instruction and Maintenance Manuals

· Inspection Record Cards/Checklists

· Quality assurance.

· Employer interfacing information such as;

· Electrical Load lists

· Virtual Signal List & Alarm List

· Mimics

· Any applicable certification required by South African regulations.

· The Contractor shall also comply with the requirements of the specification document 348-9971909 and any other requirements in this document.

3.4.3 Power Supply interruptions

The Contractor ensures that the supplied equipment is capable of safely shutting down the plant without damage in the event of partial or total loss of electrical power and shall be designed to accept a sudden restoration of electric power, without damage and without operator intervention.

3.4.4 Certificate of Compliance

The Contractor ensures that all permanent or temporary installations are subject to statutory requirements as explained in OHS Act and SANS 10142-1 for the wiring of premises which include the issuing of a Certificate of Compliance (COC) before an installation is accepted by the Project Manager. A COC shall be provided where it is required as well as the installation of all required cables and related equipment.
3.5 Use of Contractor’s design
Clause 22.1 is applicable on Contractor’s design and deliverables as stated in the Works Information and scope document number 348-9971909. 
The Contractor submits the Contractor’s Design Documents to the Project Manager for acceptance at the times and in the manner and format stated in the Works Information Acceptance of Contractor’s designs, to be applied as stated in Clause 21 of the Contract.

The Contractor grants to the Employer, with effect from the starting date, in the case of documents or other matters not yet in existence, with effect from the creation thereof (and notwithstanding the Completion or termination of this contract), an irrevocable royalty-free non-exclusive licence to use all of the documents provided to Provide the Works (including, but not limited to calculations, computer programmes and other software, drawings, manuals, models and other documents of a technical nature), for any purpose whatsoever, including for the purpose of operating, repairing, maintaining, dismantling, re-assembling and making adjustments to all parts of the Works. The Contractor ensures that each Subcontractor executes all and any further documents and takes all and any other actions as may be required in order to give effect to this licence.

3.6 Design of Equipment

The Contractor to provide works as stated in Clause 23.1 of the Contract. 

3.7 Equipment required to be included in the works. 
The Contractor is required to provide lifting facilities and other equipment required for the execution of the complete works. 
a) The Contractor to provide Equipment and the material required for execution of the works. 

b) The Contractor to supply all required tools, Equipment to their employees in order to perform              their tasks.
3.8 As-built drawings, operating manuals, and maintenance schedules

The Contractor is to provide As-built drawings, operating manuals, and maintenance schedules the before Completion of each Section of the Works.  
The Contractor shall provide as-built drawing for completed works. The Contractor provides General Arrangement (GA) diagrams to be accepted by the Employer. All drawings are to meet the requirements of the document 348-9971909 and the Eskom standards listed the specification document number 348-9971909

4 Procurement

4.1 People

4.1.1 Minimum requirements of people employed on the Site. 
People employed to Medupi Power Station should undergo Safety Induction and Covid-19 screening and other courses before they can access the project site (Medupi Power Station). 
The Contractor does not alter previous decisions communicated to the Employer or Others without the Employer’s acceptance or agreement.  

Any new foremen/Supervisors appointed by the Contractor after Contract Date or during provision of the works are fully conversant with respect to details of the methodology and communication process existing, prior to accessing the Site. The Contractor provides the CVs and all other relevant information of the replacement employees to the Project Manager as soon as possible after he is aware that a skilled employee will no longer be working on the Contract.  

Permits for foreigners – The Contractor informs the Employer of any need to employ foreigners and on acceptance by the Employer, the Contractor arranges permits for such employees. The Contractor informs the Employer when the services of specialists are required. The Contractor ensures interface with Others is managed before commitment is made to bring international specialist to Site.  

The Contractor ensures that his workforce is trained and competent to perform their respective duties.  The Contractor provides CVs and proof of qualifications of his key persons (listed in paragraph 2.7 of this Works Information) as a returnable schedule. Labour from designated areas – Where local labour resources can be utilised, the Contractor ensures that in their recruitment processes, preference is given to such resources. The Medupi information centre can be utilised for recruitment of local labour. 

Industrial Relations: The Contractor will remunerate employees in accordance with the acceptable market remuneration / minimum wage. The Contractor manages all industrial relations matters with his employees.

Eskom Holding SOC Ltd as an entity is a State-Owned Company which is subjected to regulatory compliance as applicable to Government. Medupi Power Station Project Site is designated as a National Key Point in terms of the National Key Point Act 102 of 1980. Eskom is required to comply with the requirements of paragraph 5 of the Minimum Information Security Standard (MISS) that seeks to implement a criminal check/ screening process which intends to identify individuals who might through their actions and/ or behaviour, could pose a risk to the operation of Eskom Holdings SCC Ltd. As such, the Contractor is hereby instructed to ensure that the Contractor’s employees on Site are screened by means of criminal clearance verifications with the South African Police Service (SAPS) Criminal Record Centre (CRC) or accredited supplier linked to SAPS AFIS system and provide proof to Eskom security delegated team before access to Site is granted.
4.1.2 BBBEE and preferencing scheme

The Contractor shall maintain or improve upon their current B-BBEE Contribution level for the duration of the contract. The Contractor will be required to submit a new B-BBEE certificate within three (3) months, should ownership of the company change during the life of the contract.

The Contractor is expected to submit a valid B-BBEE Verification Certificate from a SANAS accredited Verification Agency each year. Failure to submit such a Certificate may be regarded as the breach of the contract by the Employer. 
4.1.3 Accelerated Shared Growth Initiative – South Africa (ASGI-SA) (SDL&I) 

The Contractor complies with and fulfils the Contractor’s obligations in respect of the Accelerated and Shared Growth Initiative - South Africa in accordance with and as provided for in the Contractor’s SDL&I compliance schedule.

4.1.4 Local content and production

The scope of work contains products/goods, material, components and parts that are designated which means that they have stipulated minimum threshold for Local Production and Content that must be complied with, or the Contractor should obtain an exemption from the Department of Trade, Industry and Competition.
	Commodity
	Components
	Local Content

Threshold

	Electrical and Telecom Cables
	Cabling
	90%

	PPE
	Reflector Vests, Jackets, Boots, G Textiles, Clothing, Leather & Footwear, etc.
	100%


Local-to-site Procurement (Lephalale), The Tender is expected to subcontract and or procure a minimum of 10% of the Contract amount with suppliers based in Lephalale Local Municipality Area. These are some of the services/goods that may be procured: 

· Transport of Labour and Material,

· Consumables,

· Medical Surveillance services, etc.
4.1.5 Skills Development (not weighted criteria)

The Employer intends to improve skills development by ensuring that technical support is directed towards enhancing supply capacity and capability within the industry or sector of operation. By doing this the capacity and competitiveness of the local supply base will be increased and the goals of shared growth, employment creation, poverty reduction and skills development will be achieved.

a) Employer will apply the standard for developing skills through infrastructure contracts published by the Construction Industry Development Board on 23 August 2013 (Board Notice 180 of 2013, Government Gazette 36760) (“the CIDB Skills Standard”) to the contract. As such, for the purposes of the CIDB skills standard the “contract skills development goal” of 0.25% of accepted contract amount.

b) The contract skills development goal will be part of the contract as the above percentage of accepted contract amount. Value-Added Tax is excluded from the contract amount and so will also be excluded from any contract skills development credits which can be claimed by the Contractor. Note that any skills proposed shall be in line with this requirement.

c) This will not be an evaluation criterion but a condition of contract.
d) Skills development shall have specific targets that address some of the Employers core, scarce and critical skills.

e) On skills development beneficiaries, priority shall be given to the residents of Waterberg District Municipality, who meet the intake level requirement.
The Contractor shall keep accurate records and provide the Project Manager with reports on the Contractor’s actual delivery against the above stated SD&L criteria. 

The Contractor’s failure to comply with his SD&L obligations constitutes substantial failure on the part of the Contractor to comply with his obligations under this contract. 
Potential Skills to be developed (subject to agreement):

	Skills Type
	Number of

learners
	Intake
	Output

	Electrical Artisans
	3
	Trade Test Preparation
	Trade Test Certificate

	Total
	3
	
	


The above-mentioned Skills are a guideline. The actual skills/trade type may be negotiated. However, expenditure of 0.25% of the Acceptable Contract Amount in accordance with the CIDB CSDG is a Condition for Contract Award.
The Contractor is free to propose any other relevant Skills Development that will be feasible and benefit the previously disadvantaged communities. This may even include Workplace Integrated Learning (WIL) from the TVET Colleges around Limpopo Province.
4.1.6 SDL&I Penalty 
a) Employer shall be permitted to retain 1.5% (two and half percent) of the invoices (excluding VAT) as security for the fulfilment by the Contractor of their SDL&I obligations. 

b) Once the Employer has verified that Contractor have fulfilled their SDL&I obligations, the 1.5% retained shall be approved for reimbursement by the Employer to the Contractor within ninety (90) days of verification by the Employer. 
4.1.7 Reporting

a) The Contractor shall on a monthly /quarterly basis submit a report to the Employer in accordance with data collection template on their compliance with the SDL&I obligations described above.

b) The Employer shall review the quarterly reports submitted by the Contractor within sixty (60) days of receipt of the reports and notify the Contractor in writing if their SDL&I obligations have not been met.

c) Upon notification by the Employer that the Contractor have not met their SDL&I obligations, the Contractor shall be required to implement corrective measures to meet those SDL&I obligations before the commencement of the following quarter, failing which retention clauses shall be invoked.

d) Every contract shall be accompanied by the SDL&I implementation schedule which shall be completed by the Contractor and returned to SDL&I representative for acceptance before contract award. This will be used as a reference document for monitoring, measuring, and reporting on the Contractors progress in delivering on their stated SDL&I commitments.
SD&L Performance Guarantee is Not Applicable as the risk on non-fulfilment of SDL&I obligation is very low.

4.1.8 Job creation

Job creation proposals by Contractor will not form part of the tender evaluation criteria. It is, however, part of the Employers contribution towards the Government’s job-creation initiative as contained in the New Growth Path (NGP) and the New Development Plan (NDP).

The Employer has made several empowerment commitments to the local communities surrounding the areas where it conducts its construction activities. Amongst these, are commitments to be considered for local empowerment possibilities in its procurement strategy. In doing this, Employer is seeking to ensure that the local communities’ benefit from its procurement spends through wealth generation and capacity development; and that this benefit is spread as widely as possible throughout the community.

The Contractor is therefore encouraged to propose to the Employer the number of semi-skilled and unskilled labourers that will be sourced from local to site in support of this empowerment commitment to the local communities.
4.2 Subcontracting
As stated in Clause 26 of the conditions of the contract NEC document: 

· If the Contractor subcontracts work, he is responsible for Providing the works as if he had not subcontracted. This contract applies as if a Subcontractor’s employees and equipment were the Contractor’s.

· The Contractor submits the name of each proposed Subcontractor to the Project Manager for acceptance, and the Contractor does not appoint a proposed Subcontractor until the Project Manager has accepted him.
4.2.1 Preferred Subcontractors
Undertaking to sub-contract 10% of the contract value to EME or QSE’s that are at least 51% Black Owned. 

The names of all proposed Subcontractors should be submitted to the Project Manager for vetting and accepted as a returnable schedule. 
4.2.2 Subcontract documentation, and assessment of subcontract tenders

1) Subcontracting agreement signed by both with Subcontractor’s company registration documents (CK, CSD, B-BBEE certificate or affidavit).

2) Copies of sub-contracting contracts (agreements) or copies of letters from the Contractor to the Subcontractor, stating the intent to sub-contract. The Contractor should sign both documents and the Subcontractor(s) earmarked.

3) B-BBEE certificate from SANAS accredited rating agency or Sworn Affidavit from National Treasury / DTI certified by commissioner of oath will be used to verify supplier’s status. 
4.2.3 Limitations on subcontracting

Eskom Procurement and Supply Chain Management Procedure 32-1034 is applicable read together with the following: 

a) The Contractor does not sub-contract more that 25 % of the contract value to other enterprise that does not have equal or higher B-BBEE status level, unless the intended Subcontractor is an Exempted Micro Enterprise that has the capability and ability to execute the sub-contract. 

b) In relation to a designated sector, the Contractor will not be allowed to sub-contract in such a manner that the local production and content of the overall value is reduced below the stipulated minimum threshold (Percentage of the specific contract).

4.2.4 Attendance on Subcontractors
The Subcontractor attends all meetings which the Contractor attends, and all meetings as required by the Employer which requirement is not a compensation event.

4.3 Plant and Materials

4.3.1 Quality

All work should be done in accordance with the quality management system of Medupi Power Station as set out in the Contractor Quality Specification (348-389557), in addition to the ISO 9001:2015 quality management system. High quality standards are also assured by conforming to the following:

a) The use of sound design and engineering principles,

b) The design process uses a good performance and functional specification,

c) It is ensured that the installation conforms to the User Requirement Specification and Works Information.
d) Design Review Procedure is followed.

e) Engineering Change Procedure

f) Electrical Asset Creation Process

g) QA/QC on project (manufacturing, installation, commissioning)
4.3.1.1 Records Books 

The Contractor to develop, document via procedure for Project Manager’s approval and thereafter implement a system for collation or quality verification records, including change management records into Manufacturing, Construction and Commissioning Record Books. 

· Contractor to review data book progressively during 30%, 70% and 100% of the completed work and provide valid comments in the form of comment sheet per each stage of review to the Employer prior Employer’s review. 

· No data book shall be reviewed by the Employer without Contractor’s reviewed evidence and comment sheet Indicating first review second review with addressed comments and final review. 

· The Contractor to develop Data book Register and maintain for the duration of the project said Procedure shall define format, content and structure of Record books and process of compilation and handover and shall, as a minimum, conform to the following: 

a. Record Books shall be provided by the Contractor for. 

· Manufacturing - Prepared for each individual “Purchase Order refer to 240-109836134 clause 3, Scope of work and Employer requirements”. Only manufacturing records per discipline e.g., Civil, Structural steel, Mechanical, Electrical, C&I works etc. 

· Construction/Erection - Prepared for Each Discipline as in bullet 1, each geographical area for civil works and for systems/sub- systems for mechanical and electrical systems including C&I separately: Commissioning - prepared for each commissioned system. 

Note: Record books shall be not combined on Data Dossier. Manufacturing, Construction/Erection and Commissioning shall be separated. 

· The Contractor need not include documents and drawings etc. that have been approved by the Project   Manager which are included in SPO and shall instead provide and include an index of such documents in the Record Books on the basis that the originals are in SPO and traceable via the “Index”.

· Record Book shall be written in English or provided with an English translation. 

· The index of all Record Books shall be submitted to the Project Manager for approval. 

· As the work progresses, Contractor shall compile Record Books progressively with the original material certificates, installation, erection, testing, inspection and change management documents and shall verify continued and accurate updating via weekly review and spot checking against inspection performed that week.

· Contractor shall report the status of Record Book compilation progress at Weekly Progress / Quality Meetings together with the Data book Register.  
· Record Books shall be endorsed by stamp, date and signature of the Contractor and the Employer signifying completion and accuracy when complete.

· Each Record Book shall have cover sheet (With a Sleeve pocket to insert a cover sheet) of A4 size paper and a spine label on which is printed the following: 

· Title of Document, Contractor’s company logo, Unique number/SPO, Name of Project 

Contractors’ Job Code, Contractor Document number, Eskom Document Number, System KKS       number, System Description, Document type “Manufacturing or Construction or commissioning”, Contractor’s number, Name of Contractor, Volume Numbering (1 of …. or 1/10) xv. Address of Contractor, Column for signature by Contractor Representative and Employer’s representative 

· All Manufacturing Record books shall be Completed, Approved, and handed over to the Employer not later than (7) Seven days after Delivery Inspection on site Prior Installation/Construction Phase.

· All Construction Record books shall be Completed, Approved Safety Cleared, and handed over to the Employer not later than (7) Seven days after Final inspection (AFI) Prior Commissioning Phase

· For other civil / Earthwork, All Construction Record books shall be Complete, Approved and handed over to the Employer prior taking over section of works. 

· All Commissioning Record books, Operating, maintenance and training manuals shall be Completed, Approved and handed over to Eskom not later than (7) Seven days after the last test prior taking over of completed works (TOC) 

· Construction Record Book shall be compiled in A4 size with 4-post binders in loose-leaf form with numbered pages such as, Page 1 of 10 or 1/10 whichever sequential counting method that clearly identifies page numbering. 

· Summary table of each volume’s contents shall appear in all volumes. Volumes are to be numbered e.g., 1 of 3, 2 of 3, 3 of 3 etc. both on spine and front cover. 

· The binders are to be robust and not subject to distortion by impact during shipping. The binders shall not be over filled and contain only a suitable number of documents to enable convenient handling. 

· Contents shall be sectionalized and separated by properly labelled dividers. 

· Contents shall be placed in the relevant sections and sections shall be separated by properly labelled section dividers/separator sheets easy referencing with going through the content. 

· All section dividers/separator sheets shall be made of card and shall bear the Section Identifier - 1, 2... 

b)  The contents of each section, e.g., Section 1, Section 2, etc., of the Record Book shall be placed directly behind the relevant section dividers/separator sheets and each document shall be clearly marked with the following:

· Relevant section letter, Page number - every document shall receive a page number, in each section the page numbers shall run consecutively. 

i) Record Books shall contain as a minimum: 

· All material Reports and Certificates, All Inspection Reports, All Test Reports, All Release Notes, All Change Management Reports, All drawings or an index of drawings identifying drawing No. and revision status, All Defect Reports, All Procedures or an Index of Procedures, All Inspection and Test Plans if used as a Quality Verification Record or an Index of Inspection and Test Plans if used as an assurance and control document, All Drawings or an Index of Drawings.

4.3.1.1 Statutory Records 

The Contractor shall submit a statutory compliance file containing minimum documents as follows: 

a) Electrical Equipment 

· Statutory register and COCs 

b) Civil Structure 

· Statutory register, Professional Engineering Certificates, Glazing Certificates, Sewer Certificate (Subjected to exemption)

c) Pressurised Equipment 

· Statutory register, Certificate of Conformance for PER equipment, Inspection and Hydraulic 

    Pressure Test Certificate for PER equipment and Pre commissioning Certificates.

d. Lifting Equipment 

· Statutory register – lifting equipment, Statutory register – passenger conveyance lifts, Load test certificates for all lifting equipment’s and Transformer Impact Recording, Functional safety clearances for all equipment, Operating procedures, and Maintenance Procedures.

e.   Permanent KKS certificates (no temporary labels to be allowed at take-over) 

f.    Software and applications to interrogate the equipment, i.e., power electronics, All the configuration files and settings implemented, FAT, SAT and SIT Reports, CEMS, Dust and gaseous emission correlation tests to be completed.

· Boiler   Registration certificate

4.3.1.2 Handing over of Record books/Data Books by Contractor  

QA Completeness review 

· After addressing all comments given to the Contractor during QC 100% review of data books by the Employer, 

· The Contractor shall request QA via Project Manager to perform completeness review of the record books. 

· The Employer Quality Assurance team will also make reference to the data book checklist (200-616427) for compliance of format and lay out of the Record Book / Data Book.
4.3.2 Plant & Materials provided “free issue” by the Employer. 
Some network infrastructure and equipment used during the construction phase of Medupi Power Station shall be re-used to the maximum extent possible during the permanent phase. An assessment of the existing infrastructure/equipment and its re-usability needs to be completed before commencement of detailed design; this also should ensure that the re-used infrastructure/equipment can be fully integrated with permanent designed equipment/infrastructure without unnecessary duplication of equipment.
4.3.3 Contractor’s Procurement of Plant and Materials

The Contractor is to take all necessary steps to ensure that all Plants and Materials are adequately protected against damage during shipping, transport, and storage.
The Contractor provides a list of Equipment on each Section of the work for verification, review and acceptance. 

The transport section (functional unit) is suitable for handling and removal by providing mechanism for crane hooks. The transport section is suitable for handling and removal by providing mechanism to avoid damage to the functional unit. 

Transportation of the equipment will be done as per the requirement of 240-56178825. During transportation the electrical components are packaged in such a way that damage is prevented. Components of the functional unit that are transported separately are marked accordingly and are easily identifiable. 

The Contractor supplies the labelling for the Plant that forms part of the works. The Contractor provides labels for the EPPA System and equipment’s according to the labelling specification.

The labels are affixed in such a way that they are easily legible and not obstructed by the wiring or by other components. 

Clamping methods applied to the labels ensures that removal of the labels requires force.  The Project Manager will approve the proposed method of clamping prior to use.

The Contractor supplies the Project Manager, for verification and acceptance purposes, with a label list showing the text only. The Project Manager will approve the positioning and designation of labels. 

The KKS codes are used accordingly on documentation (e.g. drawings, manuals, equipment lists, cable schedules etc) as a unique identification means. References to plant are accompanied by the relevant KKS code for that item of plant.

Abbreviations to descriptions on the labels are generally not acceptable. Where abbreviations are unavoidable, due to the limited number of characters that can be engraved/etched on labels, the abbreviations are submitted to the Project Manager for acceptance. The Contractor makes use of the Employer’s Standard Plant Related Abbreviations for Inter-System Use.

Where equipment requires prolonged storage due to the outage movement, the Contractor will store the equipment on Site as per manufacture’s recommendation. 

Warranty period for the plant and materials ( as supplied by the Contractor) will start from the take-over of the Section of the works. 
4.3.4 Spares and Consumables. 
The Contractor provides as part of the operating & maintenance manual, a recommended parts list as well as a proposal for the execution thereof:

a) The Employer is responsible for procurement of recommended spares.

b) The Contractor is responsible for ensuring that consignment spares are available on time of need.

Each recommended spare part is to be uniquely identified with a part number, which can be cross referenced to a part list and associated drawing. The Employer prefers that support from the OEM is available locally in South Africa. 
Spares and consumables are to be as per technical specification document from the Employer, where applicable, and the following noted. As stated herein this section above, The Contractor supplies the Employer with a detailed complete list of all spares required in order to maintain the equipment for the first two years of operation (this is applicable Sectionally).  This list of spares is supplied three months before the delivery of the first Equipment and/or commissioning of the system (where applicable).

At the same time, a second list containing recommended spares for the subsequent two years of operation is also supplied.

Included in the list is the description of the individual spares, type, part ordering number and supplier information.

Where so requested by the Employer, additional equipment is supplied at the same price as quoted in the Activity schedule. 

The Employer prefers that support from the Original Equipment Manufacturer (OEM) is available locally in South Africa. The Contractor is required to provide technical and product support for the design life.
4.4 Tests and inspections before delivery

Inspection activities during manufacturing shall be managed according and in line with the Manufacturing Inspection and Testing work 348-860842. 

All inspections and testing to be performed in accordance with the Quality Control Plan (QCP) and Method statement developed by the Contractor in consultation with the Employer. 
Where a product nonconformity is identified by the Contractor to a system, product or process, a nonconformity shall be documented and reported to the Employer as detailed on Control of nonconformity product (348-890104)

4.5 Marking Plant and Materials outside the Working Areas

All Plant and Material paid for by the Employer shall be clearly labelled as being the Employer’s property.

4.6 Contractor’s Equipment (including temporary works).

The Contractor provides the following to complete the works:

a) All scaffolding required.

b) Any equipment necessary to complete the works.
c) Lifting facilities.

The Contractor supplies, installs, maintains, and removes all temporary construction facilities and utilities necessary to provide the works.
4.7 Cataloguing requirements by the Contractor
Not applicable 
5 Construction
5.1 Temporary works, Site services & construction constraints

5.1.1 Employer’s Site entry and security control, permits, and Site regulations. 
The Contractor makes his own assessment of, and allowance in his Prices for any access problems because of the Employer’s security requirements, permits and/or site regulations. No change to the Prices, Key Dates and/or Completion Date is allowed on account of difficulties of access to the works, or for the requirement of working adjacent to or in the same area as Others.

Access to the Site is controlled and governed by the terms and conditions laid down by the Employer. The Site is shown to the Contractor during the site meeting or clarification meeting. Parameter of the proposed Site will be included in the Site Information.

The Contractor liaises with the Employer security staff to obtain temporary permits for his staff and vehicles which will be working within the station.

The Contractor submits his application for vehicle permits to the Project Manager. The personnel and vehicles entering and leaving the site are subjected to routine searches and alcohol tests. The Contractor ensures that all its employees and Subcontractor always carry their access cards.

 The Contractor obtains a “Gate Permit” from the Employer before materials and equipment can be removed from site. A “Gate permit” gives an itemised list of materials and equipment to be removed from site. 

The Employer refuses access to Site for reasons such as security concerns, disorderly conduct, substance abuse, misconduct, criminal records. The Contractor is not entitled to a change in Prices, Key Dates and/or Completion Date because of the Employer refusal for reasons stated above. 
5.1.2 Restrictions to access on Site, roads, walkways, and barricades. 
The Contractor is required to comply with all the Employer site rules and regulations. The Contractor complies with the Site a copy of which is available at the Project Manager’s offices.

Any subject within the authority of the Project Manager may be addressed by a site regulation which does not constitute a compensation event.

Before work starts on Site, a kick-off meeting is held with the Contractor and the Project Manager, to explain in detail all requirements of the site regulations.

The Contractor is issued with current site regulations at the project kick-off meeting. The file remains the property of the Project Manager and the Contractor is responsible for its maintenance and updating to include new or revised regulations as issued by the Project Manager during the course of the works. 
5.1.3 People restrictions on Site; hours of work, conduct and records. 
People restrictions and constrains, the hours of work will be as per the project calendar, conduct and records as per the Terms and Condition of the Contract. The Contractor would need to comply with the Employers site rules and regulations. Restrictions and hours of work will apply at the Medupi Power Station. The Contractor keeps records of his employees on Site, including those of his Subcontractors which the Project Manager or Supervisor has access to at any time. These records may be required by the Employer at any given time for the following but not limited to:

a) Emergency (evacuation/drill) and investigations

b) Labour unrest

c) Absenteeism 

d) Sick leave 

e) Assessments (labour hours timesheets)

5.1.4 Health and safety facilities on Site 

The Contractor provides a First Aid service and SHE representative to his employees and Subcontractors. In the case where these prove to be inadequate, like in the event of a serious injury, the Employer’s medical centre and facilities will be available. Outside the Employer’s office hours, the Employer’s First Aid Services are only available for serious injuries and life-threatening situations. The Employer recovers the costs incurred, in the use of the above Employer’s facilities, from the Contractor.
5.1.5 Environmental controls, fauna & flora, dealing with objects of historical interest. 
Refer to EMP and ROD referenced above and as per the latest revision of the Employers Environmental Policy which is available from the Project Manager. 

5.1.6 Title to materials from demolition and excavation

The Contractor has no title to materials from excavation, demolition, stripped and material removed from Site or the plant (e. g. copper, steel etc). The Contractor notifies the Project Manager when such materials are found, and the Project Manager instructs the Contractor how to deal with such materials. In circumstances where certain equipment is required for spares, the Project Manager gives special instruction detailing a specific storage area and identifying which parts to be stripped and where different types of stripped material will be taken to. 

5.1.7 Cooperating with and obtaining acceptance of Others

There will at times be Others working in the same area as the Contractor, it is the responsibility of the Contractor to co-ordinate his work with the Employer and Others to maintain harmonious working conditions on site.

During the progress of the works the Contractor provides access to Others who also execute work in the same area, as and when required and agreed with by the Employer.

The Contractor makes his own assessment of the challenges which may be encountered for providing access to and interfacing with Others (this includes access difficulties experienced during construction or commissioning phase). Where there are difficulties or unresolved interfacing or access issues the Contractor shall ensure that they meet with Others to find solutions or resolve issues without impacting his/her execution of the works. The Contractor is not entitled to a change in Prices, Key Dates and/or Completion Date because of the interface obligations or the Contractor’s assessment.

If the Contractor and Others are unable to resolve the problem, they will meet with the Employer to find a solution or resolve the issue. The Employer will issue an instruction to the Contractor and Others on how to proceed. In areas where affected property or area is to be shared for work by different Contractors, affected Contractors shall cooperate and manage their agreements and notify the Project Manager of such agreements. 
5.1.8 Publicity and progress photographs 

No photographs are allowed to be taken or distributed on site unless permitted to do so by the Project Manager and the following process adhered at all times. The taking of photographs at the Power Station including the Project works is restricted and subject to the approval by the Project Manager.

For the purpose of the Progress Reporting Requirements, the Project Manager may prohibit the taking of such photographs and/or require that all such photographs be taken by an official Employer photographer. In the latter event, the Contractor is required to make arrangements directly with the photographer for the taking of the photographs required by the Contractor for the purpose of the Progress Reporting Requirements.

All publications on site shall not contradict Eskom regulations and publication legislation in general.
5.1.9 Contractor’s equipment

Contractor is responsible to all equipment brought onto site. Refer to Clause 4.1 in SANS 1200 A 

a) The Contractor’s equipment does not impair the operation or access to the plant.

b) The Contractor provides all, or any temporary and expendable materials required for the storage of material.

c) The Contractor provides a list of all equipment on Site whether it is owned or hired, for record purposes.

d) The Contractor ensures that all his equipment on Site including scaffolding has unique identification. 
Note : For any removal of equipment from site, refer to section 5.1.1
5.1.10 Equipment provided by the Employer. 
The Employer will not provide any equipment to the Contractor. All necessary equipment needs to be provided by the Contractor. 
Should a mobile crane be required for the execution of the works, it will be supplied by the Contractor. The availability of the crane shall be made at least seven (7) days prior to the required date. The Contractor will be responsible for operating the crane. The Contractor is required to provide its own certified riggers. The Contractor is not entitled to a change in Prices, Key Dates and/or Completion Date due to unavailability of mobile cranes. 

The Contractor shall ensure that the test certificates (e.g., load testing of cranes) for the equipment are available prior to use. 
5.1.11 Site services and facilities 
The Employer will provide power, water, waste disposal, sewer connection points If applicable. The Contractor will be responsible for the material and connection to the connection points or to the mains. The Employer will fill the water tanks with water and remove sewage from septic tanks.

It is required, for the proper co-ordination and execution of the works that the Contractor has an office on site for the duration of the contract.

A site will be made available to the Contractor for his yard within the Medupi Power Station security area. The proposed site will be shown to the Contractor during site meeting or clarification meeting. The yard is a raw site and will be used by the Contractor for the establishment of offices, workshop, and stores. The Contractor’s yard is subject to periodic inspection and audited by the Project Manager or delegation.

The location of the nearest sewer manhole, power distribution point, portable water connection, storm water channel and road access point are indicated by the Employer. The Contractor is responsible for connection to the closest point of supply.

The Contractor conducts underground surveys before any excavation is performed as per the Employer’s SHE specification and Occupational Health and Safety regulations. 

5.1.12 Supply of Electricity

Electricity is made available for construction purposes free of charge from power points which will be indicated by the Project Manager. The Contractor is responsible for the provision of the reticulation system from the point of supply. Both 220 (AC) Volt and 380 (AC) Volt are available on request. All points of supply requested by the Contractor are provided in terms of quantity and location at the discretion of the Project Manager.

No guarantees of power supply quality are given, and power supply breaks of some duration may occur without warning. Planned outages are also a possibility. The Contractor plans at his own expense to improve continuity and quality of power where necessary for any reason and no claim or Compensation Event of any nature relating to power failures is considered.

No connection is made to the permanent installation at the Medupi Power Station without the prior acceptance of the Project Manager.

The power supply is managed in accordance with the latest revision of the Employer’s safety regulations i.e.:

a) 240-114967625, Operating Regulations for High-Voltage Systems

b) 36-681, Generation Plant Safety Regulations 
c) CoC for the site installation is required prior to power being switched on

All electrical works to be carried out by a Master Installation Electrician (MIE). The Contractor also provides a Certificate of Compliance (CoC) to prove compliant to electrical work. The certificate to be included into data book for review.

5.1.13 Lighting

The Contractor at his own expense provides temporary local lighting in accordance with the requirements of the OHS Act as amended. 
5.1.14 Water

Water will be made available on request free of charge from water points on site. The Contractor supplies at his own cost all the necessary connections, fittings, piping work, temporary plumbing, and pumps necessary to lead water from the Employer’s points of supply to the various points where it is required. The Contractor is responsible for maintaining this equipment and for removing it at Completion of the whole of the works. Any water leaks shall be attended to immediately by the Contractor.

The Project Manager does not guarantee continuity of supply and the Contractor makes his own provision for standby supplies to maintain continuity of work. The Contractor is not entitled to a change in prices, key dates and/or completion date for any discontinuation or interruption of water supply.

5.1.15 Roads

Main access roads are surfaced and complete and may be used by the Contractor with the necessary care. The Employer maintains the site roads, to a fair condition. Any costs incurred by the Employer from damage caused to underground services and structures because of the Contractor not using the prescribed routes is recovered from the Contractor.

The Contractor provides temporary access points from the prescribed routes and roads to the points where the Contractor is required to perform work, having first obtained permission in writing from the Project Manager.

5.1.16 Setting-Out Beacons

The Employer provides permanent beacons marking the main setting out grid lines for the works, and permanent level benchmarks.

The Contractor takes reasonable steps to preserve beacons and benchmarks provided by the Employer who is not to be held responsible if any existing beacons are removed as long as other beacons exist.

5.1.17 Facilities provided by the Contractor. 
The Contractor shall provide all office and ablution facilities (structures or chemical toilets), including covered storage working areas, eating area, if applicable. The Contractor shall provide in the way of accommodation, EPPA services, storage, vehicles, and office equipment. The Contractor to provide water tanks and septic tanks if there is no main water or sewer connection in the allocated Contractor’s yard. All associated work and material will be for the Contractor’s account.

The Contractor includes in his establishment rates all further treatment of the yard areas that he considers necessary for his entire operation throughout his period of occupation and under all weather conditions. The Contractor also includes for all security fencing, security, and access arrangements. The yard is always kept clean and tidy, this includes all workshops and storage areas under the control of the Contractor. Maintenance of the yard is the Contractors responsibility. If the yard is not adequately maintained, the Employer instructs the Contractor to maintain the yard to the appropriate standards of which instruction does not constitute a compensation event.

Outfall drainage of all surface run-off drains is constructed by the Contractor to the acceptance of the Employer to minimise erosion and to effect control of contaminated water. The Contractor’s plan for the layout of his yard area is accepted by the Employer prior to occupying the yard and the Contractor does not occupy any site area other than that allocated to him. The Contractor’s plan states fully what measures are taken regarding removal and storage of topsoil, stabilisation of eroded areas and further loss of topsoil.

The Contractor complies with the environmental policy given in the site regulations. The Contractor provides, erects, and maintains for his own use adequate size office, accommodation and stores together with such drainage, lighting, heating, hot and cold-water services as may be required. Provision is also made for adequate parking and a turning area adjacent to all the aforesaid structures. The Employer prior to commencement of any work on site accepts all designs and layouts for these provisions.

The Contractor dismantles and clears the yard of all such temporary structures and associated foundations and infrastructure at the direction of the Employer on Completion of the whole of the works. No such dismantling and clearance work is carried out without prior acceptance from the Employer.
5.1.18 Existing premises, inspection of adjoining properties and checking work of Others

Where the Contractor requires to work in the same area as Others either at the same time or consequentially or there is interface with Others either at the same time or consequentially (“the Overlap”), the Contractor notifies the Employer and Others. The Contractor includes the Overlap in his programme and ensures Others also include it in their programmes. The Contractor’s programme will be rejected in accordance with clause 31.3 of the NEC if he fails to do so. 

The Contractor notifies the Employer and Others a minimum of two (2) calendar weeks before the Overlap starts. The Contractor inspects the Overlap area on the day he is to start work, liaises with Others and completes a report on the Overlap area and the works in the Overlap area. He submits to the Employer within forty-eight (48) hours of the date of starting work. The Contractor who requires access is responsible for compiling the report. His report includes the adequacy of the Overlap area, the works in the Overlap area; damage to the works, a record of Others working in the Overlap area and any other constraints in the area.  The Others working in the Overlap area also sign the report. The Contractor does the same when he completes the work in the Overlap area. The Contractor promptly notifies the Employer of any damage to his works or any other part of the Overlap area on both starting and completing his works and provides an explanation of how the damage occurred. The Contractor caters for the time for this activity in his revised programme for acceptance to ensure that there is no delay on his part.

The Contractor identifies all interfaces with Others in his Contractor’s Works Information and as required by paragraph 2.6 of this Works Information and does so for the execution of the works. The Contractor inspects the works of Others whom he has identified as an interface point and where alignment and compatibility between the works and Others’ works is required. Similarly, the Contractor also allows Others to inspect his works as required by them.
5.1.19 Survey control and setting out of the works. 
The Project Manager designates the working area boundary limits and assigns for the Contractor’s use, access roads, parking areas, storage areas, existing facilities areas, and construction areas. The Contractor does not trespass in or on areas not designated for his work. 

The Contractor is responsible for keeping Contractor’s personnel out of areas not designated for Contractor’s use, except, in the case of isolated work located within such areas for which the Contractor is authorised to do so.

5.1.20 Excavations and associated water control

In addition to the requirements of paragraph 2.6 of this Works Information, the Contractor notifies the Project Manager a minimum of four (4) calendar weeks prior to commencing excavation. The Contractor identifies all services in the areas affected by the excavation works and notifies the Employer and Others of his findings a minimum of three (3) weeks prior to commencing excavation.  

The Contractor conducts underground surveys before any excavation is performed as per the Employer’s SHE specification and Occupational Health and Safety regulations. All services need to be verified by the Contractor prior to excavation.

5.1.21 Underground services, other existing services, cable, and pipe trenches and covers. 
The Contractor’s method statement shall include how he will deal with known services and any unknown services which become known to the Contractor during the execution of the works. The Contractor accepts responsibility for the protection of all pipes, gauges, and the plant area. The Contractor immediately, and in any event no later than one (1) hour, notifies the Project Manager if he damages any services.  

The Contractor remedies any damage caused or procures the services of a third party to remedy such damage. The Contractor is liable for all damages, including damages suffered by Others and third parties, arising from or in connection with all services including the protection of all pipes, gauges, and the plant area.
5.1.22 Control of noise, dust, water, and waste 

The Contractor complies with the more stringent of all Laws, Employer’s standard and the Employers communicated documentation. This includes areas allocated for storage of materials, site offices and all other Working Areas. If a particular standard is not specified, the Contractor complies with the Employer’s requirements of which requirement are not a compensation event. The Contractor keeps the Working Areas clean and free from accumulation of waste materials and refuses regardless of the source.

The Contractor ensures that during sweeping and dusting, a minimum amount of dust is liberated into the atmosphere. Cleaning by vacuum cleaners is preferred and the use of compressed air for cleaning is prohibited.

The Contractor is responsible for the prompt removal of all waste to a designated disposal area. The designated disposal area will be on or in the vicinity of the Site and be indicated by the Project Manager.

“Waste” means any matter, whether liquid or solid or any combination thereof, which is a by-product, emission, residue or remainder of any process or activity carried out in connection with the works and which is not reused promptly and, in any event, no later than three (3) calendar days after production, in the carrying out the works. 

The Contractor provides enough marked bins and/or containers as and where required for the temporary storage of waste. The types of bins and/or containers comply with the latest revision of the procedure Management of Waste at Medupi. The Contractor segregates waste in accordance with the Employer’s requirements.

Bins and containers are emptied, and waste removed to the designated area at least once a week. The temporary and waste are removed to the designated area at least once a week. The temporary storage areas for bins and containers are maintained and not constitute a nuisance to Others. The Contractor ensures there is no spillage of waste alongside the bins and containers at any time. 

All waste that cannot be contained in either a bin or container is placed on a temporary waste site which the Project Manager identifies. The waste is removed as soon as possible but, in any event, at least once a week. No burning of waste is allowed at the Site.

Hazardous waste is dealt with in accordance with the Laws, Employer’s standards, Medupi Power Station requirements and the contract. The Contractor is solely responsible for the proper disposal of hazardous waste.

5.1.23 Sequences of construction or installation

The Contractor is responsible for the construction and installation of the equipment according to the Contractor’s construction and installation plans. Without derogating from the Contractor’s right for the sequencing of the works according to its design, the Contractor is to install, test and complete (where feasible) the sections in the order/ sequence provided under section 3 [Time] of the Data by Employer. However, due to power production priorities from Eskom, the Project manager may instruct the Contractor to change the sequences of the construction or installation so that the Contractor can proceed to work in other sections of the works, and this change does not constitute a Compensation Event. 
The Contractor complies with the Employer’s work co-ordination process.

Without derogating from the provisions of the conditions of contract, the work co-ordination process is used by the Project Manager to monitor and manage activities on the Site and to facilitate the integration and co-ordination of the various works by Others.

If not included in the contract, the Project Manager will notify the Contractor of the requirements of the work co-ordination process prior to the date of site establishment by the Contractor.

The Contractor is responsible for the construction and installation of the Plant and Materials according to the Contractor’s method statement. The Contractor ensures that method statements as a minimum are conducted for the following:

a) Designing a new job or task.

b) Changing jobs or task.

c) Introducing new equipment or substances.

d) Reviewing a procedure when problems have been identified, for example, from near miss incidents or an accident/incident investigation.

e) Simultaneous execution of the tanks as per the approved Contractor method statement.

The Contractor ensures that method statements and safe work procedures as a minimum contain the following:

a) The level of supervision required for the task. 
b) The training and qualifications required by the workers to perform the task. 
c) The Supervisor for the task or job and the employees who will undertake the task. 
d) The tasks that are to be undertaken that pose risks.

e) The equipment and substances that are used in these tasks.

f) The control measures that have been built into these tasks.

g) The personal protective equipment to be worn

h) Actions to be undertaken to address safety issues that may arise while undertaking the task.

All method statements shall be submitted to the Employer for review and acceptance before any work commences. Method statements and safe work procedures shall be submitted to the Employer a month before commencement of the works however during construction method statements and safe work procedures for any new activities are submitted to the Employer for review and acceptance three (3) days prior to the activity taking place, all method statements and safe working procedures shall be accompanied by a relevant risk assessment. 
Rejection of the method statement or safe work procedure due to non-conformance of the Contractor does not constitute a Compensation Event.

In addition to the requirements of paragraph 2.6 of this Works Information, the Contractor provides for access to Others and allows for interface, alignment, and compatibility between his sequence of construction or installation activities and Others’ sequence of construction or installation activities. Similarly, the Contractor accommodates Other’s requirements in relation to interface, alignment, and compatibility of their sequence of construction or installation activities.

5.1.24 Giving notice of work to be covered up

The Contractor notifies the Supervisor a minimum of five (5) working days prior to commencing work to be covered up. The Contractor notifies the Project Manager and Supervisor in writing of all planned activities for the week. 

5.1.25 Hook ups to existing works
Plant and Material may not be modified without express written permission from the Project Manager. 

The Contractors may not hook up for lifting, supporting or for any other reason to any position or existing works in the plant without a written position of the Project Manager. If the Contractor requires the use of existing infrastructure, it needs to be arranged with the Project Manager.
5.1.26 Communication and Correspondence

All correspondence shall be addressed to the Project Manager and all terms and conditions of the contract shall be adhered to with regards to communication and correspondence as required in the Contract.
5.2 Completion, testing, commissioning, and correction of Defects

5.2.1 Work to be done by the Completion Date of each section of the works. 
On or before the Completion Date of each section of the works the Contractor shall have done everything required to Provide the works except for the work listed below which may be done after the Completion Date of each section but in any case, before the dates stated. The Project Manager cannot certify Completion until all the work except that listed below has been done and is also free of Defects which would have, in his opinion, prevented the Employer from using the works and Others from doing their work. 
No alterations or adjustments will be made to the works after final checks are done without the Project Manager’s written permission.

At this stage the following shall have been achieved for each Section of the works. 
a) Installation and pre-commissioning completed.

b) Testing report and the associated certificates received.

c) Signed erection and safety clearance certificates.

d) Final Draft of the Technical, Operating and Maintenance manuals delivered. 
e) All Quality Control Plan (QCP) documentation received.

f) All Data Books submitted and accepted by the Employer. 
g) Any other items as stated in the Scope document 348-9971909.
The Project Manager cannot certify Completion until all the work including that listed above has been done and is also free of Defects which would have, in his opinion, prevented the Employer from using the works and Others from doing their work.

Sectional completion of the work will be when the entire system/ equipment of a Section is connected to the system and commissioned or operational.
On or before the Completion Date the Contractor shall have done everything required to Provide the Works except for the work listed below which may be done after the Completion Date but in any case, before the dates stated. The Project Manager cannot certify Completion until all the work except that listed below has been done and is also free of Defects which would have, in his opinion, prevented the Employer from using the works and Others from doing their work:
	Item of work
	To be completed by

	Performance testing of the works in use as specified in paragraph 5.2.8 of this Works Information.
	See performance testing requirements.

	All works (including Sections of the works) to be inspected and detailed report submitted to the Employer. (Works to be provided as stated in the Works Information)  
	As per the Accepted Programme 


5.2.2 Use of the works before Completion has been certified. 
As per clause 35.2 of the Contract, the Employer uses the works, without taking over the works, before Completion for reasons relating to the operation of the Medupi Power Station, commissioning, and/or capability testing of the works and associated plant area.

5.2.3 Materials facilities and samples for tests and inspections 

Refer core clause 40.2. where applicable, The Employer does not provide any materials, facilities and/or samples for tests and inspections. The Contractor provides all materials, facilities and/or samples required for tests and inspections.

The Contractor provides a schedule of all the required tests and connections as well as areas where these will be performed to the Project Manager for acceptance. 

a) Testing for all the electrical work 

b) Equipment to use for doing the testing may need to be inspected.

c) Providing facility for testing to assure Employer of the quality of the works.

d) Earthing test equipment etc.
5.2.4 Commissioning

The Contractor shall perform safety clearance and commission as per Employer’s commissioning procedure. 
Commissioning will not start until the following documents that are required for the commissioning of the plant is accepted by the Project Manager:

a) All relevant drawings (As-built). 
b) All type and routine test certificates

c) Commissioning procedure approved by the Employer. 
d) Data Book file with relevant documentation or records to be verified by Contractor in consultation with commissioning team in order to confirm system commissioning readiness. 
The Contractor provides the Employer with the following documents minimum of four (4) calendar weeks before the date of commissioning:

a) Erection completion certificate handed to the Project Manager,
b) The dates of the tests listed in paragraph a-k below.

The Employer elects as his sole discretion to attend the tests listed in paragraphs a-k below. The Contractor conducts, amongst others, the following tests and checks for the Employer to allow commissioning to occur:

a) Adjustment setting, operational checking and electrical injection testing of each relay, functional unit, circuit, and accessory prior to installation of cables.

b) Check for any visual damage to the circuit breakers, current transformers, bushings/insulators, instruments, switches, auxiliary relays, and all other equipment.

c) Check tightness (torque where applicable) on all connections.  

d) Power frequency voltage test where applicable.

e) Check the continuity of all current transformer and voltage transformer loops where applicable.

f) Check the fixing and locking devices on doors and covers.

g) Repetition of all functional tests (i.e., mechanical, electrical and automation functions) on some parts of the plant as done in the Contractor’s premises. 

h) Check the operation of all mechanical/manual devices for racking, earthing and spring rewind.

i) Verify the operation of the interlocking system’

j) Any other tests and checks required in terms of the Contractor’s interface, alignment and compatibility obligations and requirements.

k) Any other tests and checks specified in the Contractor’s Works Information.

The Employer conducts his own erection and commissioning checks to ensure conformance with the Contract. These checks do not release the Contractor of his obligation to ensure compliance with the Contract.

The Contractor’s failure to ensure compliance with all the pre-requisites for the Employer to allow commissioning to proceed will entitle the Employer to claim all damages arising from or in connection with this breach, including damages suffered by Others.   

The Contractor conducts the following tests as stipulated above for the Employer to certify that commissioning has occurred in accordance with the Contract requirements.

a) Any tests required in terms of the Contractor’s interface, alignment and compatibility obligations and requirements.

b) Any tests specified in the Contractor’s Works Information.

c) Any tests and required by best industry practice.  

The Contractor includes the following tests and checks for the Employer to certify SAT once the erection of the plant has been completed:

a) Any tests required in terms of the Contractor’s interface, alignment and compatibility obligations and requirements.

b) Any tests specified in the Contractor’s Works Information.
c) Any tests and required by best industry practice. 
Once the Contractor has satisfactorily completed all his tests, the Contractor provides drawings incorporating the changes arising from or in relation to commissioning within fourteen (14) calendar days. 

The Contractor provides all necessary resources during the erection, installation, testing and commissioning of the works. 

Records to be kept of each SAT in a logbook defining the tests to be undertaken, time and date of the commencement of the test, duration of the test, criteria that need to be met and results entered of the tests. These records are submitted to the Project Manager.

5.2.5 Start-up procedures required to put the works into operation. 
The Contractor gives the Project Manager written notice that the works are ready for energization. The Contractor commences with energisation no more than forty-eight (48) hours after commissioning and testing is completed. The Contractor provides the Employer with no less than five (5) working days of the date on which energisation occurs. 

No alterations or adjustments will be made to the works after final checks are done without the Project Manager’s written permission.

At this stage the following shall have been achieved:

a) Installation and pre-commissioning completed.

b) Testing report and the associated certificates received.

c) Signed erection and safety clearance certificates.

d) Final draft of the Technical, Operating and Maintenance manuals delivered.

e) All Quality Control Plan (QCP) documentation received.

5.2.6 Take over procedures. 
Take-over is after or at the same time as Completion. The Employer takes over the works on the date of safety clearance in accordance with the sectional completion dates of the Accepted Programme.

Once the Section of the works is complete as per part Section 1 and the Key Date Schedule, a Completion Certificate may be issued. (It is the Contractors responsibility to apply for the Completion Certificate). 

5.2.7 Access given by the Employer for correction of Defects. 
Refer to Clause 43.4 requires that the Project Manager arranges for the Employer to allow the Contractor access to and use of a part of the works which has been taken over if needed to correct a Defect. After the works have been put into operation, the Employer may require the Contractor to undertake certain procedures before such access can be granted.
5.2.8 Performance tests after Completion

Test to be conducted as specified in the document 348-9971909. 
5.2.9 Training and technology transfer

The Contractor provides training, for each unit on the equipment and systems included as part of the works to the various categories of the Employer's technical staff (operators, maintenance and engineering personnel) for the duration of the works.  Training will comprise both theoretical and practical training.

Training provided by the Contractor is directly applicable to the actual equipment supplied for the works. Generalised training based on similar equipment is not acceptable. The facilities for training provided by the Employer are at the Site.  It will be a suitably sized air-conditioned room, as well as trainee and trainer desks, a projector and flipchart or white board. The number of personnel to be trained to be determined and agreed with the Project Manager. 

The Contractor submits to the Project Manager for approval a detailed training programme as well as a prospectus for each course. The Contractor provides electronic and hard copies of the training material to the attendees and the Project Manager.  

The training schedule is incorporated in the Accepted Programme. The training schedule is separate. Project Manager to discuss and decide with the Contractor where it is required. 
Practical hands-on training for each individual employee forms an integral part of each of the following courses:

There are no restrictions on the Employer copying, developing and using the training material provided by the Contractor.
5.2.10 Operational maintenance after Completion

Refer to the Scope Document Number 348-9971909
6 Plant and Materials standards and workmanship
6.1 Investigation, survey, and Site clearance

Refer to the Scope Document Number 348-9971909.
6.2 Building works
Refer to the Scope Document Number 348-9971909. 
6.3 Civil engineering and structural works
Reference could be made to the SANS1200 series of specifications developed and published by South African National Standards. However, these are now very out of date and originally developed for use with SAICE (South African Institute of Civil Engineering) general conditions of Contract for works of civil engineering which have themselves been superseded twice.

All SANS 1200 specifications are in the process of being updated to make them more compatible with a wider range of contracts, including NEC, and the Contractor should check availability of the new SANS 2000 series of specifications.

Sections 3, 4 and 5 of SANS1200A are probably already covered in section 5 of this Works Information. 

This subsection would typically comprise:  
a) Particular specifications provided by the Employer. 
b) List of standardised specifications applicable to the works
c) Variations to the standardised specifications

If use is made of the 1200 series, users should include a covering note dealing with the changes in terminology, such as the one provided below. Further changes are required depending on which specifications in the 1200 series are selected.  

6.4 Electrical & mechanical engineering works
Refer to the Scope Document Number 348-9971909.
6.5 Process control and IT works
Refer to the Scope Document Number 348-9971909.
6.6 Other [as required]

Refer to Scope Document Number 348-9971909 and all documents issued to the Contractor. 
7 List of drawings

7.1 Drawings issued by the Employer. 
The Contractor is required to refer to the appendices for list of drawings issued by the Employer at or before the Contract Date and which apply to this contract.

The Contractor is further required to refer to Works Information (and to all referenced documents), Site Information and Scope of work document for all drawings and documents applicable in this Project. 
Part 4: Site Information
	Document reference
	Title
	No of pages

	
	This cover page
	1

	C4
	Site Information
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	Total number of pages
	


Part 4: Site Information

8 Site Information

Core clause 11.2(16) states:
“Site Information is information which:
· describes the Site and its surroundings and

· is in the documents which the Contract Data states it is in.”

In Contract Data, reference has been made to this Part 4 of the contract for the location of Site Information.

8.1 General description

The Medupi Power Station Project in Lephalale is a green-fields coal-fired power plant comprising of six units providing a total of 4 800MW on full capacity. The Power station is situated approximately 20Kms from the town of Lephalale (Ellisras). It is situated along the Steenbok pan Road. The works takes place in and around the boundaries of Medupi Power station.  

Medupi Power Station is located Y: 56334.69 X: 2622791.55 WGS84.

The Contractor makes his/her own assessment of and allows in his/her rates for those access problems that may be encountered. No extra payment or claim of any kind is allowed on account of difficulties of access to the works, or for the requirement of working adjacent to or in the same area as others.

Medupi Power Station is declared as National Key Point. Access to site shall be in line with the Medupi Power Station’s access procedure. The Contractor shall be required to make an application to enter site for the duration of the contract, including the warranty and defect period. A permit shall only be issued once the Contractor and his or her employees have attended the safety induction and has undergone medical checks. 

The Contractor shall have no claim against the Employer in respect of delay at the security main gate. 

Note that the speed limit on the site is 40 Km/h. The vehicle permits of any persons contravening any traffic act on site shall be cancelled. 

The Contractor complies with the Medupi Power Site Regulations, a copy of which is available for perusal at the Project Manager’s offices. 

Any subject within the authority of the Project Manager may be addressed by a Site Regulation. 

Before work starts on site, an inaugural meeting is held with the Contractor and the Project Manager to explain all requirements of the Site Regulations. 

The Medupi Power Station is currently under Commercial Operation and as such all buildings, rooms and various areas of Site have operating plants. The Contractor is therefore required to ensure compliance to all Plant Safety Regulations, including the Permit To Work systems. In accordance with ECC3 Clause 33.1: “Access to and use of the Site”, the Employer will allow access to and use of each part of the Site to the Contractor, however, the Contract will be required to adhere to the Permit To Work system to take permits (Work Permits from the plant Operator) before entering buildings, rooms and site areas with plant under operation.  
The Contractor employs staff trained or to be trained and authorised as Authorised Supervisors or Responsible Persons according to Employer’s Plant Safety Regulations. These Authorised Supervisors or Responsible Persons shall be available on site as and when required to take out Permits to Work.

At his own cost the Contractor provides his/her own accommodation and transport for all his/her employees engaged in the execution of the works. This includes the needs of his/her sub-Contractors. No accommodation is available at Medupi Power Station.

The Contractor always provides security necessary for the protection of the works until the completion of the whole of the works. 

No firearms, weapons, alcohol, illegal substances, and cameras are permitted on site. Any person suspected of being under the influence of alcohol is tested and if proved positive, is refused entry to the security area.

The Contractor implements a safety plan and maintains the safety system until the completion of the whole of the works. The plan, will as a minimum, contain PPE information, written safe working procedures, job specific risk assessments, safety meetings, etc. The plan will be to the Employer’s satisfaction and will be accepted prior to the commencement of any work. Contractor is to provide additional lighting where lighting is not sufficient in working areas.  

All equipment coming to site will be inspected by the Employer’s Safety Department.

The Contractor will be subject to periodic audits by the Employer to ensure compliance with the plan. Any deviations will be corrected to the Employer’s satisfaction. 

The Project Manager has the right to stop the Contractor's work activities which, in the opinion of Project Manager, is un-safe. The Contractor may only continue with work activities when all safety deficiencies have been corrected to the Project Manager’s satisfaction. The Contractor shall have no claim against the Employer in respect of delay due to the above.

8.2 Existing buildings, structures, and plant & machinery on the Site

The works shall be executed in and/or around the Medupi Power Station. All interfaces are as stated in the Specification document 348-9971909. 
Before Prices are submitted at tender stage, the Contractor is required to evaluate, assess, verify, and inspect each Section of the works to determine the conditions of the plant, over and above what is provided in the Works Information, Site Information and in the Scope Specification document 348-9971909. The Contractor shall have no claim (Compensation Event) against the Employer in respect of the above.  
Any equipment, or appliances, used by the Contractor is to conform to the applicable OHS Act safety standards and is maintained in a safe and proper working condition. The Project Manager has the right to stop the Contractor's use of any equipment which, in the opinion of Project Manager, does not conform to the foregoing. 

Loading and off-loading and material handling equipment is not available on site and if required, is to be provided by the Contractor.
8.3 Subsoil information
The Contractor will be required to conduct Geotech survey, and submit Geotechnical reports, to verify ground services, borehole and submit test results for parts of the Site where earthworks are required by this Contract.  
8.3.1 Hidden services 

There are no hidden services identified, however; the Contractor will be required to make reasonable assumptions at tender stage concerning such services.
8.4 Other reports and publicly available information

At publication of this tender there is no information on hydro-graphic data, hydrological information, shipping movements, tides, and published papers or Geological Surveys, which may affect the Contractor’s decision on method of working, programme, and preparation of any designs for which he is responsible, except as stated in this Contract document, Scope Specification document 348-9971909, and any other applicable document. 
� This total is required by the Employer for budgeting purposes only.  Actual amounts due will be assessed in terms of the conditions of contract.


� Available from Engineering Contract Strategies Tel 011 803 3008, Fax 011 803 3009 or see � HYPERLINK "http://www.ecs.co.za" �www.ecs.co.za� 







DOCUMENT C2.1
PAGE 2
PRICING DATA




EPPA ECC3 CONTRACT 
Page 2 of 2

