BID SPECIFICATION

ANNEXURE 1

BIDDERS MUST SUBMIT ANNEXURE 1 TOGETHER WITH THE MAIN BID DOCUMENT

| RFB No: | RFB 2602-2022 |
| --- | --- |
| Description | Appointment Of A Service Provider For Maintenance Support Of Ups System At The SITA Erasmuskloof Site For A Period Of Five (05) Years |
| Publication Date | 04 June 2022 |
| Virtual Briefing Session | Compulsory Briefing Session will be held as follows: Date: 13 July 2022 Time: 12:00pm Place: Online (MS Teams). Bidders are requested to indicate in writing on the below email address of their intension to attend the briefing session by 12 July 2022 @ 16:00pm, following which a link will be shared via email to allow attendance of the briefing session: Nokwanda.wasa@sita.co.za. |
| Closing Date for questions / queries | 18 July 2022 @16:00pm |
| Proposal Submission Address | Tender Office 459 Tsitsa Street, Erasmuskloof, Pretoria, 0105 |
| RFB Closing Details and Address | Date: 26 July 2022 Time: 11:00am (South African Time) Address: Tender Office 459 Tsitsa Street, Erasmuskloof, Pretoria, 0105 |
| RFB Validity Period | 120 Days from the Closing Date |

Contents

ANNEX A:	INTRODUCTION	4

1	PURPOSE AND BACKGROUND	4

1.1	PURPOSE	4

1.2	BACKGROUND	4

2	SCOPE OF BID	4

2.1	SCOPE OF WORK	4

2.2	DETAILS OF RELEVANT EQUIPMENT	5

2.3	DELIVERY ADDRESS	6

3	REQUIREMENTS	6

3.1	SERVICE REQUIREMENTS	6

4	BID EVALUATION STAGES	7

ANNEX A.1:	ADMINISTRATIVE PRE-QUALIFICATION	8

5	ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS	8

5.1	ADMINISTRATIVE PRE-QUALIFICATION VERIFICATION	8

5.2	ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS	8

6	TECHNICAL MANDATORY	9

6.1	INSTRUCTION AND EVALUATION CRITERIA	9

6.2	TECHNICAL MANDATORY REQUIREMENTS	10

6.3	DECLARATION OF COMPLIANCE	11

ANNEX A.2:	SPECIAL CONDITIONS OF CONTRACT (SCC)	12

7	SPECIAL CONDITIONS OF CONTRACT	12

7.1	INSTRUCTION	12

7.2	SPECIAL CONDITIONS OF CONTRACT	12

7.3	DECLARATION OF COMPLIANCE	28

ANNEX A.3:	COSTING AND PRICING	29

8	COSTING AND PRICING	29

8.1	COSTING AND PRICING EVALUATION	29

8.2	COSTING AND PRICING CONDITIONS	29

8.3	BID PRICING SCHEDULE	30

8.4	DECLARATION OF ACCEPTANCE	30

ANNEX A.4:	TERMS AND DEFINITIONS	31

9	ABBREVIATIONS	31

ANNEX B:	BIDDER SUBSTANTIATING EVIDENCE	32

10	MANDATORY REQUIREMENT EVIDENCE	32

10.1	SUPPLIER CERTIFICATION / AFFILIATION REQUIREMENTS	32

10.2	SUPPLIER EXPERIENCE AND CAPABILITY REQUIREMENTS	32

10.3	CIDB REGISTRATION REQUIREMENTS	33

10.4	TECHNICAL MANDATORY FUNCTIONAL REQUIREMENTS	33

ANNEX C:	SERVICE FUNCTIONAL REQUIREMENTS: Addendum 1	34

ANNEX D:	CIDB REGISTRATION REQUIREMENT	36

INTRODUCTION

# PURPOSE AND BACKGROUND

## PURPOSE

The purpose of this RFB is to invite Suppliers (hereinafter referred to as “bidders”) to submit bids for appointment of a service provider for maintenance support of UPS Systems at the SITA Erasmuskloof Site

## BACKGROUND

The electrical plant maintenance is essential for reliability of power supply for continued operation of critical computer environments. The higher reliability is achieved by having a good maintenance support and rapid response to the emergency interruption of services. The level expertise services and work required are not available within SITA and need to be outsourced. The scope of service is based on the schedule for planned maintenance and breakdowns to the UPS system equipment.

# SCOPE OF BID

## SCOPE OF WORK

The high-level scope of work for sites allocated to the contractor under this contract comprises, (but is not limited to):

  - On-site Disaster Recovery Support with a maximum 60-minute incident response time.

  - On-site Preventive maintenance.

(Scheduled Maintenance will be fixed rate based for Specified Services).

  - On-site Corrective/Remedial maintenance.

(The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on corrective maintenance labour unit rates and cost-plus percentage mark-up on material.)

  - On-site Call Outs.

(The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on unit rates for call-out fee per incident as specified on corrective maintenance labour unit rates.)

  - On-site Emergency Maintenance followed by a Root Cause Analysis.

(The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on unit rates for call-out as per 2.1(d) and on-site Corrective/Remedial maintenance as per 2.1(c).)

  - Support and critical repairs (with a maximum 60-minute incident response time) on UPS Systems of which the major components are (but not exclusive to):

    - Support and repairs on 160kVA UPS Units

    - Support and repairs on Battery Banks

  - Planned, periodic maintenance services on the following major components:

    - Support and repairs on 160kVA UPS Units

    - Support and repairs on Vented Lead Acid Battery Banks

  - Required service level: Availability 24/7/365 during the sixty (60) months contract period, with a maximum 60-minutes incident response time.

  - Upon SITA’s request, the bidder must provide inspection, and quality assurance services on other SITA electrical contractors’ work performed for SITA of systems that have impact to the equipment performance and services on this scope.

  - Upon SITA’s request, provide services relating to the isolation and commissioning l infrastructure specified in this scope.

  - The contractor shall perform plant room maintenance and plant inspections.

  - The services described under this scope will be required for a period of sixty months. The service will be “works order based” for known corrective maintenance requirements, and be “callout based” (followed by a works order) for power incidents where immediate response is required.

## DETAILS OF RELEVANT EQUIPMENT

Although the electrical plant for which support is required covers a wide span of electrical devices and systems, the major plant components under this contract are detailed below. Bidders should also note that SITA from time to time upgrades the electrical infrastructure for various sites, which means that the type of units and quantities of the units indicated below may change during the contract period.

  - UPS and Battery Systems:

  - UPS Unit 1 - Galaxy PW APC/Schneider Electric 160kVA UPS units. Parallel Operation.

  - UPS Unit 2 - Galaxy PW APC/Schneider Electric 160kVA UPS units. Parallel Operation.

  - UPS Unit 3 - Galaxy PW APC/Schneider Electric 160kVA UPS units. Parallel Operation

  - Battery Bank 1 - 192x YCP21 cells 268Ah Vented Lead Acid cells per Battery Bank

  - Battery Bank 2 - 192x YCP21 cells 268Ah Vented Lead Acid cells per Battery Bank

  - Battery Bank 3 - 192x YCP21 cells 268Ah Vented Lead Acid cells per Battery Bank

## DELIVERY ADDRESS

| No | Site Name | Physical Address |
| --- | --- | --- |
| 1 | Erasmuskloof Head Office | 459 Tsitsa Street, Pretoria |

REQUIREMENTS

## SERVICE REQUIREMENTS

  - On-site Disaster Recovery Support with a maximum 60-minutes incident response time.

  - On-site Preventive/Routine/Scheduled maintenance. Scheduled Maintenance will be fixed rate based for Specified Services requirement as detailed in the following documents.

  - On-site Corrective/Remedial maintenance.

(The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on corrective maintenance labour unit rates and cost-plus percentage mark-up on material.)

  - On-site Call Outs.

(The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on unit rates for call-out fee per incident as specified on corrective maintenance labour unit rates.)

  - On-site Emergency Maintenance followed by a Root Cause Analysis.

(The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on unit rates for call-out as per 2.1(d) and on-site Corrective/Remedial maintenance as per 2.1(c).)

  - Support and critical repairs (with a maximum 60-minutes incident response time) on UPS Systems of which the major components are (but not exclusive to):

    - Support and repairs on 160kVA UPS Units

    - Support and repairs on Vented Lead Acid Battery Banks

  - Planned, periodic maintenance services on the following major components:

    - Support and repairs on 160kVA UPS Units

    - Support and repairs on Vented Lead Acid Battery Banks

  - Required service level: Availability 24/7/365 during the sixty (60) months contract period, with a maximum 60-minutes incident response time.

  - Upon SITA’s request, the bidder must provide inspection, and quality assurance services on other SITA electrical contractors’ work performed for SITA of systems that have impact to the equipment performance and services on this scope.

  - Upon SITA’s request, provide services relating to the isolation and commissioning l infrastructure specified in this scope.

  - The contractor shall perform plant room maintenance and plant inspections (as defined) The relevant plant rooms and passage ways are:

    - UPS Room; and

    - Battery Room.

  - The services described under this scope will be required for a period of sixty (60) months. The service will be “works order based” for known corrective maintenance requirements, and be “callout based” (followed by a works order) for power incidents where immediate response is required.

# BID EVALUATION STAGES

- The bid evaluation process consists of several stages that are applicable according to the nature of the bid as defined in the table below.

- The bidder must qualify for each stage to be eligible to proceed to the next stage of the evaluation.

| Stage | Description | Applicable for this bid YES/NO |
| --- | --- | --- |
| Stage 1 | Administrative pre-qualification verification | YES |
| Stage 2A | Technical Mandatory requirement evaluation | YES |
| Stage 3 | Special Conditions of Contract verification | YES |
| Stage 4 | Price / B-BBEE evaluation | YES |

ADMINISTRATIVE PRE-QUALIFICATION

# ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS

## ADMINISTRATIVE PRE-QUALIFICATION VERIFICATION

- The bidder must comply with ALL of the bid pre-qualification requirements in order for the bid to be accepted for evaluation.

- If the Bidder failed to comply with any of the administrative pre-qualification requirements, or if SITA is unable to verify whether the pre-qualification requirements are met, then SITA reserves the right to-

  - Reject the bid and not evaluate it, or

  - Accept the bid for evaluation, on condition that the Bidder must submit within 7 (seven) days any supplementary information to achieve full compliance, provided that the supplementary information is administrative and not substantive in nature.

## ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS

- Submission of bid response: The bidder has submitted a bid response documentation pack

  - that was delivered at the correct physical or postal address and within the stipulated date and time as specified in the “Invitation to Bid” cover page, and;

  - in the correct format as one original document, one copy and two copies on memory stick / USB.

- Attendance of briefing session: A Compulsory Virtual Briefing session will be held. The bidder has to sign the briefing session attendance register using the same information (bidder company name, bidder representative person name and contact details) as submitted in the bidder’s response document.

- Registered Supplier. The bidder is, in terms of National Treasury Instruction Note 4A of 2016/17, registered as a Supplier on National Treasury Central Supplier Database (CSD).

# TECHNICAL MANDATORY

## INSTRUCTION AND EVALUATION CRITERIA

- The bidder must comply with ALL the requirements as per section 6.2 below by providing substantiating evidence in the form of documentation or information, failing which it will be regarded as “NOT COMPLY”.

- The bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response. During evaluation, SITA reserves the right to treat substantiation evidence that cannot be located in the bid response as “NOT COMPLY”.

- The bidder must complete the declaration of compliance as per section 6.3 below by marking with an “X” either “COMPLY”, or “NOT COMPLY” with ALL of the technical mandatory requirements, failing which it will be regarded as “NOT COMPLY”.

- The bidder must comply with ALL the TECHNICAL MANDATORY REQUIREMENTS in order for the bid to proceed to the next stage of the evaluation.

- No URL references or links will be accepted as evidence.

## TECHNICAL MANDATORY REQUIREMENTS

| TECHNICAL MANDATORY REQUIREMENTS | Substantiating evidence of compliance (used to evaluate bid) | Evidence reference (to be completed by bidder) |
| --- | --- | --- |
| - BIDDER CERTIFICATION / AFFILIATION REQUIREMENTS The Bidder must be registered at the Department of Labour as an Electrical Contractor. | Attach to ANNEX B a copy of documentation (valid certificate, license, or letter) from the Department of Labour as evidence that the bidder is registered as an electrical contractor. | provide unique reference to locate substantiating evidence in the bid response – see Annex B, section 10.1> |
| - BIDDER EXPERIENCE AND CAPABILITY - The bidder must have executed maintenance and support of a UPS System with minimum unit capacity of 160 kVA at Data Centre or Equivalent High Availability Environment to in the last Five (5) years. | Provide references for one (1) customer to whom maintenance and support services was executed on for UPS System with minimum unit capacity of 160 kVA for Data Centre or equivalent High Availability Environment (Hospital, Airport, Bank, or similar High Availability Environments) in the last five (5) years. | provide unique reference to locate substantiating evidence in the bid response – see Annex B, section 10.2, table 1> |
| - BIDDER EXPERIENCE AND CAPABILITY - The bidder must have executed maintenance of a Vented Lead Acid Battery Banks at Data Centre or Equivalent High Availability Environment to in the last 5 years. | Provide references for one (1) customer to whom maintenance services was executed on for Vented Lead Acid Battery Banks for Data Centre or equivalent High Availability Environment (Hospital, Airport, Bank, or similar High Availability Environments) in the last five (5) years. | provide unique reference to locate substantiating evidence in the bid response – see Annex B, section 10.2, table 1> |
| - CIDB REGISTRATION REQUIREMENT The bidder must be registered and active with Construction Industry Development Board (CIDB) with a minimum rating of 4EB PE or 4EP PE or 5EP or 5EP. | The Bidder needs to complete and sign ANNEX D to confirm that the Bidder is registered with the Construction Industry Development Board (CIDB) with a minimum rating of 4EB PE or 4EP PE or 5EB or 5EP. | provide unique reference to locate substantiating evidence in the bid response – see Annex B, section 10.3 and Annex D, |
| - SERVICE FUNCTIONAL REQUIREMENTS The bidder must confirm compliance to the technical mandatory functional requirements. | The bidder must confirm that they comply with the Service Functional Requirements by completing ANNEX C: Addendum 1. | <provide unique reference to locate substantiating evidence in the bid response – see Annex B section 10.4 and Annex C: Addendum 1> |

## DECLARATION OF COMPLIANCE

|  | Comply | Not Comply |
| --- | --- | --- |
| The bidder declares by indicating with an “X” in either the “COMPLY” or “NOT COMPLY” column that – - The bid complies with each and every TECHNICAL MANDATORY REQUIREMENT as specified in SECTION 6.2 above; AND - Each and every requirement specification is substantiated by evidence as proof of compliance. |  |  |

SPECIAL CONDITIONS OF CONTRACT (SCC)

# SPECIAL CONDITIONS OF CONTRACT

## INSTRUCTION

- The successful supplier will be bound by Government Procurement: General Conditions of Contract (GCC) as well as this Special Conditions of Contract (SCC), which will form part of the signed contract with the successful Supplier. However, SITA reserves the right to include or waive the condition in the signed contract.

- SITA reserves the right to –

  - Negotiate the conditions, or

  - Automatically disqualify a bidder for not accepting these conditions.

  - Award to multiple bidders.

- In the event that the bidder qualifies the proposal with own conditions, and does not specifically withdraw such own conditions when called upon to do so, SITA will invoke the rights reserved in accordance with subsection 7.1(2) above.

- The bidder must complete the declaration of acceptance as per section 7.3 below by marking with an “X” either “ACCEPT ALL” or “DO NOT ACCEPT ALL”, failing which the declaration will be regarded as “DO NOT ACCEPT ALL” and the bid will be disqualified.

## SPECIAL CONDITIONS OF CONTRACT

- CONTRACTING CONDITIONS

  - Formal Contract. The Supplier must enter into a formal written Contract (Agreement) with SITA.

  - Right of Award. SITA reserves the right to award the contract for required goods or services to multiple Suppliers.

  - Right to Audit. SITA reserves the right, before entering into a contract, to conduct or commission an external service provider to conduct a financial audit or probity to ascertain whether a qualifying bidder has the financial wherewithal or technical capability to provide the goods and services as required by this tender.

- DELIVERY ADDRESS

The supplier must deliver the required products or services at as indicated in Section 2.3, Delivery Address

- DELIVERY SCHEDULE

  - The scope of work (Section 2.1) and Section 3 (Requirements) will be over the period of 60 months.

  - The Supplier is responsible to perform the work as outlined in the following Breakdown Structure (WBS):

| WBS | Statement of Work | Delivery Timeframe |
| --- | --- | --- |
|  | On-site Disaster Recovery Support with a maximum 60-minutes incident response time. | Over the duration of 60 months |
|  | On-site Preventive/Routine/Scheduled maintenance. |  |
|  | On-site Corrective/Remedial maintenance. |  |
|  | On-site Call Outs. |  |
|  | On-site Emergency Maintenance followed by a Root Cause Analysis. |  |
|  | Support and critical repairs (with a maximum 60-minutes incident response time) on UPS Systems of which the major components. |  |
|  | Planned, periodic maintenance services on the following major components: |  |
|  | Required service level: Availability 24/7/365 during the sixty (60) months contract period, with a maximum 60-minutes incident response time. |  |
|  | Upon SITA’s request, the bidder must provide inspection, and quality assurance services on other SITA electrical contractors’ work performed for SITA of systems that have impact to the equipment performance and services on this scope. |  |
|  | Upon SITA’s request, provide services relating to the isolation and commissioning l infrastructure specified in this scope. |  |
|  | The contractor shall perform plant room maintenance and plant inspections (as defined) The relevant plant rooms and passage ways are: - UPS Room; and - Battery Room. |  |
|  | The services described under this scope will be required for a period of sixty(60) months. The service will be “works order based” for known corrective maintenance requirements, and be “callout based” (followed by a works order) for power incidents where immediate response is required. |  |

- SERVICES AND PERFORMANCE METRICS

  - During Maintenance support period the Supplier is responsible to provide the following services as specified in the Service Breakdown Structure (SBS):

| SBS | Service Element | Service Level |
| --- | --- | --- |
|  | Emergency Contact during warranty and maintenance periods | 24h x 7days x 52weeks |
|  | Incident Response during warranty and maintenance periods | Maximum 60-minutes |

- MAINTENANCE REQUIREMENTS

During Maintenance Support periods the Supplier is responsible to provide the following services on the UPS units and batteries as specified.

  - UPS Batteries Maintenance Requirements.

- The scope of maintenance will cover:

- Meeting with the original equipment manufacturer of the battery units at the respective sites will be required.

- In consultation with the original equipment manufacturer of the battery units at the respective sites, Draw up a step by step maintenance procedure for the respective battery units and submit to SITA for approval.

- Once SITA has approved the step by step battery maintenance procedure, the battery services to be strictly executed as per this procedure.

- The following minimum requirements must be incorporated into the battery maintenance procedure, and must be executed:

      - All battery terminals must be checked and torqued to the correct tension.

      - All battery units and stands must be properly cleaned. Should any one battery unit have excessive deposits on it, it must be recorded as such as a comment in the battery service book.

      - The battery acid level must be topped up to the correct level.

      - The Specific Gravity level of each battery unit must be checked and recorded in the battery service book.

      - Each battery unit’s valves must be properly cleaned.

      - Inspect each Battery unit’s acid water level and record anomalies. Top up Cells with demineralised water to the maximum levels. This includes provision for 1000 litres of distilled battery for initial top-up.

      - Inspect each Battery unit for excessive sediment formation and record anomalies.

      - Ensure all distribution boards (doors and panels) in the Battery Room are fully closed, and record.

      - Apply petroleum jelly on battery terminals.

      - Inspect Clean and Re-torque battery terminals.

      - Measuring of voltage before and after distilled water top. The measurements should be for each battery. Usually each bank has 192 battery units. The second measurement should be at least two weeks after the initial top-up.

      - Checking of battery water SG levels after top-up. This should be done at least two weeks after initial top-up.

      - Top up Cells with demineralised water

      - Clean and Re-torque

      - Perform Battery Charging and Discharge Test

  - UPS Units Maintenance Requirements.

- The scope of maintenance will cover:

- Where the input power to an UPS unit on site will be interrupted for more than 10 minutes, An OEM certified UPS technician must be in attendance on site to shut down and re-commission the UPS units.

- Where personnel will work on the input power to any UPS units, and the UPS units does not require an intentional shut down, An OEM certified UPS technician must be on site to immediately re-commission the UPS units in the event of an unintentional UPS shutdown.

- The following functions to be performed as part of the service on the UPS units:

      - The UPS units per site will not be serviced at the same time. All the UPS units per site may be serviced at the same date though.

      - The site to be transferred to generator power for the duration of the UPS service.

      - Visual inspection of the entire UPS solution on site. Search for any exceptional environmental or other conditions that could damage or affect the performance of the UPS.

      - Run full diagnosis test on the UPS system and record findings.

      - Complete a functional checkout and test of the UPS diagnostic systems.

      - Perform system and component functional tests on all UPS equipment to insure proper functioning within specified parameters.

      - Certify the condition of all the UPS capacitors.

      - Inspect all cabling and cable terminations internal to the UPS.

      - Inspect all cabling and cable terminations of the power supply to the UPS.

      - Inspect all cabling and cable terminations of the load connected to the UPS.

      - Clean and tighten all power connections at the input and output terminals, at all circuit breakers, and at the terminal posts and fuses on the rectifier and inverter legs. Check all power cabling for abrasions and burn spots. Visually check components for signs of overheating, swelling, leaking, etc. Visually check printed circuit board alignments.

      - Check condition of controller batteries.

      - Check the condition of all fans and Filters.

      - Ensure that the latest firmware relevant to the UPS unit is loaded on the system.

      - Confirm correct /optimal parallel operation (for parallel operated units).

      - Ensure all voltages and current readings on the rectifier, battery, inverter and output are correct, and record.

      - Measure the Voltage to and from the UPS and indicate imbalances.

      - Check indicator lamps, meters and controls and ensure correct operation.

      - Check the operation of the static bypass by transferring to and from the static bypass.

      - Clear any dust built up on the UPS, internal and external. Ensure that all system components are clean.

      - Confirm the full and correct functioning of the UPS alarm card.

      - Check and record the ambient temperature of the UPS equipment.

      - Cleaning of air filters.

      - Replace of all air filters every 12 months.

- Record the battery charging voltage and ensure correct rating for the relevant type of battery connected to the UPS.

- Indicate the setting of the battery charging circuit and the immediate current that will flow once the UPS input power supply is restored. The intention of this test is to ensure that the upstream circuit breakers are set to the correct values to prevent tripping of these circuit breakers once the UPS comes online.

- Record the current load on the UPS and indicate the UPS configuration load capability.

- Where the provided standard UPS service sheet does not provide for the recording of all the requirements specified above, the remainder of the details shall be recorded on the relevant company’s letterhead.

  - Plant Room Maintenance Requirements

- The contractor shall perform plant room maintenance at the frequencies as indicated under the detail scope of work per site.

- The plant room maintenance must be conducted in such a way to ensure that the plant inside the room is not taken out of service or its operation jeopardised.

- The plant room maintenance may be conducted during normal hours.

- The contractor shall ensure that all lights are fully functional in the room. Blown lamps must be replaced by the contractor and is deemed inclusive of the quoted rate. Should the light fittings require replacement, the contractor shall send the necessary quotation to SITA for approval. Provision for at least 25x 1500mm LED Tubes.

- The contractor shall meticulously clean the entire room (including walls, doors and floor).

- The contractor shall ensure the safety of his staff inside these plant rooms while performing the plant room maintenance. Non-skilled staff will not be allowed by SITA inside these areas. SITA will allow semi-skilled electrical staff inside these areas to perform the plant room maintenance.

- Passage ways leading to the respective plant rooms is deemed part of the plant room and all requirements specified for the plant room, applies to these passage ways as well.

  - UPS System Inspection Requirements

- The contractor shall perform plant inspections on minimum quarterly basis;

- The plant inspections must be conducted in such a way so that the respective unit is not taken out of service or its operation jeopardised.

- The plant inspections may be conducted during normal hours.

- The inspection report shall be part of the monthly report;

- The contractor shall notify SITA immediately should any damage, malfunction or alarm be observed on the Plant (being inspected).

- The contractor shall sign the plant room maintenance book during each plant inspection.

- The plant inspections must consist of the following

  - UPS Units:

    - Inspect each UPS unit for any visible damage, malfunction, or alarms. Record findings.

    - Inspect whether all electrical earths are present on the UPS units, and record.

    - Confirm airtime balance on alarm unit, and record.

    - Ensure all distribution boards (doors and panels) in the UPS Room are fully closed, and record.

    - Confirm all lights are functional inside the UPS room and record.

    - The UPS Units shall be cleaned of any dust.

  - Battery Units:

    - Ensure all distribution boards (doors and panels) in the Battery Room are fully closed, and record.

    - Confirm all lights are functional inside the Battery room and record.

    - Inspect condition anomality’s of the battery in terms of spillage, corrosion on the terminals and battery water level this to include any leaks of battery water.

    - The battery cells and stands shall be cleaned of any dust/dirt.

  - Service Pack Requirements.

- The cost of the Plant Inspection reports is deemed included in the service / inspection costs quoted.

- Two service packs per equipment, per site to be provided. The service pack must conform to the following:

    - The service pack hard copy information must be contained within a file, of which each page must be in a plastic pocket, to ensure longevity of the documentation.

    - Upon SITA approval of the service pack contents, the one file must be inserted into the service folders on site, and the other file must be delivered to the SITA Centurion office for archiving.

    - The files must be clearly marked with a printed front page indicating the Erasmuskloof Site name

    - An electronic copy must be made of the entire service pack for the relevant to the equipment serviced, and be stored on an USB storage device. One USB storage device may be provided containing the information for all the serviced sites.

    - Should additional items been specified in this technical service requirements that does not appear on the given standard service sheet, it must be noted on a separate dated letterhead with associated test results.

- SERVICE LEVEL REQUIREMENTS, WARRANTIES, AND PENALTIES

All Service Level time lines indicated below are relevant any time of day, any time of year, during the contract period.

The following SLA time windows are applicable to this contract:

  - The Change Control windows will be planned by both parties (SITA and the contractor) and practical timeslots (which must not exceed the specified maximum number of timeslots or the specified maximum duration of each timeslot) and dates be agreed to. The scope of work to be executed and completed for each of the Change Control windows will be agreed to by both SITA and the contractor. A penalty to the value of R10000 (Excl VAT) will be applied per incident to the contractor should the contractor not implement the scoped work during the planned and approved Change window dates and timeslots, or should the contractor not be able to fully commission the electrical installation at the end of the planned and approved Change window dates and timeslots, or should the contractor not attend an arranged and notified (24 hours in advance) Change window.

  - SITA will notify the contractor telephonically that a problem is experienced at (in scope) site, and that he needs to attend to site immediately. The contractor shall provide the number of his emergency contact details, or representative that needs to be contacted for this purpose. The contractor shall have a qualified technician on site within 60minutes from the first telephonic call/call attempt (unless SITA agrees to an alternative response time with the contractor during the call). Plant / Infrastructure repairs shall start within 60minutes from the first telephonic call/call attempt (unless SITA agrees to an alternative response time with the contractor during the call or on-site inspection). The 60minute requirement will be heavily dependent on the severity of the incident. If the incident is less severe, SITA will settle for slightly longer response times. SITA will be the judge of the incident severity. Should the Support Contractor’s response time to site exceed the specified 60minutes (or alternative duration as agreed to by SITA) a penalty equivalent to R5000 (Excl VAT) will be applied, per incident.

  - Penalties shall be applied at SITA’s discretion, following the breach of a Service Level Agreement. The contractor shall have the opportunity to provide a report, within seven calendar days following the incident or SITA’s notice of penalty, indicating why the contractor deem the penalty not to be applied. SITA shall take this into consideration, but SITA’s decision shall be final and shall deduct penalty values from the monthly invoices for the relevant site(s).

- SUPPLIER PERFORMANCE REPORTING

  - The Supplier will report on a Bi-annual y basis to SITA/Client during the duration of the maintenance contract.

  - The Supplier is required to generate regular reports as outputs during the maintenance and support cycle within the following service levels (the report type will drive the service level agreement; definition of the content of each report type will be finalised at the time of concluding the contracted service level agreement).

- CERTIFICATION, EXPERTISE AND QUALIFICATION

- The Bidder must be registered at the Department of Labour as an Electrical Contractor.

- The bidder must have executed maintenance of a UPS System with minimum unit capacity of 160 kVA at Data Centre or Equivalent High Availability Environment to in the last 5 years.

- The bidder must have executed maintenance of a Vented Lead Acid Battery Banks at Data Centre or Equivalent High Availability Environment to in the last 5 years.

- The bidder must be registered with Construction Industry Development Board (CIDB) with a minimum rating of 4EB PE or 4EP PE or 5EP or 5EP

- The Supplier represents that,

  - it has the necessary expertise, skill, qualifications and ability to undertake the work required in terms of the Statement of Work or Service Definition with the technical personnel qualified and OEM trained.

  - it is committed to provide the Services; and

  - perform all obligations detailed herein without any unplanned interruption to the Customer.

- The Supplier must provide the service in a good and workmanlike manner and in accordance with the practices and high professional standards used in well-managed operations performing services similar to the Services;

- The Supplier must perform the Services in the most cost-effective manner consistent with the level of quality and performance as defined in Statement of Work or Service Definition;

- Original Equipment Manufacturer (OEM) or Original Software Manufacturer (OSM) work:

  - The Supplier must ensure that preventative work or service on the UPS system is performed according to OEM requirements. The bidder shall indicate the potential risks of following this servicing methodology.

  - The Supplier must be able to access to the UPS control system for service diagnostics and possible repairs. The Supplier must have the latest software as approved by OSM APC/Schneider Electric

- Electrical Work. The Supplier must ensure that Electrical Work is performed as prescribed by the Occupation Health and Safety Act (Act 85 of 1993 as amended), Electrical Regulations 2009, including,

  - The standard of work conforms to SABS SANS 10142-1: The code of practice for wiring of premises; and

  - Any Electrical installation or alteration is certified after completion of work by means of a Certificate of Compliance.

- LOGISTICAL CONDITIONS

- Hours of work, 08h00 – 16h30.

- Provision to be made for work which will be Saturday and Sunday.

- It must be noted that Erasmuskloof site is a live site, and downtimes are limited. All site services will have to be restored at the end of the scheduled downtime. The Supplier to make sure all the resources, tools and equipment are available to work continuously during that period to complete all the scheduled tasks during that period.

- All the work that require downtime of services or have potential to cause unplanned downtime will have to be approved before commencing. The approval will have to follow SITA change management process.

- The scheduled work that does not require downtime, those can be completed during hours in 7(a) and 7(b).

- In the event that SITA grants the Supplier permission to access SITA's Environment including hardware, software, internet facilities, data, telecommunication facilities and/or network facilities remotely, the Supplier must adhere to SITA's relevant policies and procedures (which policy and procedures are available to the Supplier on request) or in the absence of such policy and procedures, in terms of, best industry practice.

- Tools of Trade. The Supplier must bring their necessary tools of trade in order for them to perform their duties adequately. This includes relevant software and passwords to access the UPS system diagnostic tools.

- On-site and Remote Support. The Supplier must give off-site and remote support, and only when off-site support is not sufficient, then on-site support will be required upon approval by SITA representative.

- Support and Help Desk. After hours helpdesk support is required for the period of the maintenance support.

- Emergency Maintenance & Call Outs: The activity involved with restoring, repairing or replacing on a non-scheduled maintenance basis. This maintenance activity would be a result of a service affecting or possible service affecting defect resulting in the loss of operation or potential loss of operation of any part or component of the electrical installation at the listed sites.

- Emergency Maintenance action shall be required at any time day or night including weekends and holidays. The Emergency maintenance response times shall meet or exceed the Service Level Agreements timelines set within this document.

- During Emergency Maintenance action the Support contractor’s objective shall always be to prevent a site failure or service failure by any means possible.

- Where the input power to an UPS unit on site will be interrupted for more than 10 minutes, the contractor must have technician in attendance on site to shut down and recommission the UPS units.

- Where the contractor will work on the input power to any UPS units, and the UPS units does not require an intentional shut down, the contractor must still have an technician on site to immediately recommission the UPS units in the event of an unintentional UPS shutdown.

- SITA has no As Built records available of the existing electrical installations or major electrical plant components.

- SKILLS TRANSFER AND TRAINING

  - The Supplier must provide training on the proposed solution or product to technical staff and operator to enable SITA to operate and support the product or solution after implementation.

- REGULATORY, QUALITY AND STANDARDS

  - The Supplier must for the duration of the contract ensure compliance with ISO/IEC General Quality Standards, ISO27001, and Protection of Personal Information Act (POPIA).

  - The Supplier must for the duration of the contract ensure compliance with General Quality Standards, ISO 9001

- PERSONNEL SECURITY CLEARANCE

- The Supplier personnel who are required to work with GOVERNMENT CLASSIFIED information or access government RESTRICTED areas must be a South African Citizen and at the expense of the Supplier be security vetted (pre-employment screening, criminal record screening and credit screening).

- The Supplier must ensure that the security clearances of all personnel involved in the Contract remains valid for the period of the contract.

- The Supplier must provide proof of security vetting

- CONFIDENTIALITY AND NON-DISCLOSURE CONDITIONS

- The Supplier, including its management and staff, must before commencement of the Contract, sign a non-disclosure agreement regarding Confidential Information.

- Confidential Information means any information or data, irrespective of the form or medium in which it may be stored, which is not in the public domain and which becomes available or accessible to a Party as a consequence of this Contract, including information or data which is prohibited from disclosure by virtue of:

    - the Promotion of Access to Information Act, 2000 (Act no. 2 of 2000);

    - being clearly marked "Confidential" and which is provided by one Party to another Party in terms of this Contract;

    - being information or data, which one Party provides to another Party or to which a Party has access because of Services provided in terms of this Contract and in which a Party would have a reasonable expectation of confidentiality;

    - being information provided by one Party to another Party in the course of contractual or other negotiations, which could reasonably be expected to prejudice the right of the non-disclosing Party;

    - being information, the disclosure of which could reasonably be expected to endanger a life or physical security of a person;

    - being technical, scientific, commercial, financial and market-related information, know-how and trade secrets of a Party;

    - being financial, commercial, scientific or technical information, other than trade secrets, of a Party, the disclosure of which would be likely to cause harm to the commercial or financial interests of a non-disclosing Party; and

    - being information supplied by a Party in confidence, the disclosure of which could reasonably be expected either to put the Party at a disadvantage in contractual or other negotiations or to prejudice the Party in commercial competition; or

    - information the disclosure of which would be likely to prejudice or impair the safety and security of a building, structure or system, including, but not limited to, a computer or communication system; a means of transport; or any other property; or a person; methods, systems, plans or procedures for the protection of an individual in accordance with a witness protection scheme; the safety of the public or any part of the public; or the security of property; information the disclosure of which could reasonably be expected to cause prejudice to the defence of the Republic; security of the Republic; or international relations of the Republic; or plans, designs, drawings, functional and technical requirements and specifications of a Party, but must not include information which has been made automatically available, in terms of the Promotion of Access to Information Act, 2000; and information which a Party has a statutory or common law duty to disclose or in respect of which there is no reasonable expectation of privacy or confidentiality;

- Notwithstanding the provisions of this Contract, no Party is entitled to disclose Confidential Information, except where required to do so in terms of a law, without the prior written consent of any other Party having an interest in the disclosure;

- Where a Party discloses Confidential Information which materially damages or could materially damage another Party, the disclosing Party must submit all facts related to the disclosure in writing to the other Party, who must submit information related to such actual or potential material damage to be resolved as a dispute;

- Parties may not, except to the extent that a Party is legally required to make a public statement, make any public statement or issue a press release which could affect another Party, without first submitting a written copy of the proposed public statement or press release to the other Party and obtaining the other Party's prior written approval for such public statement or press release, which consent must not unreasonably be withheld.

- GUARANTEE AND WARRANTIES

The Supplier warrants that:

- The warranty of goods supplied under this contract remains valid for twelve (12) months after the goods, or any portion thereof as the case may be, have been delivered to and accepted at the final destination indicated in the contract, or for eighteen (18) months after the date of shipment from the port or place of loading in the source country, whichever period concludes earlier;

- as at Commencement Date, it has the rights, title and interest in and to the Product or Services to deliver such Product or Services in terms of the Contract and that such rights are free from any encumbrances whatsoever;

- the Product is in good working order, free from Defects in material and workmanship, and substantially conforms to the Specifications, for the duration of the Warranty period;

- during the Warranty period any defective item or part component of the Product be repaired or replaced within 3 (three) days after receiving a written notice from SITA;

- the Products is maintained during its Warranty Period at no expense to SITA;

- the Product possesses all material functions and features required for SITA’s Operational Requirements;

- the Product remains connected or Service is continued during the term of the Contract;

- all third-party warranties that the Supplier receives in connection with the Products including the corresponding software and the benefits of all such warranties are ceded to SITA without reducing or limiting the Supplier’s obligations under the Contract;

- no actions, suits, or proceedings, pending or threatened against it or any of its third-party suppliers or sub-contractors that have a material adverse effect on the Supplier’s ability to fulfil its obligations under the Contract exist;

- SITA is notified immediately if it becomes aware of any action, suit, or proceeding, pending or threatened to have a material adverse effect on the Supplier’s ability to fulfil the obligations under the Contract;

- any Product sold to SITA after the Commencement Date of the Contract remains free from any lien, pledge, encumbrance or security interest;

- SITA’s use of the Product and Manuals supplied in connection with the Contract does not infringe any Intellectual Property Rights of any third party;

- the information disclosed to SITA does not contain any trade secrets of any third party, unless disclosure is permitted by such third party;

- it is financially capable of fulfilling all requirements of the Contract and that the Supplier is a validly organized entity that has the authority to enter into the Contract;

- it is not prohibited by any loan, contract, financing arrangement, trade covenant, or similar restriction from entering into the Contract;

- the prices, charges and fees to SITA as contained in the Contract are at least as favourable as those offered by the Supplier to any of its other customers that are of the same or similar standing and situation as SITA; and

- any misrepresentation by the Supplier amounts to a breach of Contract.

- INTELLECTUAL PROPERTY RIGHTS

- SITA retains all Intellectual Property Rights in and to SITA's Intellectual Property. As of the Effective Date, the Supplier is granted a non-exclusive license, for the continued duration of this Contract, to perform any lawful act including the right to use, copy, maintain, modify, enhance and create derivative works of SITA's Intellectual Property for the sole purpose of providing the Products or Services to SITA pursuant to this Contract; provided that the Supplier must not be permitted to use SITA's Intellectual Property for the benefit of any entities other than SITA without the written consent of SITA, which consent may be withheld in SITA's sole and absolute discretion. Except as otherwise requested or approved by SITA, which approval is in SITA's sole and absolute discretion, the Supplier must cease all use of SITA's Intellectual Property, at of the earliest of:

    - termination or expiration date of this Contract;

    - the date of completion of the Services; and

    - the date of rendering of the last of the Deliverables.

- If so required by SITA, the Supplier must certify in writing to SITA that it has either returned all SITA Intellectual Property to SITA or destroyed or deleted all other SITA Intellectual Property in its possession or under its control.

- SITA, at all times, owns all Intellectual Property Rights in and to all Bespoke Intellectual Property.

- Save for the license granted in terms of this Contract, the Supplier retains all Intellectual Property Rights in and to the Supplier’s pre-existing Intellectual Property that is used or supplied in connection with the Products or Services.

- FIRE SUPPRESSION AND FIRE DETECTION SYSTEMS

- The contractor must take care during his operations not to activate and discharge the automatic fire suppression system. SITA will place the automatic fire suppression system into Manual mode during the contractor’s work on site, should he request SITA to do so. Should the contractor or his sub-contractor(s) manage to activate and discharge the automatic fire suppression system, the refill of the suppression gas / agent shall be for the contractor’s account.

- The contractor must take care during his operations not to activate the fire detection system and cause an alarm on the fire panel. Should the contractor or his sub-contractor(s) manage to activate the fire detection system and in the process cause an alarm on the fire panel, the callout cost for the fire detection contractor to reset the panel and the air conditioning contractor to restart the air conditioning units shall be for the contractor’s account.

- OCCUPATIONAL HEALTH AND SAFETY

  - The contractor must provide within one month of contract commencement all his technical staff used on the SITA contract’s Occupational Health and Safety Training Certificates.

  - The contractor must provide within one week of contract commencement the details of his occupational health and safety representative for this contract.

  - The contractor must submit a Health and Safety plan to SITA covering the full scope of work under this document for approval within three weeks after signature of the contract. Any changes and or improvements as requested by SITA must be resubmitted within two weeks.

  - The safety of SITA personnel and visitors to SITA premises must be placed first, at all times and great care must be taken not to damage any infrastructure or equipment.

  - Provide SITA with the compliant safety file.

- GENERAL

  - The supplier will be bound by Government Procurement: General Conditions of Contract.

  - (GCC) as well as this Special Conditions of Contract (SCC), which will form part of the signed contract with the Supplier. However, SITA reserves the right to include or waive the condition in the signed contract.

  - SITA reserves the right to:

    - Negotiate the conditions, or

    - Automatically disqualify a bidder for not accepting these conditions.

    - Right to Audit: SITA reserves the right, before entering into a contract, to conduct or commission an external service provider to conduct probity to ascertain whether a qualifying bidder has the technical capability to provide the goods and services as required by this tender.

  - “The parties in this Agreement agree that the offer price of all the equipment shall be at the wholesale price or below wholesale price as agreed with the OEM. Should, at any time during the existence of the agreement that the offered price which is higher than the wholesale price or as agreed with the OEM, SITA client shall be entitled to such wholesale price with the exclusion of the mark-up which the reseller may have charged”.

NOTE: These conditions will form part of the contract obligations and suppliers are expected to comply in order for SITA to conclude an agreement with the potential suppliers. Failure to comply during finalisation of a contract may result to disqualification.

- COUNTER CONDITIONS

Bidders’ attention is drawn to the fact that amendments to any of the Bid Conditions or setting of counter conditions by bidders may result in the invalidation of such bids.

- FRONTING

  - The SITA supports the spirit of Broad Based Black Economic Empowerment and recognizes that real empowerment can only be achieved through individuals and businesses conducting themselves in accordance with the Constitution and in an honest, fair, equitable, transparent and legally compliant manner. Against this background the SITA any form of fronting.

  - The SITA, in ensuring that bidders conduct themselves in an honest manner will, as part of the bid evaluation processes, conduct or initiate the necessary enquiries/investigations to determine the accuracy of the representation made in bid documents. Should any of the fronting indicators as contained in the Guidelines on Complex Structures and Transactions and Fronting, issued by the Department of Trade and Industry, be established during such enquiry/investigation, the onus will be on the bidder / contractor to prove that fronting does not exist. Failure to do so within a period of 14 days from date of notification may invalidate the bid / contract and may also result in the restriction of the bidder/contractor to conduct business with the public sector for a period not exceeding ten (10) years, in addition to any other remedies SITA may have against the bidder/contractor concerned.

- BUSINESS CONTINUITY AND DISASTER RECOVERY PLANS

- The bidder confirms that they have written business continuity and disaster recovery plans that define the roles, responsibilities and procedures necessary to ensure that the required services under this bid specification is in place and will be maintained continuously in the event of a disruption to the bidder’s operations, regardless of the cause of the disruption.

- SUPPLIER DUE DILIGENCE

SITA/ Client reserves the right to conduct supplier due diligence prior to final award or at any time during the Contract period and this may include pre-announced/ non-announced site visits. During the due diligence process the information submitted by the bidder will be verified and any misrepresentation thereof may disqualify the bid or Contract in whole or parts thereof.

## DECLARATION OF COMPLIANCE

|  | ACCEPT ALL | DO NOT ACCEPT ALL |
| --- | --- | --- |
| - The bidder declares to ACCEPT ALL the Special Condition of Contract as specified in section 7.2 above by indicating with an “X” in the “ACCEPT ALL” column, OR - The bidder declares to NOT ACCEPT ALL the Special Conditions of Contract as specified in section 7.2 above by - - Indicating with an “X” in the “DO NOT ACCEPT ALL” column, and; - Provide reason and proposal for each of the conditions that is not accepted. |  |  |
| Comments by bidder: Provide reason and proposal for each of the conditions not accepted as per the format: Condition Reference: Reason: Proposal: |  |  |

COSTING AND PRICING

# COSTING AND PRICING

## COSTING AND PRICING EVALUATION

- In terms of Preferential Procurement Policy Framework Act (PPPFA), the following preference point system is applicable to all Bids:

  - the 80/20 system (80 Price, 20 B-BBEE) for requirements with a Rand value of up to R50 000 000 (all applicable taxes included); or

  - the 90/10 system (90 Price and 10 B-BBEE) for requirements with a Rand value above R50 000 000 (all applicable taxes included).

- This bid will be evaluated using the preferential point system of 80/20, subject to the following conditions –

  - If the lowest acceptable bid price is up to and including R50 000 000 (all applicable taxes included) then the 80/20 preferential point system will apply to all acceptable bids; or

  - If the lowest acceptable bid price is above R50 000 000 (all applicable taxes included) then the 90/10 preferential point system will apply to all acceptable bids;

- The bidder must complete the declaration of acceptance as per section 8.4 below by marking with an “X” either “ACCEPT ALL”, or “DO NOT ACCEPT ALL”, failing which the declaration will be regarded as “DO NOT ACCEPT ALL” and the bid will be disqualified.

- Bidder will be bound by the following general costing and pricing conditions and SITA reserves the right to negotiate the conditions or automatically disqualify the bidder for not accepting these conditions. These conditions will form part of the Contract between SITA and the bidder. However, SITA reserves the right to include or waive the condition in the Contract.

## COSTING AND PRICING CONDITIONS

- SOUTH AFRICAN PRICING. The total price must be VAT inclusive and be quoted in South African Rand (ZAR).

- TOTAL PRICE

  - All quoted prices are the total price for the entire scope of required services and deliverables to be provided by the bidder.

  - The cost of delivery, labour, S&T, overtime, etc. must be included in this bid.

  - All additional costs must be clearly specified.

  - The bidder to ensure the accuracy and calculation of the values used in the pricing schedule corresponds quantities and unit prices.

- SITA will budget for provisional amounts for corrective/remedial materials and spares to be purchased.

- Percentage mark-up on materials for corrective/remedial to be purchased may not exceed 15%;

## BID PRICING SCHEDULE

- The bidder must complete the pricing schedule as per attached spreadsheet.

- All the services will be on work order basis and actual quantities might change.

- The indicative maintenance labour unit rates will be used for payments of corrective/remedial maintenance.

- All the rates for specified/scheduled services must include travel to the relevant site, labour, material and tools and the specified service pack required to perform the specified services

Note: Bidders will complete the bid pricing schedule in the Excel spreadsheet format provided    and include this as part of the hard copy submission documents and on the memory stick/USB.

NB: SITA reserves the right to negotiate pricing with the successful bidder prior to the award as well as envisaged quantities.

## DECLARATION OF ACCEPTANCE

|  | ACCEPT ALL | DO NOT ACCEPT ALL |
| --- | --- | --- |
| - The bidder declares to ACCEPT ALL the Costing and Pricing conditions as specified in section 8.2 above by indicating with an “X” in the “ACCEPT ALL” column, or - The bidder declares to NOT ACCEPT ALL the Costing and Pricing Conditions as specified in section 8.2 above by - - Indicating with an “X” in the “DO NOT ACCEPT ALL” column, and; - Provide reason and proposal for each of the condition not accepted. |  |  |
| Comments by bidder: Provide the condition reference, the reasons for not accepting the condition. |  |  |

TERMS AND DEFINITIONS

# ABBREVIATIONS

BBBEE	Broad Based Black Economic Empowerment

CSD		Central Supplier Database

EME		Exempted Micro Enterprise

GCC		General Condition of Contract

ICT		Information and Communication Technology

IEC		International Electro-technical Commission

ISO		International Standardization Organization

LV		Low Voltage

N/A		Not Applicable

NT		National Treasury

OEM		Original Equipment Manufacturer

OSM		Original Software Manufacturer

PDP		Power Distribution Panels

POC		Proof of Concept

QSE		Qualifying Small Enterprise

RFA		Request for Accreditation

RFB		Request for Bid

RFP		Request for Proposal

RFQ		Request for Quotation

RSA		Republic of South Africa

SBD		Standard Bidding Document

SCC		Special Condition of Contract

SCM		Supplier Chain Management

SITA		State Information Technology Agency

SMME	Small Medium and Micro Enterprise

TCV		Total Contract Value

UPS		Uninterrupted Power Supply

USD		United States Dollar

VAT		Value Added Tax

ZAR 		South African Rand

BIDDER SUBSTANTIATING EVIDENCE

# MANDATORY REQUIREMENT EVIDENCE

## SUPPLIER CERTIFICATION / AFFILIATION REQUIREMENTS

Attach a copy of documentation (valid certificate, license, or letter) from the Department of Labour as evidence that the bidder is registered as an electrical contractor.

## SUPPLIER EXPERIENCE AND CAPABILITY REQUIREMENTS

- Complete table below, noting that:

    - The bidder must have executed maintenance of a UPS System with minimum unit capacity of 160 kVA at Data Centre or Equivalent High Availability Environment (Hospital, Airport, Bank, or similar High Availability Environments);

    - The bidder must have executed maintenance of a Vented Lead Acid Battery Banks at Data Centre or Equivalent High Availability Environment (Hospital, Airport, Bank, or similar High Availability Environments),

    - Project end-date must be current or not older than 5 years from date this bid is advertised,

    - Scope of work must be related.

Table 1: References

| No | Company name | Reference Person Name, Tel and/or email | Project Scope of work | Project Start and End-date |
| --- | --- | --- | --- | --- |
|  | <Company name> <Site Address> | <Person Name> <Tel> <email> | < Provide scope details of the UPS system Maintenance Support Contract that was delivered in the last five (5) years. | Start Date: End Date: |
|  | <Company name> <Site Address> | <Person Name> <Tel> <email> | < Provide scope details of the Vented Lead Acid Battery Banks Maintenance Support Contract that was delivered in the last five (5) years. | Start Date: End Date: |

## CIDB REGISTRATION REQUIREMENTS

- The Bidder needs to complete and sign ANNEX D to confirm that the Bidder is registered with the Construction Industry Development Board (CIDB) with a minimum rating of 4EB PE or 4EP PE or 5EB or 5EP. Attach signed Annex D and supporting information here.

## TECHNICAL MANDATORY FUNCTIONAL REQUIREMENTS

- The Bidder must confirm that they comply with the Service Functional Requirements by completing ANNEX C: Addendum1 below and attach it here.

SERVICE FUNCTIONAL REQUIREMENTS: Addendum 1

The bidder must confirm that they comply with the Service Functional Requirements for the provision of Maintenance for SITA UPS system)

| No | Service and Support (Milestones) | Timelines | Indicate Comply=Yes / Not Comply =No |
| --- | --- | --- | --- |
|  | On-site Disaster Recovery Support with a maximum 60-minutes incident response time. | For the duration of the contract. |  |
|  | On-site Preventive/Routine/Scheduled maintenance. | For the duration of the contract. |  |
|  | On-site Corrective/Remedial maintenance. | For the duration of the contract. |  |
|  | On-site Call Outs. | For the duration of the contract. |  |
|  | On-site Emergency Maintenance followed by a Root Cause Analysis. | For the duration of the contract. |  |
|  | Support and critical repairs (with a maximum 60-minutes incident response time) on UPS Systems of which the major components. | For the duration of the contract. |  |
|  | Planned, periodic maintenance services on the following major components: | For the duration of the contract. |  |
|  | Required service level: Availability 24/7/365, with a maximum 60-minutes incident response time. | For the duration of the contract. |  |
|  | Upon SITA’s request, the bidder must provide inspection, and quality assurance services on other SITA electrical contractors’ work performed for SITA of systems that have impact to the equipment performance and services on this scope. | For the duration of the contract. |  |
|  | The contractor shall perform plant room maintenance and plant inspections (as defined) The relevant plant rooms and passage ways are: - UPS Room; and - Battery Room. | For the duration of the contract. |  |
|  | Upon SITA’s request, provide services relating to the isolation and commissioning l infrastructure specified in this scope. | For the duration of the contract. |  |
|  | The services described under this scope will be required for a period of sixty(60) months. The service will be “works order based” for known corrective maintenance requirements, and be “callout based” (followed by a works order) for power incidents where immediate response is required. | For the duration of the contract. |  |
|  | The Supplier represents that, it has the necessary expertise, skill, qualifications and ability to undertake the work required in terms of the Statement of Work or Service Definition with the technical personnel qualified and OEM trained | For the duration of the contract. |  |
|  | The Supplier must ensure that preventative work or service on the UPS system is performed according to OEM requirements. | For the duration of the contract. |  |
|  | The Supplier must be able to access to the UPS control system for service diagnostics and possible repairs. The Supplier must have the latest software as approved by OSM | For the duration of the contract. |  |

I, the bidder (Full names)………………………………………………………….representing (company name)…………………………………………………………….. Hereby confirm that I comply with the above Technical Mandatory Requirements and understand that it will form part of the contract and is legally binding.

Thus done and signed at …………………………………….. On this………day of……………..….20….

……………………………….

Signature

CIDB REGISTRATION REQUIREMENT

      - The Bidder needs to indicate their CIDB rating by ticking next to the relevant CIDB rating in the table below:

| Service and Support (Milestones) | CIDB Rating | Indicate the CIDB rating here by ticking next to the appropriate rating | Registration Status Indicate Yes – Active/ No - Expired |
| --- | --- | --- | --- |
| CIDB Rating | 4EB PE |  |  |
|  | 4EP PE |  |  |
|  | 5EB |  |  |
|  | 5EP |  |  |

      - The Bidder needs to provide their CRS number in the space in the table below:

| Requirement | Bidder CRS Number |
| --- | --- |
| Bidder to provide their CRS number: |  |

      - The Bidder needs to also attach proof of CIDB registration with this Annex D.

Note:

SITA reserves the right to verify the information

I, the Supplier (Full names) …………………………………………………. representing (company name) …………………………………………………………….. hereby confirm that the Bidder is registered with Construction Industry Development Board (CIDB) and understand that it will form part of the contract and is legally binding.

Thus done and signed at ……………………………………. On this………day of……………….20….

__________________

Signature

Designation: