# Tender Returnable Technical Schedules

## General

This document provides the specific technical requirements and schedules for the Bidder to complete and return during the Tender phase.

The Bidder completes this document with the clear understating and information presented in. The Bidder is free to deliver information in a free form outside the given tables, wherever this seems to be suitable. However, the Bidder shall abide by the topics and the numbering of the schedules and completely provide the requested information together with the respective schedule.

The column “Tendered” shall be filled in by the Bidder for all items. The given information and specification shall be part of the agreement and binding for all delivery and services.

The technical data sheets shall be supplemented by additional descriptions, explanations, drawings, and all other information necessary for a clear understanding of its application to enable the Employer to undertake the necessary assessment, evaluation, and verification of the technical and performance features of the Tender.

The Bidder ensures that wherever the information is required in respect to multiple units, the Bidder provides the required information on a unit-by-unit basis.

The Bidder provides all figures in this returnable to no more than two decimal places, unless required in specific section/s.

## Experience and Eligibility

### EPC Contractor Experience

Table C-1: General information about EPC Bidder

| No. | Item | Details |  |
| --- | --- | --- | --- |
| 1 | Name of EPC Bidder |  |  |
| 2 | Home office address |  |  |
| 3 | Regional office address |  |  |
| 4 | Telephone / email address |  |  |
| 5 | Name, Position and Title of contact person |  |  |
| 6 | Legal form |  |  |
| 7 | Area of main business |  |  |
| 8 | No. of staff in main business | Engineers: | Others: |
| 9 | Number of Solar PV power projects successfully completed |  |  |

Table C-2: Specific EPC PV Project Experience

| Item No. | Description | Unit | Required | Tendered |
| --- | --- | --- | --- | --- |
| 1 | Experience |  |  |  |
| 1.1 | Number of PV projects designed, constructed, and commissioned by EPC Bidder | Number | Successful execution of at least one (1) completed commercial ground mounted PV project within the last seven (7) years |  |
| 1.2 | Capacity of Solar PV projects previously designed, constructed and commissioned by the EPC Bidder as principal EPC Contractor | MWac | At least one (1) project shall be ≥ 24 MWac |  |
| 2 | Project Details from experience presented above |  |  |  |
| 2.1 | Name of Solar PV plant | - | To be provided by Bidder |  |
| 2.2 | Location of Solar PV plant | - | To be provided by Bidder |  |
| 2.3 | Name of Solar PV plant Owner(s) / Developer(s) | - | To be provided by Bidder |  |
| 2.4 | Contact details of Solar PV plant Owner(s) / Developer(s) | - | To be provided by Bidder |  |
| 2.5 | Type of PV module technology | - | To be provided by Bidder |  |
| 2.6 | Type of PV mounting (fixed-tilt, tracking) | - | To be provided by Bidder |  |
| 2.7 | Installation capacity | MWac | ≥ 24 |  |
| 2.8 | Duration of construction | Months | To be provided by Bidder |  |
| 2.9 | Commercial operation date | - | To be provided by Bidder |  |
| 2.10 | Photographs if possible | - | To be provided by Bidder |  |
| 2.11 | Proof verifying completed Solar PV plant in the form of contract, test on completion certificate, or take over certificate, with references from solar PV plant Owner(s) / Developer(s) | - | To be provided by Bidder |  |

### O&M Contractor Experience

  - The EPC Contractor will perform the role of O&M Contractor during the O&M period, defined as the first two (2) years of plant operations and maintenance during the Defects Liability Period. The EPC Contractor must have successfully performed or subcontracted the Operations and Maintenance (O&M) duties for at least two (2) years for at least one (1) commercial ground mounted PV plant with an installed capacity greater than 24 MWac.

  - The required operations and maintenance experience must be presented as indicated in Table C-4Table C-2: .

If the EPC Contractor is subcontracting the work for operations and maintenance of the Project for the O&M period, then the required Subcontractor’s general information must be included as indicated in Table C-3: , and the Subcontractor’s operations and maintenance experience must be presented as indicated in Table C-4:Table C-4. Furthermore, a signed letter of intent between the two parties shall be submitted during the tender stage.

Table C-3: General information about O&M Service Provider

| No. | Item | Details |  |
| --- | --- | --- | --- |
| 1 | Name of O&M Service Provider |  |  |
| 2 | Home office address |  |  |
| 3 | Regional office address |  |  |
| 4 | Telephone / email address |  |  |
| 5 | Name, Position and Title of contact person |  |  |
| 6 | Legal form |  |  |
| 7 | Area of main business |  |  |
| 8 | No. of staff in main business | Engineers: | Others: |
| 9 | Number of Solar PV power projects successfully operated and maintained |  |  |
| 10 | Signed letter of intent between O&M Service Provider and EPC Bidder (if subcontracting O&M service) | To be provided by Bidder |  |

Table C-4: Specific O&M PV Project Experience

| Item No. | Description | Unit | Required | Tendered |
| --- | --- | --- | --- | --- |
| 1 | Experience |  |  |  |
| 1.1 | Number of PV projects operated and maintained by O&M Contractor | Number | Successful O&M of at least one (1) commercial ground mounted PV plant |  |
| 1.2 | Capacity of individual solar PV project(s) previously operated and maintained by the O&M Contractor | MWac | ≥ 24 |  |
| 1.3 | Period of operations and maintenance for each of the PV projects listed | Years | Successful O&M duties for at least two (2) years per PV project |  |
| 2 | Project Details from experience presented above |  |  |  |
| 2.1 | Name of Solar PV plant | - | To be provided by Bidder |  |
| 2.2 | Location of Solar PV plant | - | To be provided by Bidder |  |
| 2.3 | Name of Solar PV plant Owner(s) / Developer(s) | - | To be provided by Bidder |  |
| 2.4 | Contact details of Solar PV plant Owner(s) / Developer(s) | - | To be provided by Bidder |  |
| 2.5 | Type of PV module technology | - | To be provided by Bidder |  |
| 2.6 | Type of PV mounting (fixed-tilt, tracking) |  | To be provided by Bidder |  |
| 2.7 | Installation capacity | MW | ≥ 24 |  |
| 2.8 | Duration of operations and maintenance | Months | To be provided by Bidder |  |
| 2.9 | Commercial operation date | - | To be provided by Bidder |  |
| 2.10 | Photographs if possible | - | To be provided by Bidder |  |
| 2.11 | Proof verifying Solar PV plant O&M duties in the form of EPC Contract(s) or O&M Contract(s) contract, test on completion certificate, take over certificate, or letter from Owner(s) / Developer(s) | - | To be provided by Bidder |  |

## Project Implementation Schedule

- The Bidder shall provide a Level II project implementation schedule showing all the Project activities to be performed, including activities that will be subcontracted. The entire scope of works of the Project shall be represented.

## Key Personnel

  - The Bidder shall ensure that suitably qualified personnel are included in design, construction, commissioning, operation, and maintenance of the Project. The minimum requirements of key personnel for the Project are presented in Table C-5.

  - The Bidder shall provide a detailed organogram for the entire project, including the design, construction, commissioning, operation, and maintenance phases. The organogram shall indicate the key personnel for the project

  - The Bidder shall provide the detailed CV of each key personnel responsible including ECSA or equivalent registration where applicable for the works mentioned in Table C-5Table C-5: and indicated on the detailed organogram.

  - If any replacement is required during the design, construction, commissioning, operation, and maintenance of the Project, the Bidder shall ensure that the replacement has equivalent or higher experience and qualifications than the one being replaced.

Table C-5: Experience of Key Personnel

| Item No. | Description | Unit | Required | Tendered |
| --- | --- | --- | --- | --- |
| 1 | Designer |  |  |  |
| 1.1 | Solar PV system | Years | ≥ 5 |  |
| 1.2 | Electrical works | Years | ≥ 5 |  |
| 1.3 | C&I works | Years | ≥ 5 |  |
| 1.4 | Civil / Structural works | Years | ≥ 5 |  |
| 1.5 | Structural works | Years | ≥ 5 |  |
| 2 | Managers |  |  |  |
| 2.1 | Site Manager during construction | Years | ≥ 5 |  |
| 2.2 | Site Manager during operation and maintenance | Years | ≥ 3 |  |
| 2.3 | Project Manager | Years | ≥ 3 |  |  |
| 2.4 | Commissioning Manager | Years | ≥ 5 |  |  |
| 2.5 | Quality Manager | Years | ≥ 5 |  |  |
| 2.6 | Health, Safety, and the Environment (HSE) Manager | Years | ≥ 5 |  |  |
| 3 | Trainers – Design, Construction, Commissioning, and O&M |  |  |  |
| 3.1 | Training Coordinator | Years | ≥ 3 |  |
| 4 | Detailed CV of all personnel mentioned above | - | To be provided by Bidder |  |
| 5 | Organogram for the entire project, including the design, construction, commissioning, operation, and maintenance phases | - | To be provided by Bidder |  |

## Equipment Warranty

  - The Bidder provides equipment warranty according to minimum requirement set in Table C-6: below.

In addition (and without prejudice) to the defect’s liability, the Bidder releases warranty on equipment (including not limited to strategic part warranty). No equipment warranty shall limit another warranty or otherwise.

The Bidder transfers the ownership of all manufacturer equipment warranties to the Employer during the Substantial Completion of the Project.

Table C-6: Equipment Warranty

| Equipment |  | Minimum Warranty Period in Years | Warranty Period in Years provided by Bidder |
| --- | --- | --- | --- |
| PV Modules | Product Warranty against Manufacturing defects | 12 |  |
|  | Linear Power Performance | 25 |  |
| Mounting structures | Steel structure components | 10 |  |
|  | Corrosion | 20 |  |
|  | Tracker motors and gear (if applicable) | 5 |  |
|  | Communication and Control system (if applicable) | 2 |  |
| Inverters |  | 5 |  |
| MV Transformers |  | 5 |  |
| MV Switchgear (Primary and Secondary distribution) |  | 5 |  |
| HV Transformers |  | 5 |  |
| HV Switchgear |  | 5 |  |
| Civil Works (latent defect warranty) |  | 10 |  |

## Solar PV Plant Configuration and Performance Criteria

  - The Bidder ensures the Solar PV system design is performed according to all relevant standards, permits, licenses, best industry practice, and according to the site conditions.

The Bidder designs a PV Plant with a minimum AC capacity of 24 MWac, complying with the requirements indicated below.

Table C-7: Solar PV System Design

| Item No. | Description | Unit | Required | Tendered |
| --- | --- | --- | --- | --- |
| 1 | Basic Design Conditions |  |  |  |
| 1.1 | Design lifetime of the plant | Years | ≥ 25 |  |
| 1.2 | Ambient Temperature | ° C | -5 to 55 |  |
| 1.3 | Complying with site environmental conditions | Yes/No | Yes |  |
| 1.4 | Complying with Environmental Permit and Water Use license permit | Yes/No | Yes |  |
| 2 | PV Capacity |  |  |  |
| 2.1 | Nominal AC capacity | MWac | ≥ 24 |  |
| 2.2 | DC capacity | MWp | ≥ 28 |  |
| 2.3 | Ratio of DC to AC capacity | - | ≥ 1.15 |  |
| 3 | Major Components – General Information |  |  |  |
| 3.1 | Total number of PV modules offered for the project | - | To be provided by Bidder |  |
| 3.2 | Total number of inverters offered for the project | - | To be provided by Bidder |  |
| 3.3 | Total number of Inverter Stations offered for the project (if applicable) | - | To be provided by Bidder |  |
| 3.4 | Total number of MV/LV inverter transformers offered for the project | - | To be provided by Bidder |  |
| 4 | PV Module – Inverter Configuration |  |  |  |
| 4.1 | Number of PV modules per string | - | To be provided by Bidder |  |
| 4.2 | String voltage (Vmpp) at maximum operating module temperature (at 85°C module temperature) | V | ≥ 110% of minimum MPP input voltage of respective inverter |  |
| 4.3 | String voltage (Vmpp) at minimum operating module temperature (at 0° C module temperature) | V | Below the maximum MPP input voltage of respective inverter |  |
| 4.4 | String voltage (Voc) at minimum module temperature (at 0° C module temperature) | V | Below the maximum input voltage of respective inverter |  |
| 5 | Supportive Information |  |  |  |
| 5.1 | PV Array Layout | Yes/No | Yes |  |
| 5.2 | String Voltage calculation | Yes/No | Yes |  |
| 5.3 | Technical datasheet of PV module | Yes/No | Yes |  |
| 5.4 | Technical datasheet of PV module mounting structure / tracker | Yes/No | Yes |  |
| 5.5 | Technical datasheet of inverter | Yes/No | Yes |  |
| 5.6 | Technical datasheet of Inverter Stations | Yes/No | Yes |  |
| 5.7 | Technical datasheet of MV/LV inverter transformer | Yes/No | Yes |  |

## Guarantee on Performance and Availability

  - The Bidder provides guarantee on the:

Plant Performance Ratio (PR), and

Plant Availability

  - These Performance Guaranteed Values will be verified during the Provisional Acceptance Certificate (PAC) Test (PAT) and Final Acceptance Certificate (FAC) Tests.

  - The actual Performance Ratio (PR) shall be evaluated at 100% plant availability. The actual Plant Availability shall be evaluated separately.

  - The Bidder is required to provide Performance Guaranteed Values as indicated in Error! Reference source not found.

Table C-8 Plant Performance Guarantees

| Year | Parameter | Minimum required by Employer | Guaranteed by Bidder |
| --- | --- | --- | --- |
| 1 | Guaranteed annual average Performance Ratio for year 1 of operation - Tests After Date of Completion (Year 1) | 78 % |  |
|  | Guaranteed annual average Plant Availability for year 1 of operation - Tests After Date of Completion (Year 1) | 98 % |  |
| 2 | Guaranteed annual average Performance Ratio for year 2 of operation - Tests After Date of Completion (Year 2) | 78 % |  |
|  | Guaranteed annual average Plant Availability for year 2 of operation - Tests After Date of Completion (Year 2) | 98 % |  |

With regards to the “Guaranteed annual average Performance Ratio for year 1 of operation - Tests After Date of Completion (Year 1)” provided in Error! Reference source not found., the Bidder is required to provide a monthly breakdown of this year 1 Performance Ratio (PR) guarantee, along with estimation of solar irradiation on module plane, in a tabular format as shown in Table C-9.

The Performance Ratio (PR) guaranteed for the Tests After Date of Completion (Year 1) will be the corresponding monthly average PR (shown in Table C-9) during which the test is performed. If the test duration covers period of two consecutive months, then the guaranteed PR during the Tests After Date of Completion (Year 1) is calculated based on weighted average PR of the two respective months.

Table C-9: Monthly breakdown of Guaranteed Performance Ratio for first year

| Month | Breakdown of first year annual guaranteed PR (%) | Estimated Solar Irradiation on Module Plane (kWh/m2) |
| --- | --- | --- |
| January |  |  |
| February |  |  |
| March |  |  |
| April |  |  |
| May |  |  |
| June |  |  |
| July |  |  |
| August |  |  |
| September |  |  |
| October |  |  |
| November |  |  |
| December |  |  |
| Annual Average |  |  |

The Bidder provides the following supportive information and documents (indicated in Table C-10Table C-10:) which shall verify the guaranteed level of Performance Ratio (PR).

Table C-10: Plant Performance Estimation

| Item No. | Description | Unit | Required | Tendered |
| --- | --- | --- | --- | --- |
| 1 | Documents and Diagrams |  |  |  |
| 1.1 | Energy yield assessment report | Yes/No | Yes |  |
| 1.2 | TMY datasets used by the Bidder for energy yield estimation report (P50, P90, and P99 for 1-year, 10-year and 25-year return periods) | Yes/No | Yes |  |
| 1.3 | PV Module tilt angle (for fixed-tilt) | ° | 10 – 25 degrees |  |
| 1.4 | Row to row distance | m | To be provided by Bidder |  |
| 2 | Losses Estimation |  |  |  |
| 2.1 | Near shading losses | % | ≤ 2.5 |  |
| 2.2 | Reflection (IAM) losses | % | To be provided by Bidder |  |
| 2.3 | Soiling losses | % | To be provided by Bidder |  |
| 2.4 | Losses due to irradiance level | % | To be provided by Bidder |  |
| 2.5 | Losses due to temperature | % | To be provided by Bidder |  |
| 2.6 | Mismatch losses | % | To be provided by Bidder |  |
| 2.7 | Module quality losses | % | To be provided by Bidder |  |
| 2.8 | DC cabling losses | % | To be provided by Bidder |  |
| 2.9 | AC cabling losses | % | To be provided by Bidder |  |
| 2.10 | Losses in inverter | % | To be provided by Bidder |  |
| 2.11 | Technical availability | % | To be provided by Bidder |  |
| 2.12 | MV/LV Transformer losses | % | To be provided by Bidder |  |
| 2.13 | Self-consumption losses | % | To be provided by Bidder |  |
| 2.14 | Power evacuation losses | % | To be provided by Bidder |  |
| 2.15 | Annual module degradation | % | To be provided by Bidder |  |
| 2.16 | Others (specify) | % | To be provided by Bidder |  |

## Electrical System

### Electrical System Criteria

Table C-11: Electrical Single Line Diagram and Reports

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Full Compliance to Electrical Requirements |  |  |  |
| 1.1 | - The Bidder submits a technical report or methodology confirming full compliance or any deviations if applicable for the electrical design, installation, commissioning, and handover requirements specified in the electrical scope as stipulated 559-189375010, Installation of Solar PV Plant at Tutuka Power Station Functional Specification. | - | To be provided by Bidder |  |
| 2 | Type Test Certificates and/or Datasheets |  |  |  |
| 2.1 | Submission of typical Type test certificate and/or datasheet for Primary and Secondary MV Switchgear | - | To be provided by Bidder |  |
| 2.2 | Typical Type Test certificate and/or datasheet for HV/MV Power Transformer. | - | To be provided by Bidder |  |
| 3 | Plant Electrical Single Line Diagram |  |  |  |
| 3.1 | Submission of a high level Conceptual Electrical reticulation or Single Line Drawing containing the following as a minimum: - PV Modules - DC and AC Cabling - Combiner boxes - Inverter stations - Primary and secondary Switchgear - HV/MV Transformers - Power protection and surge devices - Overhead line - Indication of Point of Connection (POC) | - | To be provided by Bidder |  |
| 4 | Power System Study |  |  |  |
| 4.1 | Submission of Power System Study report previously done by the Contractor for similar scope of work | - | To be provided by Bidder |  |

### Technical Schedules

#### PV Modules

Table C-12: PV Modules Schedules

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Product information |  |  |  |
| 1.1 | PV Module manufacturer | Name | To be provided by Bidder |  |
| 1.2 | Proof / supporting documentation that the offered PV module manufacturer is on the BNEF PV Module Tier 1 list | - | To be provided by Bidder |  |
| 1.3 | Module Type | - | To be provided by Bidder |  |
| 2 | Technical Characteristics |  |  |  |
| 2.1 | PV Module/Cell technology | - | To be provided by Bidder |  |
| 2.2 | String maximum Voltage | VDC | 1500 |  |
| 2.3 | Positive Power Tolerance | W | 0 to +5 (or 0 to +3%) |  |
| 2.4 | Module efficiency | % | ≥ 20% |  |
| 2.5 | Bifaciality factor for bifacial module, where applicable | % | ≥ 70% ±5% |  |
| 2.6 | Operating temperature | °C | between -40 °C and 85 °C |  |
| 2.7 | Static mechanical load | Pa | ≥ 2400 |  |
| 2.8 | Increased distributed mechanical load on the front glass surface | Pa | ≥ 5400 |  |
| 2.9 | Temperature coefficient | %/°C | ≥ -0.37 |  |
| 2.10 | Light induced degradation loss | % | ≤ 2 |  |
| 2.11 | Nominal Module Operating Temperature (NMOT) lower than or equal to | °C | ≤ 44 °C ±2 °C (NMOT @800 W/m2, 20 °C, AM 1.5, Wind speed 1 m/s) |  |
| 3 | Product Performance Guarantee |  |  |  |
| 3.1 | Power output guaranteed during the first year of operation | % | Minimum: 98% |  |
| 3.2 | Linear power degradation coefficient from year 2 to year 25 | %/year | Maximum degradation of -0.55%/year |  |
| 3.3 | Guaranteed output of the nominal power after 10 years | % | Minimum 90% |  |
| 3.4 | Guaranteed output of the nominal power after 25 years | % | Minimum 80% |  |
| 4 | Minimum Certificates and Standards |  |  |  |
| 4.1 | As per 559-189375010, Installation of Solar PV Plant at Tutuka Power Station Functional Specification, indicating required minimum certificates and standards. | Yes/No | Yes |  |
| 5 | Track Record |  |  |  |
| 5.1 | Manufacturer Production track record | year | ≥ 5 |  |
| 5.2 | Minimum annual production capacity | MWp | ≥ 500 |  |
| 5.3 | Capacity installed | MWp | ≥ 1,000 |  |
| 5.4 | A letter of confirmation certifying that the above requirements are met shall be issued by the module manufacturer and received by the Employer. | - | To be provided by Bidder |  |
| 5.5 | Module type in operation in at least three (3) commercial plants of similar size (>24 MWac) that have been in successful operation for at least one (1) year. | Yes/No | Yes |  |
| 5.5.1 | Location of each Project | - | To be provided by Bidder |  |
| 5.5.2 | Capacity of each Project | MWp | To be provided by Bidder |  |
| 5.5.3 | Commercial operation date of each project | - | To be provided by Bidder |  |
| 6 | Supportive Documents |  |  |  |
| 6.1 | Module Datasheet | - | To be provided by Bidder |  |
| 6.2 | Brief description of the cleaning strategy instruction (from module manufacturer) | - | To be provided by Bidder |  |
| 6.3 | A letter of confirmation certifying that module manufacturer track record is as per 5.1, 5.2, and 5.3 of this table. | - | To be provided by Bidder |  |
| 6 | Additional Information – To be listed by the Bidder |  |  |  |
| 6.1 | To be defined by the Bidder | - |  |  |

#### Inverters

Table C-13: Inverter Schedules

| Item No. | Description | Unit | Required | Response from Bidder |  |
| --- | --- | --- | --- | --- | --- |
| 1 | Product information |  |  |  |  |
| 1.1 | Inverter manufacturer | Name | To be provided by Bidder |  |  |
| 1.2 | Inverter Type | - | To be provided by Bidder |  |  |
| 2 | Track Record |  |  |  |  |
| 2.1 | Manufacturer Production track record | year | ≥ 5 |  |  |
| 2.2 | Minimum annual production capacity | MW | ≥ 500 |  |  |
| 2.3 | Minimum capacity installed | MW | ≥ 1,000 |  |  |
| 2.4 | A letter of confirmation certifying that the above requirements are met shall be issued by the inverter manufacturer and received by the Employer. | - | To be provided by Bidder |  |  |
| 2.5 | Inverter type or series in operation in at least three (3) commercial plants totalling 200 MWac or higher nominal power (not demonstration projects), for at least twelve (12) months and have recorded a technical availability of at least 99% for twelve (12) consecutive months of operation. | Yes/No | Yes |  |  |
| 2.5.1 | Location of each Project | - | To be provided by Bidder |  |  |
| 2.5.2 | Capacity of each Project | MW | To be provided by Bidder |  |  |
| 2.5.3 | Commercial operation date of each project | - | To be provided by Bidder |  |  |
| 2.6 | Inverter type or series in operation in similar ambient conditions (up to ≥ 50°C) | months | ≥ 12 |  |  |
| 3 | Inverter Characteristics |  |  |  |  |
| 3.1 | Inverter technology/type | - | Central/String |  |  |
| 3.2 | Inverter rated capacity per unit | MVA | To be provided by Bidder |  |  |
| 3.3 | Nominal AC output Voltage | V | To be provided by Bidder |  |  |
| 3.4 | Maximum conversion efficiency | % | ≥ 98 |  |  |
| 3.5 | European efficiency | % | ≥ 98 |  |  |
| 3.6 | Operating ambient temperature range | °C | -5 … +50 |  |  |
| 3.7 | Cooling method/mechanism | - | To be provided by Bidder. (The inverter cooling method shall be designed for installation and operating site conditions to ensure the inverter functions within its operating ambient temperature range) |  |  |
| 3.8 | Inverter Maximum DC voltage | V | 1,500 |  |  |
| 3.9 | Connection phases | - | Three-Phase |  |  |
| 3.10 | Frequency | Hz | 50 |  |  |
| 3.11 | Total harmonic distortion, Power Factor, Anti-islanding protection | - | According to South African Grid code compliance: Grid connection code for Renewable Power Plants (RPPs) connected to the electricity Transmission system (TS) or the Distribution system (DS) in South Africa |  |  |
| 3.14 | Protection type IP rating | IP | Indoor ≥ IP54, Outdoor ≥ IP65 |  |  |
| 3.15 | Controllability of inverter output per remote control / energy management system, if possible. | Yes/No | Yes: Dynamic adjustable |  |  |
| 3.16 | Earthing concept/philosophy | Yes/No | Yes Earthing according to installation requirements of PV module and inverter manufacturer. |  |  |
| 3.17 | Input Failure detection | Yes/No | Yes |  |  |
| 3.18 | Frequency protection | Yes/No | Yes |  |  |
| 3.19 | DC overvoltage protection | Yes/No | Yes |  |  |
| 3.20 | Surge protection | Yes/No | Yes |  |  |
| 4 | Minimum required standards |  |  |  |  |
| 4.1 | As per 559-189375010, Installation of Solar PV Plant at Tutuka Power Station Functional Specification indicating required minimum certificates and standards. | Yes/No | Yes |  |  |
| 5 | Monitoring system requirements |  |  |  |
| 5.1 | Continuous data logging to the CMS system for the defined technical plant performance parameters including events and status | Yes/No | Yes |  |  |
| 5.2 | Connection interface to CMS | Yes/No | Yes |  |  |
| 6 | Product Warranty Extension |  |  |  |  |
| 6.1 | The Bidder shall indicate if the inverter manufacturer has an option for extension of product warranty. If yes, maximum duration of the warranty shall be indicated | years | To be provided by Bidder |  |  |
| 7 | Supportive Documents |  |  |  |  |
| 7.1 | Inverter datasheet | - | To be provided by Bidder |  |  |
| 7.2 | A letter of confirmation certifying that inverter manufacturer track record is as per 2.1, 2.2, and 2.3 of this table. | - | To be provided by Bidder |  |  |
| 8 | Additional Information – To be listed by the Bidder |  |  |  |  |
| 8.1 | To be defined by the Bidder | - |  |  |  |

#### Inverter Station

Table C-14: Inverter Station Schedules

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Product information |  |  |  |
| 1.1 | Inverter Station manufacturer | Name | To be provided by Bidder |  |
| 2 | Track Record |  |  |  |
| 2.1 | Have been used in Projects of 24 MWac in capacity or more. | Yes/No | Yes |  |
| 2.1.1 | Location of project | - | To be provided by Bidder |  |
| 2.1.2 | Capacity of project | - | To be provided by Bidder |  |
| 2.1.3 | Commercial operation date | - | To be provided by Bidder |  |
| 3 | Inverter Station Characteristics |  |  |  |
| 3.1 | For central inverter; shall at minimum house inverters and associated protection and control equipment and LV/LV auxiliary transformer. | Yes/No | Yes |  |
| 3.2 | Ventilation system type | - | To be defined by the Bidder |  |
| 3.3 | Degree of Protection (SANS 60529) | IP | ≥ IP65 |  |
| 3.4 | Designed/protected to withstand outdoor conditions for at least 25 years | Yes/No | Yes |  |
| 3.5 | Fire protection system | Yes/No | Yes |  |
| 3.6 | Corrosion resistance | Yes/No | Yes |  |
| 4 | Product Warranty |  |  |  |
| 4.1 | Product warranty | Year | ≥ 5 |  |
| 5 | Supportive Documents |  |  |  |
| 5.1 | Inverter Power Station datasheet | - | To be provided by Bidder |  |
| 6 | Additional Information – To be listed by the Bidder |  |  |  |
| 6.1 | To be defined by the Bidder | - |  |  |

#### MV/LV Inverter transformer

Table C-15: MV/LV Inverter transformer Schedules

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Product information |  |  |  |
| 1.1 | MV/LV Inverter transformer manufacturer | Name | To be provided by Bidder |  |
| 2 | Transformer Characteristics |  |  |  |
| 2.1 | Transformer Type | - | To be provided by Bidder |  |
| 2.2 | Rated Capacity | MVA | To be provided by Bidder |  |
| 2.3 | Nominal Voltage (Low voltage side) | V | To be provided by Bidder |  |
| 2.4 | Nominal Voltage (Medium voltage side) | kV | To be provided by Bidder |  |
| 2.5 | Rated Frequency | Hz | 50 |  |
| 2.6 | Tap-Changer Type | - | off-load |  |
| 2.7 | Tap-changer - number of steps | No. | 5 |  |
| 2.8 | Tap-changer –Ratio of each step | % | -5% to 5% |  |
| 2.9 | Type of protection | - | To be provided by Bidder |  |
| 2.10 | Transformer insulating medium | Type | Biodegradable oil or Dry-type |  |
| 2.11 | Transformer Cooling method | - | To be provided by Bidder |  |
| 2.12 | IP Rating | IP | ≥ IP55 for outdoor ≥IP4X for indoor |  |
| 2.13 | No-load losses | W | To be provided by Bidder |  |
| 2.14 | Load losses | W | To be provided by Bidder |  |
| 2.15 | Climatic class (dry-type transformer only) | - | C2 |  |
| 2.16 | Environmental class (dry-type transformer only) | - | E2 |  |
| 2.17 | Fire class (dry-type transformer only) | - | F1 |  |
| 2.18 | Insulation Class (dry-type transformer only) | - | F |  |
| 3 | Minimum required standards (to be proven by respective Certificate or Conformity Declaration) |  |  |  |
| 3.1 | As per 559-189375010, Installation of Solar PV Plant at Tutuka Power Station Functional Specification indicating required minimum certificates and standards | Yes/No | Yes |  |
| 4 | Monitoring system requirements |  |  |  |
| 4.1 | Continuous data logging to the CMS system for the defined transformer performance parameters including events and status. | Yes/No | Yes |  |
| 4.2 | Connection interface to CMS system using protocols. | Yes/No | Yes |  |
| 5 | Supportive Documents |  |  |  |
| 5.1 | Transformer Datasheet | - | To be provided by Bidder |  |
| 6 | Additional Information – To be listed by the Bidder |  |  |  |
| 6.1 | To be defined by the Bidder | - | To be provided by Bidder |  |

#### MV/LV Auxiliary transformer

Table C-16: MV/LV Auxiliary transformer Schedules

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Product information |  |  |  |
| 1.1 | MV/LV Aux transformer manufacturer | Name | To be provided by Bidder |  |
| 2 | Transformer Characteristics |  |  |  |
| 2.1 | Transformer Type | - | To be provided by Bidder |  |
| 2.2 | Rated Capacity | MVA | To be provided by Bidder |  |
| 2.3 | Nominal Voltage (Low voltage side) | V | To be provided by Bidder |  |
| 2.4 | Nominal Voltage (Medium voltage side) | kV | To be provided by Bidder |  |
| 2.5 | Rated Frequency | Hz | 50 |  |
| 2.6 | Tap-Changer Type | - | off-load |  |
| 2.7 | Tap-changer - number of steps | No. | 5 |  |
| 2.8 | Tap-changer –Ratio of each step | % | -5% to 5% |  |
| 2.9 | Type of protection | - | To be provided by Bidder |  |
| 2.10 | Transformer insulating medium | Type | Biodegradable oil or dry-type |  |
| 2.11 | Transformer Cooling method | - | To be provided by Bidder |  |
| 2.12 | IP Rating | IP | ≥ IP55 for outdoor ≥IP4X for indoor |  |
| 2.13 | No-load losses | W | To be provided by Bidder | No-load losses |
| 2.14 | Load losses | W | To be provided by Bidder | Load losses |
| 2.15 | Climatic class (dry-type transformer only) | - | C2 |  |
| 2.16 | Environmental class (dry-type transformer only) | - | E2 |  |
| 2.17 | Fire class (dry-type transformer only) | - | F1 |  |
| 2.18 | Insulation Class (dry-type transformer only) | - | F |  |
| 3 | Minimum required standards (to be proven by respective Certificate or Conformity Declaration) |  |  |  |
| 3.1 | - As per 559-189375010, Installation of Solar PV Plant at Tutuka Power Station Functional Specification, indicating required minimum certificates and standards | Yes/No | Yes |  |
| 4 | Monitoring system requirements |  |  |  |
| 4.1 | Continuous data logging to the CMS system for the defined transformer performance parameters including events and status. | Yes/No | Yes |  |
| 4.2 | Connection interface to CMS system using protocols. | Yes/No | Yes |  |
| 5 | Supportive Documents |  |  |  |
| 5.1 | Transformer Datasheet | - | To be provided by Bidder |  |
| 6 | Additional Information – To be listed by the Bidder |  |  |  |
| 6.1 | To be defined by the Bidder | - | To be provided by Bidder |  |

#### MV Secondary Switchgear (RMU)

Table C-17: MV Switchgear (RMU) Schedules

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Product information |  |  |  |
| 1.1 | Switchgear manufacturer | Name | To be provided by Bidder |  |
| 1.2 | RMU Type/Model | Type | To be provided by Bidder |  |
| 2 | Ratings |  |  |  |
| 2.1 | Nominal voltage | kVrms | To be provided by Bidder |  |
| 2.2 | Rated voltage | kVrms | To be provided by Bidder |  |
| 2.3 | System frequency | Hz | 50 |  |
| 3 | Design |  |  |  |
| 3.1 | Indoor/Outdoor application | - | To be provided by Bidder |  |
| 3.2 | Insulating medium | - | SF6-free GIS |  |
| 3.3 | Interrupting technology (switch dis-connectors) | - | Vacuum |  |
| 3.4 | Interrupting technology (circuit breaker) | - | Vacuum |  |
| 4 | Supportive Documentation |  |  |  |
| 4.1 | RMU datasheet/Catalogue | - | To be provided by Bidder |  |
| 5 | Minimum required standards |  |  |  |
| 5.1 | As per 559-189375010, Installation of Solar PV Plant at Tutuka Power Station Functional Specification, indicating required minimum certificates and standards | Yes/No | Yes |  |
| 6 | Additional Information – To be listed by the Bidder |  |  |  |
| 6.1 | To be defined by the Bidder | - |  |  |

#### MV Primary Switchgear

Table C-18: MV Primary Switchgear Schedules

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Product information |  |  |  |
| 1.1 | Switchgear manufacturer | Name | To be provided by Bidder |  |
| 1.2 | Type/Model | Type | To be provided by Bidder |  |
| 2 | Ratings |  |  |  |
| 2.1 | Nominal voltage | kVrms | To be provided by Bidder |  |
| 2.2 | Rated voltage | kVrms | To be provided by Bidder |  |
| 2.3 | System frequency | Hz | 50 |  |
| 3 | Design |  |  |  |
| 3.1 | Indoor/Outdoor application | - | Indoor |  |
| 3.2 | Insulating medium | - | AIS |  |
| 3.3 | Type | Withdrawable or Fixed-patten | Withdrawable |  |
| 3.4 | Interrupting technology | - | Vacuum |  |
| 4 | Supportive Documentation |  |  |  |
| 4.1 | Switchgear datasheet/Catalogue | - | To be provided by Bidder |  |
| 5 | Minimum required standards |  |  |  |
| 5.1 | As per 559-189375010, Installation of Solar PV Plant at Tutuka Power Station Functional Specification, indicating required minimum certificates and standards | Yes/No | Yes |  |
| 6 | Additional Information – To be listed by the Bidder |  |  |  |
| 6.1 | To be defined by the Bidder | - |  |  |

#### Grid Code Compliance

Table C-19: Grid Code Compliance

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Minimum Plant Technical Grid Code Requirements for category C Plant |  |  |  |
| 1.1 | Voltage range as per Category C in the renewable Grid Code of South Africa | Yes/No | Yes |  |
| 1.2 | Frequency as per Category C in the renewable Grid Code of South Africa | Yes/No | Yes |  |
| 1.3 | Voltage ride through as per Category C in the renewable Grid Code of South Africa | Yes/No | Yes |  |
| 1.4 | Power Quality as per Category C in the renewable Grid Code of South Africa | Yes/No | Yes |  |
| 1.5 | Power Frequency response as per Category C in the renewable Grid Code of South Africa | Yes/No | Yes |  |
| 1.6 | Reactive Power Capabilities as per Category C in the renewable Grid Code of South Africa | Yes/No | Yes |  |
| 1.7 | Protection and fault levels as per Category C in the renewable Grid Code of South Africa | Yes/No | Yes |  |
| 2 | Plant Required Control Functions |  |  |  |
| 2.1 | Voltage Control | Yes/No | Yes |  |
| 2.2 | Power Factor Control | Yes/No | Yes |  |
| 2.3 | Reactive Power Control | Yes/No | Yes |  |
| 3 | Minimum required standards |  |  |  |
| 3.1 | Grid Connection Code for Renewable Power Plants (RPPs) Connected to the Electricity Transmission system (TS) or the Distribution System (DS) in South Africa | Yes/No | Yes |  |
| 4 | Additional Information – To be listed by the Bidder |  |  |  |
| 4.1 | To be defined by the Bidder | - | - |  |

## Control And Monitoring System (CMS)

### CMS Criteria

Table C-20: CMS CRITERIA

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Experience in CMS or SCADA systems for Utility scale PV plant applications |  |  |  |  |
| 1.1 | The Bidder shall provide proof of successful installation of the proposed CMS/SCADA network on PV plants. Proof shall be provided in a table of references with plant name, plant capacity, year commissioned, CMS system details. | - | Five (5) PV plants around the world, of ≥ 24 MWac each, during the past 7 years |  |
| 1.2 | The Bidder provides proof of experience with the proposed software. Proof shall be provided in a table of references with plant name, plant capacity, year commissioned, CMS system details, The CMS details shall include network layout, CMS overview report including Original Equipment Manufacturer (OEM) equipment information of all hardware and software, operator Human Machine Interface (HMI) screen dumps of the various display tabs. | - | Two (2) PV plants ≥ 24 MWac each, during the past 5 years |  |
| 2 | CMS Compliance |  |  |  |  |
| 2.1 | CMS network single line diagram showing Plant Interface architecture (high level) | Yes/No | Yes |  |
| 2.2 | CMS equipment and cable list in tabular format (basic) | Yes/No | Yes |  |
| 2.3 | Field wiring philosophy (basic) | Yes/No | Yes |  |
| 2.4 | CMS power supply and power distribution diagram, showing UPS and battery bank sizing (high level) | Yes/No | Yes |  |
| 2.5 | 19” network cabinet specifications and general arrangement drawing (basic) | Yes/No | Yes |  |
| 2.6 | CMS equipment panel specifications and general arrangement drawings (basic) | Yes/No | Yes |  |
| 2.7 | CMS design report describing the hardware and software, the operating philosophy, information servers and data analysis tools (basic philosophy) | Yes/No | Yes |  |
| 2.8 | Control and server room layout drawing (high-level) | Yes/No | Yes |  |
| 3 | C&I Design Criteria |  |  |  |  |
| 3.1 | The system shall be designed to ensure high availability, i.e., greater than 99.9%. | Yes/No | Yes |  |
| 3.2 | Data shall be stored locally and externally, with periodic backups performed with external hard drives which are to be kept in a secure location. | Yes/No | Yes |  |
| 3.3 | Compliance with Eskom’s Standard for Demilitarised Zone (DMZ) Designs for Operational Technology (240-79669677), Information Security – IT/OT and Third Party Remote Access Standard (32-373), Eskom Cyber Security Standard for Operation Technology (240-55410927), and Human Machine Interface Design Requirements Standard (240-56355728) | Yes/No | Yes |  |
| 3.4 | Open data exchange: data exchange interface must make it possible for the Employer’s centralized control and monitoring system to exchange data with the SCADA system for both real time and historical data. | Yes/No | Yes |  |
| 3.5 | The Plant SCADA system and field control system shall allow for automatic start-up and shut down of the Plant. | Yes/No | Yes |  |
| 3.6 | The field control system shall be designed to ensure normal operation even in the event of loss of software communication link. | Yes/No | Yes |  |
| 3.7 | The Contractor shall ensure that the SCADA system has an operational life span of 25 years from the Plant’s Commercial Operations Date (COD), which involves being capable of adapting to software updates. The Contract shall provide a lifecycle management plan for the SCADA system hardware and the OS and APP software. | Yes/No | Yes |  |
| 3.8 | A minimum of ten (10) user licenses shall be provided to the Employer, and it shall be possible to restrict user-access to rational levels to protect the integrity of the system and prevent unwanted, unwarranted, and/or unsafe Project configuration changes | Yes/No | Yes |  |
| 3.9 | The SCADA system vendor must be able to offer technical support for the operational life of the system. The Contractor shall provide a lifecycle management plan for the SCADA hardware and OS and APP software | Yes/No | Yes |  |
| 3.10 | The Employer will require licenses and access to make changes to the SCADA system/PLC system and all programmable devices as and when required. | Yes/No | Yes |  |
| 4 | High-level plant interface Architecture |  |  |  |  |
| 4.1 | The Bidder will provide a High-level Plant Interface Architecture | - | To be provided by Bidder |  |

### Technical Schedules

Table C-21: Control and Monitoring Systems Schedules

| Item No. | Description | Unit | Required | Tendered |
| --- | --- | --- | --- | --- |
| 1 | Data Sheets and Manuals |  |  |  |
| 1.1 | CMS Servers | Yes/No | Yes |  |
| 1.2 | Network Switches | Yes/No | Yes |  |
| 1.3 | GPS time server | Yes/No | Yes |  |
| 1.4 | Thin clients (CPU, monitors, keyboard, mouse) | Yes/No | Yes |  |
| 1.5 | KVM extenders | Yes/No | Yes |  |
| 1.6 | Firewall gateway | Yes/No | Yes |  |
| 1.7 | Web server | Yes/No | Yes |  |
| 1.8 | Fire panels | Yes/No | Yes |  |
| 1.9 | Fire sensors and alarm equipment | Yes/No | Yes |  |
| 1.10 | Programmable logic controllers | Yes/No | Yes |  |
| 1.11 | IO cards / RTUs | Yes/No | Yes |  |
| 1.12 | UPS and battery banks | Yes/No | Yes |  |
| 1.13 | DC power supplies | Yes/No | Yes |  |
| 1.14 | CMS application software for operating, monitoring and configuration (i.e., SCADA software manual) | Yes/No | Yes |  |
| 1.15 | Antivirus software | Yes/No | Yes |  |
| 1.16 | OPC server software | Yes/No | Yes |  |
| 1.17 | BMS server/workstation | Yes/No | Yes |  |
| 1.18 | BMS application software | Yes/No | Yes |  |
| 2 | CMS Servers |  |  |  |
| 2.1 | No of units | pcs | 2 (dual redundant configuration) |  |
| 2.2 | Manufacturer | - | To be provided by Bidder |  |
| 2.3 | Product/Model/Type | Yes/No | Yes |  |
| 2.4 | Communication capabilities Ethernet, Serial RS485, Optical fibre | Yes/No | Yes |  |
| 2.5 | Redundant array of independent disks (RAID) configuration | Yes/No | Yes |  |
| 2.6 | Redundant power supplies with dual power input ports | Yes/No | Yes |  |
| 2.7 | Redundant case fans, | Yes/No | Yes |  |
| 2.8 | 19” (inch.) rack-mountable type enclosure for the servers and power supplies installed in the plant server room | Yes/No | Yes |  |
| 2.9 | On-board database to continuously process and store all real time plant data for the lifespan of the plant, | Yes/No | Yes |  |
| 2.10 | Tront accessible universal serial bus (USB) ports. | Yes/No | Yes |  |
| 3 | SCADA/CMS Software |  |  |  |
| 3.1 | Microsoft Windows 11 Operating system | Yes/No | Yes |  |
| 3.2 | Only industry recognised software shall be used. | Yes/No | Yes |  |
| 3.3 | Licences for the software systems will be purchased by the Contractor and made available with step-in rights for the future purchasers and operators of the Plant. | Yes/No | Yes |  |
| 3.4 | The Contractor shall provide all project specific software, firmware, and operating system developed for, and applicable to, the control and monitoring systems being provided. The SCADA system shall include novel modelling approaches and techno-financial indicators allowing the operators to predict failures, detect root causes of errors, and optimise the Plant operation in a cost-effective manner. | Yes/No | Yes |  |
| 3.5 | The software shall be completely documented by the Contractor and be provided on a non-proprietary basis. The Contractor shall provide a remote monitoring system and software with a supervisory role and access to historic values. | Yes/No | Yes |  |
| 3.6 | Custom software required to adapt or customise the control and monitoring systems shall be provided by the Contractor. | Yes/No | Yes |  |
| 3.7 | CMS application software for comprehensive operating, monitoring and configuration of all plant equipment and sub-systems | pcs | ≥ 2 |  |
| 3.8 | Web-server application software for remote clients | Yes/No | Yes |  |
| 3.9 | Information server application software | pcs | ≥ 2 |  |
| 3.10 | Hosting the anti-virus software | pcs | ≥ 2 |  |
| 3.11 | Firewall software | Yes/No | Yes |  |
| 3.12 | OPC server software | Yes/No | Yes |  |
| 3.13 | Other 3rd party system software | - | To be provided by Bidder |  |
| 4 | Operator Thin Clients |  |  |  |
| 4.1 | No of CPU units | pcs | ≥ 2 |  |
| 4.2 | Manufacturer | - | To be provided by Bidder |  |
| 4.3 | Product/Model/Type | Yes/No | Yes |  |
| 4.4 | Communication capabilities - Ethernet | Yes/No | Yes |  |
| 4.5 | 19-inch rack type | Yes/No | Yes |  |
| 4.6 | 100% operational availability per thin client | Yes/No | Yes |  |
| 4.7 | 19-inch (minimum)TFT LCD monitors | Pcs | 6 (3 per thin client) |  |
| 4.8 | 40-inch (minimum)TFT LCD monitors | Pcs | 2 (1 per thin client) |  |
| 4.9 | Monitor Manufacturer | - | To be provided by Bidder |  |
| 4.10 | Monitor Product/Model/Type | Yes/No | Yes |  |
| 4.11 | Monitor Communication capabilities, HDMI, DisplayPort, VGA | Yes/No | Yes |  |
| 4.12 | Number of keyboards and mouse sets | pcs | 2 |  |
| 4.13 | Keyboard and mouse Manufacturer | - | To be provided by Bidder |  |
| 4.14 | Keyboard and mouse Product/Model/Type | Yes/No | Yes |  |
| 4.15 | Keyboard and mouse product data sheet and manual | Yes/No | Yes |  |
| 4.16 | Keyboard video and mouse (KVM) extenders per thin client | pcs | 4 (2 per thin client) |  |
| 5 | CMS Web Server |  |  |  |
| 5.1 | On-site web-server for access to remote web-clients | Yes/No | Yes |  |
| 5.2 | Number of web-client licences for remote monitoring (concurrent access) | - | 20 |  |
| 6 | Ethernet Network switches |  |  |  |
| 6.1 | No. in Server room (installed in 19” cabinet, rack mount) | pcs | 2 (dual redundant) |  |
| 6.2 | No. in Inverter Stations and switchgear rooms (installed in CMS panels, DIN mount) | pcs | 10 (1 per location) |  |
| 6.3 | Switch Manufacturer | - | To be provided by Bidder |  |
| 6.4 | Product/Model/Type | - | To be provided by Bidder |  |
| 6.5 | Product data sheet and manual | - | To be provided by Bidder |  |
| 6.6 | Optical fibre and Ethernet ports | Yes/No | Yes |  |
| 6.7 | Managed type with online management and configuration via the thin clients using a network management software installed on the CMS servers. | Yes/No | Yes |  |
| 6.8 | Compatibility with Simple network management protocol version 3 (SNMP v3) and Internet protocol version 6 (IPv6). | Yes/No | Yes |  |
| 6.9 | Online monitoring of the port connections, communication link status, bandwidth, and device heath status indicating alarms and faults to the server and remote users. | Yes/No | Yes |  |
| 6.10 | Power supply from dual redundant power sources (230 Vac or 24 Vdc) | Yes/No | Yes |  |
| 6.11 | Dual power input ports | Yes/No | Yes |  |
| 6.12 | Optical fibre and Ethernet ports | Yes/No | Yes |  |
| 6.13 | 10% unused ports (rounded up) | Yes/No | Yes |  |
| 6.14 | Wide operating temperature range (typically between -40C to +75C) | Yes/No | Yes |  |
| 6.15 | Auto negotiation capability | Yes/No | Yes |  |
| 6.16 | Auto crossover (MDIX) capability | Yes/No | Yes |  |
| 6.17 | Full duplex communication capability | Yes/No | Yes |  |
| 6.18 | Single fault tolerant, backbone CMS network | Yes/No | Yes |  |
| 6.19 | Network topology (Ring, Star) with single fault tolerance | - | Ring with Redundancy Manager |  |
| 7 | Network Time Synchronisation |  |  |  |
| 7.1 | 19” time server unit installed in server room | Yes/No | Yes |  |
| 7.2 | GPS antenna | Yes/No | Yes |  |
| 7.3 | NTP synchronisation via Ethernet | Yes/No | Yes |  |
| 7.4 | Time stamping accuracy (UTC+2) | ms | 10 |  |
| 7.5 | Automatic self-calibrating function | Yes/No | Yes |  |
| 7.6 | Power source (UPS) | V | 230 |  |
| 7.7 | On-board display and function keys | Yes/No | Yes |  |
| 8 | CMS Field Equipment Panels |  |  |  |
| 8.1 | Wall mounted | Yes/No | Yes |  |
| 8.2 | Protection class (indoor) | IP | 54 |  |
| 8.3 | Protection class for string combiner boxes and weather stations (outdoor) | IP | 65 |  |
| 8.4 | Open/Close door sensor | Yes/No | Yes |  |
| 8.5 | Internal ambient temperature sensor | Yes/No | Yes |  |
| 8.6 | Power source (100% availability) | V | 230 |  |
| 9 | Server Room Network cabinets |  |  |  |
| 9.1 | 19” rack type, 42U height | Yes/No | Yes |  |
| 9.2 | Network and power cabling, bottom entry | Yes/No | Yes |  |
| 9.3 | Use of grommets at cable entries | Yes/No | Yes |  |
| 9.4 | Internal cable channels for routing of cables | Yes/No | Yes |  |
| 9.5 | Removable blanking panels | Yes/No | Yes |  |
| 9.6 | Perforated front and rear panels | Yes/No | Yes |  |
| 9.7 | Perforated side panels | Yes/No | Yes |  |
| 9.8 | Removable front and rear doors | Yes/No | Yes |  |
| 9.9 | Open/close door sensors | Yes/No | Yes |  |
| 9.10 | Internal lighting | Yes/No | Yes |  |
| 9.11 | Internal ambient temperature sensor | Yes/No | Yes |  |
| 9.12 | Supplied general arrangement (GA) drawings of server room network panels | Yes/No | Yes |  |
| 10 | Fire Detection System |  |  |  |
| 10.1 | No. of fire panels (depending on communication medium limits per zone) | pcs | To be provided by Bidder |  |
| 10.2 | Protection class (indoor installation) | IP | 54 |  |
| 10.3 | SANS 10139 compliance | Yes/No | Yes |  |
| 10.4 | Product datasheet of fire panels | Yes/No | Yes |  |
| 10.5 | Smoke/Heat sensors make and model | - | To be provided by Bidder |  |
| 10.6 | Sensor and alarming products datasheet | Yes/No | Yes |  |
| 10.7 | Real time monitoring at PV control room via operator HMI | Yes/No | Yes |  |
| 11 | CMS Power Supply |  |  |  |
| 11.1 | Dual- redundantly configured, online UPS system with seal-type battery backup, and back-up time of 1 hour per UPS unit | Yes/No | Yes |  |
| 11.2 | Sealed type nickel cadmium or lithium-ion batteries | Yes/No | Yes |  |
| 11.3 | CMS field panels to be supplied from 230V AC supply. | Yes/No | Yes |  |
| 12 | CMS Interfaces |  |  |  |
| 12.1 | Meteorological systems (weather station, instruments), Modbus RS485 | Yes/No | Yes |  |
| 12.2 | String combiner boxes, Modbus RS485 | Yes/No | Yes |  |
| 12.3 | Central inverters, Modbus RS485 or TCP | Yes/No | Yes |  |
| 12.4 | Switchgear MCCBs, Modbus RS485 or TCP, 24V potential free | Yes/No | Yes |  |
| 12.5 | MV and LV Transformers, Modbus RS485, 4-20mA. | Yes/No | Yes |  |
| 12.6 | Energy meters, Modbus RS485 or TCP | Yes/No | Yes |  |
| 12.7 | Switchgear electrical protection relays, Modbus RS485 or TCP | Yes/No | Yes |  |
| 12.8 | Electrical battery tripping units (BTU) | Yes/No | Yes |  |
| 12.9 | CMS uninterruptable power supply (UPS) units | Yes/No | Yes |  |
| 12.10 | Internal environmental sensors of equipment panels, network cabinets, Inverter Power Stations, | Yes/No | Yes |  |
| 12.11 | Balance of plant (BoP) potable water and sewage tank levels | Yes/No | Yes |  |
| 12.12 | Fire detection system | Yes/No | Yes |  |
| 12.13 | Heating, ventilation and air-conditioning (HVAC) system | Yes/No | Yes |  |
| 12.14 | Interface to Eskom IT network. OPC DA | Yes/No | Yes |  |
| 12.15 | Firewalled connectivity to internet for full remote monitoring functionality of the PV plant | Yes/No | Yes |  |
| 12.16 | The Bidder to provide internet service provider (ISP) via ADSL or 3G for use on the plant during the installation and O&M period. | Yes/No | Yes |  |
| 12.17 | Provision of an Eskom approved gateway for future interface to the NSP using the DNP3 protocol. | Yes/No | Yes |  |
| 12.18 | CMS MODBUS interface to Power station EOD control system | Yes/No | Yes |  |
| 12.19 | A3 colour printer connected to CMS network | Yes/No | Yes |  |
| 13 | Data Communication Medium |  |  |  |
| 13.1 | Cat6 shielded twisted pair (STP) | Yes/No | Yes |  |
| 13.2 | Single mode optical fibre > 2kM | Yes/No | Yes |  |
| 13.3 | Multi-mode optical fibre < 2kM | Yes/No | Yes |  |
| 13.4 | Wireless / Bluetooth communication | Yes/No | No |  |

## Civil, Structural And Infrastructure Works

### Civil, Structural and Infrastructure Criteria

Table C-22:  Civil, structural and infrastructure criteria

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Work Methodology |  |  |  |
| 1.1 | Technical proposal detailing the work methodology, which complies to the full scope and describes how the scope will be executed (both design and construction phases of the project). Technical proposal must demonstrate understanding of the scope and include the following as a minimum: - Proposed plant, equipment and tools - Methodology for the proposed works - Foreseen risks and concerns - Health and safety requirements - Quality management requirements - Required temporary works (if any) | - | To be provided by Bidder |  |

### Technical Schedules

Table C-23: Civil & Structural Compliance to Functional Specification

| Item No. | Description | Unit |  | Required | Response from Bidder |
| --- | --- | --- | --- | --- | --- |
| 1 | Geotechnical Investigation |  |  |  |  |
| 1.1 | Detailed geotechnical investigation to be carried out by the Bidder | Yes/No |  | Yes |  |
| 2 | Foundation for Mounting Structure |  |  |  |  |
| 2.1 | Foundation type | - |  | To be provided by Bidder |  |
| 2.2 | Foundation design applicable to Environmental Permit and Water Use license permit | Yes/ No |  | Yes |  |
| 3 | Hydrological Impact Assessment |  |  |  |  |
| 3.1 | Detailed hydrological impact assessment to be carried out by the Bidder |  | Yes/ No | Yes |  |
| 4 | Topographical survey |  |  |  |  |
| 4.1 | Detailed topographical survey to be carried out by the Bidder |  | Yes/No | Yes |  |
| 5 | Supportive Documents |  |  |  |  |
| 5.1 | Indicative Plant Layout drawing, including roads, fence, O&M building, Laydown area, MV/LV inverters, substation buildings and yards. |  | Yes/No | Yes |  |
| 6 | Coal ash waste resource |  |  |  |  |
| 6.1 | Ash waste resource to be incorporated into the civil and structural designs as per 10.11.3 of the Employer’s Requirements [375-172742] |  | Yes/No | Bidder to specify |  |
| 6.2 | Additional information to be provided in relation to 6.1 |  | Yes | Yes |  |

## Balance Of Plant

Table C-24: General information about the Subcontractor (if applicable)

| No. | Item | Details |  |
| --- | --- | --- | --- |
| 1 | Name of subcontractor |  |  |
| 2 | Home office address |  |  |
| 3 | Regional office address |  |  |
| 4 | Telephone / email address |  |  |
| 5 | Name, Position and Title of contact person |  |  |
| 6 | Legal form |  |  |
| 7 | Area of main business |  |  |
| 8 | No. of staff in main business | Technical: | Others: |
| 9 | PSiRA registration number |  |  |

### Fire Protection

Table C-25: Fire protection Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Fire protection system design |  |  |  |
| 1.1 | The Bidder shall submit a Fire Protection Services design philosophy, covering aspects such as the fire protection/detection assessment, system and component description, system sizing approach, system design and construction codes, and system process (diagram). | Yes/no | Yes |  |

### Water Supply and Reticulation

Table C-26: Water Supply and Reticulation Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Potable and Process Water Supply and Reticulation System |  |  |  |
| 1.1 | The Bidder submits a Potable and Process Water Supply and Reticulation Design Philosophy Report. The report shall include system and component descriptions, system sizing approach, applicable system design and construction codes, treatment of water for cleaning PV modules, monitoring mechanisms, etc. | Yes/No | Yes |  |

### Heating, Ventilation and Air Conditioning (HVAC)

Table C-27: HVAC Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | HVAC system design |  |  |  |
| 1.1 | The Bidder submits a HVAC Services Design Philosophy Report. The report shall include system and component descriptions, system sizing approach, applicable system design and construction codes, etc., thereby documenting the design philosophy for: - O&M Control room - O&M Server Room - Offices - O&M Spare Parts Workshop - O&M Ablutions and locker rooms - Inverter stations - Substations | Yes/No | Yes |  |

### Monitoring And Meteorological Equipment and Instrumentation

Table C-28: Monitoring and Meteorological Equipment and Instrumentation Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | General |  |  |  |
| 1.1 | No. of meteorological stations | - | ≥ 4 |  |
| 2 | Meteorological Station Equipment and Instrumentation |  |  |  |
| 2.1 | Irradiance |  |  |  |
| 2.1.1 | No. of Pyranometer installed at Horizontal plane to measure GHI | pcs | ≥ 2 |  |
| 2.1.2 | No. of Pyranometer installed at POA to measure POA irradiance | pcs | ≥ 2 |  |
| 2.1.3 | No. of albedometers for bifacial modules: No. horizontally mounted albedometer installed away from the solar array in an unobstructed area OR No. of in-plane rear-side irradiance albedometers | pcs | ≥ 2 ≥ 6 |  |
| 2.1.4 | Product type | - | To be provided by Bidder |  |
| 2.1.5 | Class (according to ISO 9060) | - | Second |  |
| 2.1.6 | Measurement uncertainty | % | ≤ 2% |  |
| 2.1.7 | Product data sheet | Yes/No | Yes |  |
| 2.1.8 | Calibration certificate | Yes/No | Yes |  |
| 2.2 | PV Array Temperature Measurement |  |  |  |
| 2.2.1 | No. of temperature sensors | pcs | ≥ 6 |  |
| 2.2.2 | Manufacturer | - | To be provided by Bidder |  |
| 2.2.3 | Product/Model/Type | Yes/No | Yes |  |
| 2.2.4 | Product data sheet | Yes/No | Yes |  |
| 2.2.5 | Measurement accuracy | °C | ±1 |  |
| 2.2.6 | According to IEC 61724-1 or equivalent | Yes/No | Yes |  |
| 2.2.7 | Temperature range | °C | -40 to 100°C |  |
| 2.3 | Ambient temperature measurement |  |  |  |
| 2.3.1 | No. of temperature sensors | pcs | ≥ 2 |  |
| 2.3.2 | Manufacturer | - | To be provided by Bidder |  |
| 2.3.3 | Product/Model/Type | Yes/No | Yes |  |
| 2.3.4 | Product data sheet | Yes/No | Yes |  |
| 2.3.5 | Measurement accuracy | ±°C | 1 |  |
| 2.3.6 | According to IEC 62724-1 or equivalent | Yes/No | Yes |  |
| 2.4 | Soiling |  |  |  |
| 2.4.1 | No. of soiling measurement instruments | pcs | ≥ 2 |  |
| 2.4.2 | Manufacturer | - | To be provided by Bidder |  |
| 2.4.3 | Product/Model/Type | Yes/No | Yes |  |
| 2.4.4 | Product data sheet | Yes/No | Yes |  |
| 2.4.5 | Calibration according to IEC 61724-1 Photovoltaic system performance. | Yes/No | Yes |  |
| 2.4.7 | Uncertainty of measurement | % | ≤ 3% |  |
| 2.4.8 | Calibration certificate | Yes/No | Yes |  |
| 2.5 | Wind speed and Wind direction measurement |  |  |  |
| 2.5.1 | No of Anemometer | pcs | ≥ 2 |  |
| 2.5.2 | Manufacturer/Product type | - | To be provided by Bidder |  |
| 2.5.3 | Product data sheet | Yes/No | Yes |  |
| 2.5.4 | Anemometer suitable of wind energy applications | Yes/No | Yes |  |
| 2.5.5 | Operational Temperature | °C | -20 to 70 |  |
| 2.5.6 | Speed Range | m/s | 0 to 70 |  |
| 2.5.7 | Wind direction accuracy | ° | ± 5° |  |
| 2.6 | Rainfall gauge |  |  |  |
| 2.6.1 | No. of rain gauge | pcs | ≥ 2 |  |
| 2.6.2 | Manufacturer/Product type | - | To be provided by Bidder |  |
| 2.6.3 | Product data sheet | Yes/No | Yes |  |
| 2.7 | Moisture Meter – Relative Humidity Measurement |  |  |  |
| 2.7.1 | No. of moisture meter | pcs | ≥1 |  |
| 2.7.2 | Manufacturer/Product type | - | To be provided by Bidder |  |
| 2.7.3 | Product data sheet | Yes/No | Yes |  |
| 2.7.4 | Range | % RH | 0 - 100 |  |
| 2.7.5 | Overall Accuracy | % | ± 2 % |  |
| 2.7.6 | Response Time | s | 20 s (T90) or less |  |

### Sewage and Waste Disposal Services

Table C-29: Sewage and Waste Disposal Services Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Sewage and Waste Disposal System |  |  |  |
| 1.1 | The Bidder submits a Sewage and Waste Disposal Design Philosophy Report. The report shall include system and component descriptions, system sizing approach, applicable system design and construction codes, monitoring mechanisms, etc. | Yes/No | Yes |  |

## Operation And Maintenance

### Operation And Maintenance Plan

Table C-30: Operations and Maintenance Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Operations and Maintenance Plan |  |  |  |
| 1.1 | The Bidder shall submit a preliminary (high-level) operations and maintenance plan/approach, providing a general overview for operations and preventative maintenance of the main components. | Yes/No | Yes |  |
| 1.2 | The Bidder shall submit a preliminary corrective maintenance approach, including envisaged response and repair times for the main components. | Yes/No | Yes |  |

### Operation And Maintenance Training

Table C-31: Training Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Training Plan |  |  |  |
| 1.1 | The Bidder shall submit a preliminary training plan. The plan shall describe the timing, type, and level of detail for the various training interventions, including O&M, Inverter, SCADA/CMS, etc. | Yes/No | Yes |  |

### Spare Parts

Table C-32: Spare parts Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Spare parts |  |  |  |
| 1.1 | The Bidder submits a letter confirming Bidder acceptance of spare parts minimum requirements as per 559-189375010, Installation of Solar PV Plant at Tutuka Power Station Functional Specification. The Bidder highlights any proposed deviations and additions. | Yes/No | Yes |  |

## Grid Connection Works

- It is a requirement that the Engineering Design be performed under the self-build agreement by the Contractor, be performed by a consulting engineer accredited by Eskom for Substations, Control Plant and HV lines. The same consultant shall also design the Solar Substation as both the Solar Substation and the Eskom Switching Station will share a common platform and adjacent earth mats. Details of the Consulting Engineer to be provided in Table C-33.

- It is a requirement that the construction works performed under the self-build agreement be performed by a contractor accredited by Eskom for Substations, Control Plant, and HV lines. Details of the HV Subcontractor to be provided in Table C-34.

Table C-33: General information about the Consulting Engineer

| No. | Item | Details |  |
| --- | --- | --- | --- |
| 1 | Name of Consulting Engineer |  |  |
| 2 | Home office address |  |  |
| 3 | Regional office address |  |  |
| 4 | Telephone / email address |  |  |
| 5 | Name, Position and Title of contact person |  |  |
| 6 | Legal form |  |  |
| 7 | Area of main business |  |  |
| 8 | Signed letter of intent between Consulting Engineer and EPC Bidder | To be provided by Bidder |  |
| 9 | Proof that the Consulting Engineer is accredited by Eskom | To be provided by Bidder |  |

Table C-34: General information about the HV Subcontractor

| No. | Item | Details |  |
| --- | --- | --- | --- |
| 1 | Name of HV Subcontractor |  |  |
| 2 | Home office address |  |  |
| 3 | Regional office address |  |  |
| 4 | Telephone / email address |  |  |
| 5 | Name, Position and Title of contact person |  |  |
| 6 | Legal form |  |  |
| 7 | Area of main business |  |  |
| 10 | Signed letter of intent between HV Subcontractor and EPC Bidder | To be provided by Bidder |  |
| 11 | Proof that the HV Subcontractor is Eskom approved | To be provided by Bidder |  |

### Grid connection schedules

#### MV Cables

Table C-35: MV Cable Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Cables |  |  |  |
| 1.1 | Cable type |  | Yes |  |
| 1.2 | Cable length | m | Yes |  |

#### Grid Connection and HV/MV Transformer Schedule

Table C-36: Grid connection Schedules

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Overhead line (OHL) |  |  |  |
| 1.1 | Provide documented evidence (data sheet or other) for the OHL phase conductor | Yes/No | Yes |  |
| 2 | HV/MV Transformer |  |  |  |
| 2.1 | Product Information |  |  |  |
| 2.1.1 | Transformer manufacturer | Specify | To be provided by Bidder |  |
| 2.2 | General Requirements |  |  |  |
| 2.2.1 | No of Transformers | No. | ≥2 |  |
| 2.2.2 | Nominal rating | MVA | To be provided by Bidder |  |
| 2.2.3 | Primary Voltage | kV | 33 |  |
| 2.2.4 | Secondary Voltage | kV | 132 |  |
| 2.2.5 | Rated Frequency | Hz | 50 |  |
| 2.2.6 | Maximum Flux density | T | 1.7 |  |
| 2.2.7 | Tap-Changer Type | Specify | On-load |  |
| 2.2.8 | Diverter Type | Specify | Vacuum |  |
| 2.2.9 | Transformer insulating medium | Type | Biodegradable oil |  |
| 2.2.10 | No-load Losses | W | To be provided by Bidder |  |
| 2.2.11 | Load losses | W | To be provided by Bidder |  |
| 2.3 | General Design Conditions |  |  |  |
| 2.3.1 | Altitude above sea-level | m | 1800 |  |
| 2.3.2 | Ambient air temperatures: Maximum Monthly Average Yearly Average Minimum | ºC | 38 31 25 -8 |  |
| 2.3.3 | Amount by which the temperature rise limits are reduced according to IEC60076-2 | ºC | 5 |  |
| 2.3.4 | Additional amount by which the temperature rise limit is reduced above the values stipulated in IEC60076-2, as per additional safety margin | ºC | 5 |  |
| 2.3.5 | Total amount by which the temperature rise limit is reduced | ºC | 5 + 5 = 10 |  |
| 2.3.6 | Humidity | % | 61.5 |  |
| 2.3.7 | Solar radiation | kW/m2 | 2.5 |  |
| 2.3.8 | Atmospheric UV radiation | High/Low | High |  |
| 2.3.9 | Pollution (Insulators) | IEC 60815 Table 1 | IV- Very Heavy |  |
| 2.3.10 | Seismic | IEC60068-3-3 | Yes, Mining activity, according to IEC 60076 requirements |  |
| 2.4 | Transformer Design Review |  |  |  |
| 2.4.1 | The bidder shall make commercial allowance for appointment of a 3rd party power transformer specialist to form part of the technical design reviews and factory acceptance tests. | Yes/No | Yes |  |
| 2.5 | Minimum required specifications |  |  |  |
| 2.5.1 | As per Eskom Specification 240-68973110 – Specification for Power Transformers rated for 1.25 MVA and above and highest voltage of 2.2 kV or above and Eskom Standard 240-56227520 Large Power Generator Transformers in Power Stations for transformers rating above 2.5 MVA and winding operating at or above 11kV. | Yes/No | Yes |  |
| 2.6 | Monitoring system requirements |  |  |  |
| 2.6.1 | Continuous data logging to the CMS system for the transformer performance parameters including events and status. | Yes/No | Yes |  |
| 2.6.2 | On-line gas analyser with alarming and status monitoring in the Control Room | Yes/No | Yes |  |
| 2.6.3 | On-line Tap-changer monitoring | Yes/No | Yes |  |
| 2.7 | Supportive Documents |  |  |  |
| 2.7.1 | Transformer Datasheet | - | To be provided by Bidder |  |
| 2.8 | Additional Information – To be listed by the Bidder |  |  |  |
| 2.8.1 | To be defined by the Bidder | - | To be provided by Bidder |  |

#### MV Primary Switchgear

Table C-37: MV Primary Switchgear Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Product Information |  |  |  |
| 1.1 | Switchgear manufacturer | Name | To be provided by Bidder |  |
| 1.2 | Type/Model | Type | To be provided by Bidder |  |
| 2 | Ratings |  |  |  |
| 2.1 | Nominal voltage | kVrms | To be provided by the Bidder |  |
| 2.2 | Rated voltage | kVrms | To be provided by the Bidder |  |
| 2.3 | System frequency | Hz | 50 |  |
| 3 | Design |  |  |  |
| 3.1 | Indoor/Outdoor application | - | Indoor |  |
| 3.2 | Insulating medium | - | AIS |  |
| 3.3 | Type | Withdrawable or Fixed patter | To be provided by the Bidder |  |
| 3.4 | Interrupting technology | - | Vacuum |  |
| 4 | Supportive Documentation |  |  |  |
| 4.1 | Switchgear data sheet / catalogue | - | To be provided by the Bidder |  |
| 5 | Minimum required standards |  |  |  |
| 5.1 | • 559-189375010 Installation of Solar PV Plant at Tutuka Power Station Functional Specification • Appendix C: Tender Returnable Technical Schedules | Yes/No | Yes |  |
| 6 | Additional Information – To be listed by the Bidder |  |  |  |
| 6.1 | To be defined by the Bidder | Yes/No | Yes |  |

#### HV Primary Switchgear

Table C-38: HV Primary Switchgear Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Product Information |  |  |  |
| 1.1 | Switchgear manufacturer | Name | To be provided by the Bidder |  |
| 1.2 | Type/Model | Type | To be provided by the Bidder |  |
| 2 | Ratings |  |  |  |
| 2.1 | Nominal voltage | kVrms | 132 |  |
| 2.2 | Rated voltage | kVrms | To be provided by the Bidder |  |
| 2.3 | System frequency | Hz | 50 |  |
| 3 | Design |  |  |  |
| 3.1 | Indoor/Outdoor application | - | Outdoor |  |
| 3.2 | Insulating medium | - | To be provided by the Bidder |  |
| 3.3 | Type | - | To be provided by the Bidder |  |
| 3.4 | Interrupting technology |  | To be provided by the Bidder |  |
| 4 | Supportive Documentation |  |  |  |
| 4.1 | Switchgear data sheet / catalogue | - | To be provided by the Bidder |  |
| 5 | Minimum required standards |  |  |  |
| 5.1 | • 559-189375010 Installation of Solar PV Plant at Tutuka Power Station Functional Specification • Appendix C: Tender Returnable Technical Schedules | - | Yes |  |
| 6 | Additional Information – To be listed by the Bidder |  |  |  |
| 6.1 | To be defined by the Bidder | Yes/No | Yes |  |

#### MV Primary Switchgear Protection

Table C-39: MV Primary Switchgear Protection Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Product Information |  |  |  |
| 1.1 | Protection relay manufacturers | Name | To be provided by the Bidder |  |
| 1.2 | Type/Models/Scheme Designation | Type | To be provided by the Bidder |  |
| 2 | Ratings |  |  |  |
| 2.1 | Scheme voltage | kVrms | To be provided by the Bidder |  |
| 3 | Design |  |  |  |
| 3.1 | Provide interlocking methodologies | - | To be provided by the Bidder |  |
| 3.2 | Provide proposed protection block diagram MV feeders, transformer bay | - | To be provided by the Bidder |  |
| 3.3 | Description of MV protection and control IED’s | - | To be provided by the Bidder |  |
| 3.4 | Details of MV protection schemes for incoming circuits and transformer feeders | - | To be provided by the Bidder |  |
| 3.5 | Software communication to remote engineering device | - | Yes |  |
| 3.6 | Disturbance recording ability | - | Yes |  |
| 4 | Supportive Documentation |  |  |  |
| 4.1 | Protection Systems data sheets, catalogues, product brochures, background literature | - | To be provided by the Bidder |  |
| 5 | Minimum required standards |  |  |  |
| 5.1 | • 559-189375010 Installation of Solar PV Plant at Tutuka Power Station Functional Specification • Appendix C: Tender Returnable Technical Schedules |  | Yes |  |
| 6 | Additional Information – To be listed by the Bidder |  |  |  |
| 6.1 | To be defined by the Bidder | Yes/No | Yes |  |

#### HV Primary Switchgear Protection

Table C-40: HV Primary Switchgear Protection Schedule

| Item No. | Description | Unit | Required | Response from Bidder |
| --- | --- | --- | --- | --- |
| 1 | Product Information |  |  |  |
| 1.1 | Protection relay manufacturers | Name | To be provided by the Bidder |  |
| 1.2 | Type/Models/Scheme Designation | Type | To be provided by the Bidder |  |
| 2 | Ratings |  |  |  |
| 2.1 | Scheme voltage | kVrms | To be provided by the Bidder |  |
| 3 | Design |  |  |  |
| 3.1 | Provide interlocking methodologies applied | - | To be provided by the Bidder |  |
| 3.2 | Provide proposed protection block diagram HV feeders, transformer bay | - | To be provided by the Bidder |  |
| 3.3 | Description of HV protection and control IED’s | - | To be provided by the Bidder |  |
| 3.4 | Details of HV protection schemes for incoming circuits and transformer feeders including details of interfacing to existing systems | - | To be provided by the Bidder |  |
| 3.5 | Description of overall HV switchboard control systems and interfacing to existing systems | - | To be provided by the Bidder |  |
| 3.6 | Details of power supply for control voltages and protection systems supplies | - | To be provided by the Bidder |  |
| 3.7 | Software communication to remote engineering device | - | Yes |  |
| 3.8 | Disturbance recording ability | - | Yes |  |
| 4 | Supportive Documentation |  |  |  |
| 4.1 | Protection Systems data sheets, catalogues, product brochures, background literature | - | To be provided by the Bidder |  |
| 5 | Minimum required standards |  |  |  |
| 5.1 | • 559-189375010 Installation of Solar PV Plant at Tutuka Power Station Functional Specification • Appendix C: Tender Returnable Technical Schedules | Yes/No | Yes |  |
| 6 | Additional Information – To be listed by the Bidder |  |  |  |
| 6.1 | To be defined by the Bidder | Yes/No | Yes |  |

-End-

e.g., company, partnership, cooperation, consortium, joint venture, etc.

The Bidder provides the information requested in Item No. 2 for all the Solar PV projects indicated in Item No. 1 as the Bidder’s claimed experience.

e.g., company, partnership, cooperation, consortium, joint venture, etc.

The Bidder provides the information requested in Item No. 2 for all the Solar PV projects indicated in Item No. 1 as the Bidder’s claimed experience.

e.g., company, partnership, cooperation, consortium, joint venture, etc.

e.g., company, partnership, cooperation, consortium, joint venture, etc.

e.g., company, partnership, cooperation, consortium, joint venture, etc.