# AIR TRAFFIC AND NAVIGATION SERVICES SOC. LTD

REPUBLIC OF SOUTH AFRICA

APPOINTMENT OF A SERVICE PROVIDER TO SUPPLY, DELIVER, INSTALL AND COMMISSION WAM EXPANSION PROJECT SHELTERS AND CIVIL WORKS IN THE SOUTHERN REGION OF THE COUNTRY

REQUEST FOR PROPOSAL:

VOLUME 2,3 and 4

JULY 2023

The information contained within this document is confidential to ATNS in all respects and it is hereby acknowledged that the information as provided shall only be used for the preparation of a response to this document.  The information furnished will not be used for any other purpose than stated and that the information will not directly or indirectly, by agent, employee or representative, be disclosed either in whole or in part, to any other third party without the express written consent by the Company or its representative.

# TABLE OF CONTENTS

Table of Contents

INTRODUCTION4

Document Structure5

RESPONSE TO THIS DOCUMENT6

TECHNICAL SPECIFICATIONS7

1.1 General Requirements7

1.2 WAM Shelter Requirements8

2.1 Civil Works Specification..14

PROJECT MANAGEMENT & INTERGRATED LOGISITICS 17

APPENDIX 1: WAM EXPANSION SITES19

# ABBREVIATIONS

| ANSP | Air Navigation Service Provider |
| --- | --- |
| ASBU | Aviation System Block Upgrades |
| ATC | Air Traffic Controller |
| ATM | Air Traffic Management |
| ATNS | Air Traffic and Navigation Services |
| ATS | Air Traffic Service |
| BC | Business Case |
| CAATS | Collaborative Advanced Air Traffic System |
| CAPEX | Capital Expenditure |
| ECSA | Engineering Council of South Africa |
| PBU | Period of Beneficiary Use |
| SAAATS | South African Air Traffic System |
| SACAA | South African Civil Aviation Authority |
| SAT | Site Acceptance Test |
| SLA | Service Level Agreement |
| EOL | End of Life |
| OEM | Original Equipment Manufacturer |
| LORA WAM | Level of Repair Analysis Wide Area Multilateration |

# INTRODUCTION

ATNS is mandated by the state to provide reliable infrastructure and service to support Air Traffic Control Services in order to meet the demands placed by the Aviation Community in terms of efficiency, safety, functionality, and quality of service.

ATNS achieves its high quality of service through the use of communication, navigation, and surveillance equipment (CNS). This infrastructure is strategically placed across country, some within the airports and some in remote areas, providing air situation display.

The CAPEX plan submitted to and approved by the Regulator and the aviation users in 2009 (WAM1 - Sur_2012_135) and 2014 (WAM2 - Sur_2012_136) identified the need for cooperative secondary surveillance Projects that will provide surveillance network services to Air Traffic Management (ATM) or Air Traffic Control (ATC) applying Multilateration and ADS-B technology. These WAM&ADS-B system coverages are targeted at the airspace where there is minimal or no radar coverage especially at lower flight levels.

Figure 1 demonstrates WAM1 (yellow shaded region) and WAM2 (red shaded region) multilateration principle with a distribution of ground stations that detect, time stamp and process target messages in order to achieve the reception of the same signal at various geographical locations.

Multilateration applications, particularly when combined with ADS-B, are expected to provide important operational improvements by addressing some of the limitations of the traditional radar surveillance system optimising the controller workload, and providing benefits in the areas of safety, capacity, efficiency and environmental impact, thus contributing to the overall CNS/ATM objectives.

This document outlines the functional and technical specification for the acquisition of 33 WAM Expansion Shelters ,Civil Works and associated ancillaries.

## Document Structure

This document is divided into four sections. The first section defines the general information and instructions for bidders, the second section, which is Chapter 1 presents the Technical Specifications (VOLUME 2), the third section, Chapter 2 presents the Project Management specifications (VOLUME 3), and the fourth section, Chapter 3 presents the Integrated Logistic Support Specifications (VOLUME 4).

# Response to this document

The Tenderer shall submit all responses, diagrams, project management documentation and drawings according to the GENERAL INFORMATION AND INSTRUCTIONS TO TENDERERS document and in the English language.

ALL RESPONSES TO THE REQUIREMENTS IN THIS DOCUMENT SHALL BE PROVIDED AS FOLLOWS:

TENDERERS SHALL RESPOND IN FULL TO EACH ITEM IN THE FORMAT PROVIDED AND REFERENCES TO DOCUMENTS AND RELEVANT INFORMATION SUPPORTING THE RESPONSES SHALL BE INDICATED IN THE SPACE PROVIDED. THIS INFORMATION WILL BE THE ONLY RESPONSE USED FOR THE EVALUATION AND ASSESSMENT.

Responses, provided in the space allowed, that are not clear or inadequate or the lack thereof shall be interpreted as “Not Compliant” even though the compliance column is declared as “Comply” and/or the Tenderer’s offer meets the requirement.  Tenderers shall ensure that each response correctly addresses the requirement stated. Responses not addressing the requirement of the specific paragraph shall be interpreted as “Not Compliant”.

Tenderers shall declare compliance to each and every paragraph of this document in the column labelled “Compliance” as follows:

C:	fully compliant 	= 2 points:

PC:	partly compliant = 1 points;

NC:	not compliant 	= 0 points.

For paragraphs marked “PC” or “NC”, Tenderer’s shall include a statement as to the nature of the variation and may additionally supply supporting information in the space provided to demonstrate how the proposal meets the needs of ATNS.

# TECHNICAL SPECIFICATIONS FOR LEBOMBO WAM MAST

# Technical Specifications

## GENERAL REQUIREMENTS

### Tenderers shall have already and successfully supplied and commissioned shelters/containers at several locations around the South Africa. Only tenders from Tenderers that can prove such success and acceptance shall be evaluated;

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Tenderers shall provide detailed proof of their shelters’ local or global deployment;

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Tenderers shall provide contact details of current customers that can be contacted. The sub-contractors shall be advised to expect enquiries.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Tenderers shall be ISO 9001 accredited;

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Bidders shall provide indicative equipment breakdown for both, WAM Shelter and Civil Works, in separate columns for each site as listed in Appendix 1.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

## WAM2 SHELTER REQUIREMENTS

### The Conventional WAM2 shelter shall be a combination of ISO reinforced and standard shelter manufactured from high quality material with a good life expectancy and low in maintenance. The shelter shall have excellent insulation properties to keep the temperature constant at all times.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Shelter Size : The Conventional/Reinforced WAM2 shelter shall have the following dimensions in size.

3m x 3m x 2.5m (LxWxH) with pitch roof. See Figure 2 below for exact intended dimensions of the required shelter.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### The Conventional/Reinforced WAM2 shelter shall have the following back view and front view dimensions, see Figure 3 below.

- Figure 1. WAM Shelter Front/Back View

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### The Conventional Standard WAM2 shelter shall be built from the following material

Base Frame and cupping (side and roof), Stainless/Steel 304, 2mm. Wall and roof panels, 50mm ISO panel (ESP), inner and outer skin 0.5mm Chromadec. Color:  frost white         See Figure 4 below for Conventional WAM2 Shelter material specification details.

- Figure 2. WAM Shelter Material Type

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### The contractor shall provide detailed specifications of the Reinforced Shelter

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### The Conventional/Reinforced WAM2 shelter shall be waterproof and all components that are exposed to the elements shall be treated to prevent corrosion. Sealant: polyurethane base UV stable, moisture curing. All items such as hinges, bolts, nuts and cable gland plates etc. shall be made from a higher grade stainless steel.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Shelter Floor : The Conventional/Reinforced WAM2 shelter floor shall be made from shutter ply wood sheeting. The underside and the edges of the wood floor shall be waterproofed with fibre glass chopped strand resin and shall be completely sealed. The floor shall be finished with a durable paint.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### Shelter Floor:  The access door shall comprise of one entrance door with dust proof seals placed on the short sides of the shelter.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### The access door shall be fitted with two hinges.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### The locking mechanism of the door shall be a three-way mechanism securing the door at the bottom, center and top.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### The door retainer shall be used to secure the door in a fully open position.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### The minimum acceptable door aperture size shall be 2.1m x 1m (height x  width)  that will ensure that there is adequate clearance to put the WAM equipment into the shelter and also allow easy access to the WAM equipment rack.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### Shelter Paint:  The shelter shall be constructed with a pre painted cold rolled baked silicone polyester sandwich panels, pre painted Chromadek, colour frost white on the inside and the outside.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### Air Conditioners:  The Conventional/Reinforced WAM2 shelter air conditioners shall be 1 x 12 000 BTU split unit air conditioners. The air conditioner shall be a window mount unit. The air conditioner shall be mounted on the side of the shelter and shall be protected by a vandal protection case. The air conditioner shall be powered from the shelter DB board.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### Cable Entry Plate: The cable entry plate shall comprise of: The cable entry plate shall be fitted to the back of the shelter and can be in the form of a Z –type entry plate. This kind of entry plate shall be weather proof. The entry plate shall be manufactured from a 2mm stainless steel plate. The bulk head RF lightning and surge protection units shall be mounted onto the plate. A weather shield shall be installed over the cable entry to protect the cables from all elements.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### The main power cable access to the shelter shall go through the shelter floor. The power cable shall be protected in galvanized metal conduit.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### The PVC truncking shall be fitted internally on the walls and on the roof to house the wiring. Truncking at a predetermined height of the floor shall be able to house wiring, plugs and switches.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### Ducting and Cable Trays All cable trays and cable ducting shall fit to the walls by means of pop rivets and unistruts

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### The design of the WAM Shelter shall allow for the RF cables to be installed inside a cable tray on the back wall. The RF cable tray shall be a galvanized wire mesh type. The requested tray dimensions shall be 300 mm (W) x 50 mm (D). All cable trays shall be secured to 40 mm (W) x 20 mm (D) support channels riveted to the wall.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### Security Fence and gate For The Renosterberg Site: The contractor shall erect a 8mX8m Palisade Fence  and associated car gate at the Renosterberg site.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### The contractor shall allow for clearing site for the width of 1,000 mm where fencing runs are to be erected including removing trees, shrubs etc. not exceeding 200mm girth, grubbing up roots and roughly levelling.

| COMPLIANCE (C/PC/NC) |  |  |
| --- | --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |  |

### Electrical System Specification: AC Distribution Box (14 way): The AC distribution box shall be mounted on the wall (At the right hand side if entering the door). The AC distribution board shall house all circuit breakers, earth leakage units and lightning surge protection units and shall be single phase. All cable entries and exits from this box shall go through a PVC cable trunking.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Internal Lights The shelter shall be fitted with two single 3 ft. fluorescent light mounted on the roof, to allow maximum lighting for the entire area.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### The shelter shall be fitted with four power outlets mounted in the trunking along the walls. Two South African 16A outlets.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### The shelter shall be fitted with a Single phase class Type 1 and 2 surge protection unit.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### WAM Shelter Earthing / Grounding System: The Earth or grounding Stud shall be installed inside the shelter under the AC distribution box above the floor and shall comprise of: A single copper earth stud connected to the site earth. All the equipment shall be earthed to this earth stud. Antenna access plates, lighting protection, etc. shall all be connected to this earth system.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### All Earth Rods – Holes shall be pre drilled 2.4m and the rod shall be enclosed in Macronite. See Figure 5 below for detailed site earthing requirements.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Connection Clamps - All Connection Clamps shall be sealed with Denso tape and Bare Copper shall buried at min depth of 300mm.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

## CIVIL WORKS SPECIFICATION

### Geotech Survey – The contractor shall provide reporting and confirmation of soil testing and ground conditions.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Site Clearance – The contractor shall be responsible for cleaning of site & rubble removal (this will be done regularly until occupation).

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Excavations: The contractor shall excavate in earth not exceeding 2m deep below natural, elevated or reduced ground level for trenches and holes.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Excavations: The contractor shall keep excavations free of water other than subterranean water.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Backfilling – The contractor shall be responsible for backfilling from excavations to trenches and holes compacted to 93% modified AASHTO density

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Backfilling: Filling under floors - Imported G5 material in 150mm thick layers under concrete slab compacted to 97% modified AASHTO density shall be supplied by the contractor.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Weed killers and Insecticides - Approved brand of anti-termite soil poison shall be applied by a Registered Pest Control company and guaranteed against termite infestation for ten years. Under floors, etc., including forming and poisoning shallow furrows against foundation walls, etc., filling in furrows and ramming

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Formwork - Formworks to soffits of solids shall be deemed to be slabs not exceeding 200mm thick from the surface unless otherwise approved by the accredited engineer. Formwork to sides of bases, pile caps, ground beams shall only be measured where it is prescribed by the engineer for design reasons.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### H.D. Bolts and Miscellaneous Metal Work - All H.D bolts, washers and nuts shall be supplied by the Contractor. Rates shall include sandblasting and galvanising all bolts and metal work to applicable specification.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Concrete - Reinforced Concrete MP2 Standard Mix shall be cast against excavated surfaces and in surface beds cast over waterproofing membrane. Reinforced Concrete 25MPa/19mm in slabs including beams shall also be used.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Concrete Size – The size of the concrete shall accommodate the housing of the WAM Conventional/Reinforced Shelter dimensions (3.0m x 3.0m x 2.5m (L x W x H)) with concrete slab dimensions of 4000mm x 4000mm (L x W).

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Test – The contractor shall be responsible for making and testing of concrete strength. The contractor shall submit the test report to the Project Manager at ATNS.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Surface treatment – The contractor shall be responsible for finishing top surfaces of concrete smoothly with a power float . The surface shall be swept and shall be left clean.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Formwork – The contractor shall be responsible for edges of slabs, risers, ends and reveals not exceeding 200mm from ground surface.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### Reinforcement Steel Bars – The contractor shall use high-tensile steel bar reinforcement to structural concrete work that include 16mm diameter bars, 12mm diameter bars as well as 6mm - 8mm Mesh.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

## PROJECT MANAGEMENT AND INTERGRATED LOGISTICS

### Engineering Certification – The Contractor shall provide appropriate and accredited certification for the concrete and structural works performed at each site.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### The submitted response shall include a draft project schedule and deployment timelines for the WAM2 Shelters and Civil Works deployment and installation (M).

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### The Bidder shall provide a proposed Work Breakdown Structure (WBS) for the project in association with the project schedule.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### The Bidder shall give details of Quality Management procedures and methods for the proposed WAM2 Shelters and Civil Works deployment and installation.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### The Bidder shall provide a draft risk management plan, the plan shall identify project related risks and provide mitigation methods.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

### The Bidder shall provide a draft Health and Safety document, the plan shall identify project related resources responsible for health and safety activities at each site. The final Health and Safety document shall be provided by the Contractor during project kick-off.

| COMPLIANCE (C/PC/NC) |  |
| --- | --- |
| [INSERT FULL RESPONSE FOR EVALUATION HERE] |  |
| [INSERT REFERENCE TO ADDITIONAL INFORMATION HERE] |  |

Appendix 1

Table 1: WAM Expansion Project Confirmed Sites

| SITE NAME | SITE OWNER | Site Co-ordinates | Shelter Required | Concrete Slab Required |
| --- | --- | --- | --- | --- |
| Nooitgedach Single GSR | TELKOM | -25.8604477778°, 27.5312947222° | YES | YES |
| Kleinfontein Single GSR | TELKOM | -26.485811°, 27.260099° | YES | YES |
| Davel Single GSR | TELKOM | -26.457384°, 29.624264° | YES | YES |
| Bethlehem | TELKOM | -28.2452154167°, 28.3008583333° | YES | YES |
| Senekal Single GSR | ESKOM | -28.2070952778°, 27.5758633333° | YES | YES |
| Kroonstad | TELKOM | -27.5986647222°, 27.2469558333° | YES | YES |
| Theinessen Single GST | TELKOM | -28.3984041667°, 26.7070302778° | YES | YES |
| Bloem Tower Single GST | ATNS | -29.095750°, 26.297970° | NO | NO |
| Bloem Telkom | TELKOM | -29.1020355556°, 26.2281283333° | YES | YES |
| Langberg Single GSR | TELKOM | -29.5909188889°, 25.4676891667° | YES | YES |
| Brandtfort Single GSR | TELKOM | -28.6944758333°, 26.4594783333° | YES | YES |
| Ladybrand Single GSR | TELKOM | -29.1613666667°, 27.3831261111° | YES | YES |
| Bullsberg Single GSR | TELKOM | -29.7171425°, 26.522945° | YES | YES |
| Vaalport Single GST | TELKOM | -27.271985°, 25.376804° | YES | YES |
| Glenred Single GSR | TELKOM | -27.8967561111°, 24.9324641667° | YES | YES |
| Douglas Single GSR | TELKOM | -29.0561358333°, 23.7749697222° | YES | YES |
| Springfontein Single GST | TELKOM | -30.282026889°, 25.6219558333° | YES | YES |
| Koffiefontein Single GST | TELKOM | -29.4035508333°, 24.995622° | YES | YES |
| Noupoort Single GSR | ESKOM | -31.3039452778°, 24.9307361111° | YES | YES |
| Renosteberg Single GSR | TELKOM | -30.4624352778°, 23.976688333° | YES | YES |
| Nelspoort Single GST | TELKOM | -32.1068613889°, 23.0328497222° | YES | YES |
| Carnavon Single GSR | ESKOM | -30.897067222°, 22.3717816667° | YES | YES |
| Koeberg | CityofCapeTown | -33.7154477778°, 18.55830972222° | YES | YES |
| Van Rhynsdorp Single GST | TELKOM | -31.754139°, 18.691369° | YES | YES |
| Sutherland Single GST | MTN | -32.422606°, 20.582561° | YES | YES |
| Simonsberg Single GSR | ATNS | -33.8627852778°, 18.9069233333° | YES | YES |
| Piketberg Single GSR | TELKOM | -32.8174413889°, 18.7352613889° | YES | YES |
| Calvinia Single GST | ESKOM | 31.6128302778°, 19.8581872222° | YES | YES |
| Matjiesfontein Single GSR | TELKOM | -33.2819441667°, 20.5064116667° | YES | YES |
| Jonaskop Single GSR | TELKOM | -34.0091263889°, 19.6718261111° | YES | YES |
| Hanskop Single GST | TELKOM | -34.10233°, 18.9665561111° | YES | YES |
| Kanonkop Single GST | Telkom | -33.825586°, 18.604919° | YES | YES |
| Napier Single GSR | Eskom | -34.5298861111°, 19.8909777778° | YES | YES |