{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["A&B Schedules","Deviation Schedule"],"not_rendered":{"external_links":2,"defined_names":3},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"A&B Schedules","index":0,"n_rows":56,"n_cols":8,"rows_kept":56,"merged":[[0,1,0,7],[1,1,1,7],[2,1,2,7],[3,1,3,7],[5,4,5,6],[6,4,6,6],[8,1,8,7],[9,1,9,7],[12,2,12,3],[13,2,13,3],[14,3,14,4],[20,3,20,4],[28,3,28,4],[31,3,31,4],[34,3,34,4],[36,3,36,4],[38,2,38,4],[39,2,39,4],[40,3,40,4],[42,3,42,4],[45,1,46,7],[48,0,48,7],[50,0,50,1],[55,2,55,3]],"flags":["formulas_cached_only"]}
[null,"Technical Schedules A and B for"]
[null,"Sulphur Hexaflouride (SF6) Gas "]
[null,"NB. UNIQUE SCHEDULES ARE TO BE COMPLETED PER SAP NUMBER LISTED BELOW "]
[null,"NB. SUPPLIERS TO CONFIRM ADHERENCE TO THE LATEST PUBLISHED REVISION OF ALL APPLICABLE ESKOM DOCUMENTS AND DRAWINGS"]
[]
[{"$nulls":3},"Sap Number","Description",null,null,"Eskom Standard"]
[]
[]
[null,"Schedule A:  Purchasers specific requirements"]
[null,"Schedule B:  Guarantees and technical particulars of equipment offered"]
[]
[null,1,null,2,null,3,4,5]
[null,"Item ","Description",null,null,"UM","Schedule A","Schedule B"]
[null,1,"Product Information"]
[null,1.1,"·","Purchasing details"]
[null,"1.1.1",null,"Eskom SAP No","Not Aplicable"]
[{"$nulls":3},"Supplier",null,null,"xxxxxxxxxx"]
[null,"1.1.2",null,"Manufacturer","Manufacturer name",null,"xxxxxxxxxx"]
[{"$nulls":3},"Manufacturer's Product Code","Specify Code",null,"xxxxxxxxxx"]
[null,"1.1.3",null,"Description","Sulphur Hexaflouride (SF6) Gas ",null,"xxxxxxxxxx"]
[null,1.2,"·","Cylinder – Type, size and marking"]
[null,"1.2.1",null,"SF6 gas cylinders type",null,"Type","Class 1 steel cylinder, seamless metallic "]
[{"$nulls":3},"The seamless metallic type gas cylinders shall be in accordance with SANS 10019",null,null,"Yes"]
[{"$nulls":3},"A ring type guard shall be supplied with each cylinder. ",null,null,"Yes"]
[{"$nulls":3},"Each cylinder shall be equipped with a one way type shutoff valve which ensures the contents may only be extracted by the user.",null,null,"Yes"]
[{"$nulls":3},"The shutoff valve outlet shall be in accordance with SANS 10019 ",null,null,"Yes"]
[null,"1.2.2",null,"SF6 cylinder capacity ",null,"kg",9]
[]
[null,1.3,null,"Gas Purity"]
[{"$nulls":3},"SF6 required purity  ","As specified in IEC 60376 standard ",null,"Yes"]
[{"$nulls":3},"SF6 purity proof","Shall be supplied in the form of a batch Certificate as well as a batch reference label attached to each and every gas cylinder.",null,"Yes"]
[null,1.4,null,"SF6 gas cylinders manufacturing and testing"]
[{"$nulls":3},"Copy of the valid test Certificate of hydrostatic testing (hydraulic burst test) from the OEM. ","Very important: Eskom shall accept cylinders that have a legible hydrostatic test date stamped on them and that gas shall be accepted in cylinders that have at the minimum 3 years remaining before next hydrostatic test due date.",null,"Yes"]
[{"$nulls":3},"Strict adherence to South African National Standard SANS 10019 standard",null,null,"Yes"]
[null,1.5,"·","Packing requirements "]
[{"$nulls":3},"Package as specified. 9 kg of gas cylinder and specified accessories. ",null,null,"Yes"]
[null,1.6,"·","Marking requirements "]
[{"$nulls":3},"The marking of SF6 gas cylinders (Class 1 category) shall be according to its contents,manufactures name and product code. Cylinder stampings shall comply with the requirements of an approved manufacturing standard according to the requirements of SANS 10019 standard ",null,null,"Yes"]
[null,2,"Documentation (to be submitted with tender)"]
[null,null,"Note:  All documentation to also be provided in electronic format."]
[null,2.1,"·","General",null,null,"Required"]
[null,"2.1.1",null,"Approved Manufacturer catalouge with user manual. The supplier shall comply to this Eskom specification, thus as part of the Technical Returnables, shall prepare and submit a written Clause-by-clause undertaking to meet Eskom requirements. ","1 Set submitted",null,"Yes"]
[null,2.2,"·","Product Acceptence Reports ",null,null,"Required"]
[null,"2.2.1",null,"Proof that the product is approved by SANS 10019 standard",null,null,"Yes"]
[]
[null,"Deviations to any of the stated requirements are to be captured on the Deviation Schedule."]
[]
[]
["SUPPLIER SIGNATURES"]
[]
[null,null,"         "]
[{"$nulls":3},"Name (Print)",null,null,"Company name"]
[]
[]
[]
[null,null,"Sign",{"$nulls":3},"Date"]

{"sheet":"Deviation Schedule","index":1,"n_rows":45,"n_cols":6,"rows_kept":45,"merged":[[0,0,0,6],[1,0,1,6],[1,7,1,13],[1,14,1,20],[1,21,1,27],[1,28,1,34],[1,35,1,41],[1,42,1,48],[1,49,1,55],[1,56,1,62],[1,63,1,69],[1,70,1,76],[1,77,1,83],[1,84,1,90],[1,91,1,97],[1,98,1,104],[1,105,1,111],[1,112,1,118],[1,119,1,125],[1,126,1,132],[1,133,1,139],[1,140,1,146],[1,147,1,153],[1,154,1,160],[1,161,1,167],[1,168,1,174],[1,175,1,181],[1,182,1,188],[1,189,1,195],[1,196,1,202],[1,203,1,209],[1,210,1,216],[1,217,1,223],[1,224,1,230],[1,231,1,237],[1,238,1,244],[1,245,1,251],[1,252,1,255],[2,0,2,6],[2,7,2,13],[2,14,2,20],[2,21,2,27],[2,28,2,34],[2,35,2,41],[2,42,2,48],[2,49,2,55],[2,56,2,62],[2,63,2,69],[2,70,2,76],[2,77,2,83],[2,84,2,90],[2,91,2,97],[2,98,2,104],[2,105,2,111],[2,112,2,118],[2,119,2,125],[2,126,2,132],[2,133,2,139],[2,140,2,146],[2,147,2,153],[2,154,2,160],[2,161,2,167],[2,168,2,174],[2,175,2,181],[2,182,2,188],[2,189,2,195],[2,196,2,202],[2,203,2,209],[2,210,2,216],[2,217,2,223],[2,224,2,230],[2,231,2,237],[2,238,2,244],[2,245,2,251],[2,252,2,255],[3,0,3,6],[4,2,4,6],[5,2,5,6],[6,2,6,6],[7,2,7,6],[8,2,8,6],[9,2,9,6],[10,2,10,6],[11,2,11,6],[12,2,12,6],[13,2,13,6],[14,2,14,6],[15,2,15,6],[16,2,16,6],[17,2,17,6],[18,2,18,6],[19,2,19,6],[20,2,20,6],[21,2,21,6],[22,2,22,6],[23,2,23,6],[24,2,24,6],[25,2,25,6],[26,2,26,6],[27,2,27,6],[28,2,28,6],[29,2,29,6],[30,2,30,6],[31,2,31,6],[32,2,32,6],[33,2,33,6],[34,2,34,6],[37,0,37,6],[39,0,39,1],[40,2,40,3],[44,2,44,3]],"flags":["formulas_cached_only"]}
["Deviation schedule"]
["Sulphur Hexaflouride (SF6) Gas "]
["SAP No:.                            (To Be Specified)"]
["Any deviations offered to this specification shall be listed below with reasons for deviation.  In addition, evidence shall be provided that the proposed deviation will at least be more cost-effective that that specified by Eskom."]
["Item","Clause","Description of Deviation"]
{"$rows_empty":32}
["SUPPLIER SIGNATURES"]
[]
[null,null,"         "]
[null,null,"Name (Print)",null,null,"Company name"]
[]
[]
[]
[null,null,"Sign",null,null,"Date"]