The following clarifications are applicable.

Question is in Blue and answers are provided in black.

| No | Clarification/ Discussion |
| --- | --- |
| CIDB Requirements: - As mentioned, the tender requires a CIDB CE Rating. However, in my experience there are very few civil companies which will have an Authorised person in their employment, this includes Civolt Project. However, companies with a CIDB level EP will have authorised persons more often as the EP grading is for Power Line Contractors. Thus, can you open the tender for CIDB EP grading companies please? | Question 1 |
| - Respondents /companies must have a contractor grading designation of 5CE or 5EP or higher | Answer/ Response to Question 1 |
| Outcome level required for the Authorised Person: - Please clarify the outcome level required for the Authorised Person? | Question 2 |
| - As per Item 1.5 of document LES1537, there should be at least one person in the employ of the supplier that has been trained, is experienced and holds a valid certificate of ORHVS authorisations level HVO 04. | Answer/ Response to Question 2 |
| ARC-off during the construction period: - Will the line be permanent on ARC-off during the construction period, or will we have to request it on a daily or weekly basis? | Question 3 |
| - A total outage must be given for working on towers where main-leg members require replacing and the tower requires to be stabilized. It is safe to replace anti-climbs without getting into the live chamber. The grid will be available to monitor the contractor and ensure the work is done safely. It should be noted that a risk assessment based of the site conditions will determine measures that need to be in place. | Answer/ Response to Question 3 |
| Bill of Quantities BOQ: - Item 5.1 change "(4 towers x 4 legs)" to "(1 tower x 4 legs)" ? | Question 4 |
| - See revised BOQ attached below: | Answer/ Response to Question 4 |
| Staking table of the line with the tower types and number: - Can you please share a staking table of the line with the tower types and number? | Question 5 |
| - See attached TxSIS data below. It shows the salient aspects of the line, including the coordinates of the structures. | Answer/ Response to Question 5 |
| Evaluation criteria: - Will the evaluation criteria be updated to include construction manager? | Question 6 |
| - With regards to Revision 1 of document LES1537 that is dated May 2022 and entitled “Engineering Tender Evaluation Returnable Form: Buffalo – Port Rex 2 132 kV line - stub corrosion refurbishment,” the description of Item 1.2 has been relaxed to be inclusive of a construction manager. As such, the description of Item 1.2 should be taken to read “Provide CV of project manager and/or construction manager with SACPCMP registration.” Please note that document LES1537 will not be revised. The evaluation team will be made aware of the relaxation. | Answer/ Response to Question 6 |

NOTES AND ATTACHMENTS: