{"text_format":"3","workbook":"xls","n_sheets":7,"sheets":["Electrical Schedule A&B","Civil Schedule A&B","Deviation from schedule","Architectural Schedule A&B","C&I Schedule A&B","Mechanical Schedule A&B","Security Schedule A&B"],"not_rendered":{"images":1,"external_links":2,"defined_names":16},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Electrical Schedule A&B","index":0,"n_rows":98,"n_cols":10,"rows_kept":98,"merged":[[1,1,3,3],[1,4,1,9],[2,5,2,9],[3,5,3,9],[4,1,4,4],[4,5,4,9],[5,2,5,4],[6,2,6,4],[7,2,7,4],[8,2,8,4],[9,2,9,4],[10,2,10,4],[12,2,12,4],[16,2,16,4],[17,2,17,4],[18,2,18,4],[22,2,22,4],[23,2,23,4],[24,2,24,4],[32,2,32,4],[33,2,33,4],[36,2,36,4],[41,2,41,4],[68,2,68,4],[69,2,69,4],[72,2,72,4],[74,2,74,4],[75,2,75,4],[76,2,76,4],[77,2,77,4],[78,2,78,4],[79,2,79,4],[80,2,80,4],[81,2,81,4],[82,2,82,4],[83,2,83,4],[84,2,84,4],[85,2,85,4],[86,2,86,4],[87,2,87,4],[89,2,89,4],[91,2,91,4],[92,2,92,4],[93,2,93,4],[94,2,94,4],[95,2,95,4],[96,2,96,4],[97,2,97,4]],"flags":["formulas_cached_only"]}
[]
[{"$nulls":4},"ERE RENOVATIONS AND REFURBISHMENT CONTRACT TECHNICAL SPECIFICATION SCHEDULE A&B"]
[{"$nulls":4},"Project Name:   ","ERE RENOVATIONS AND REFURBISHMENT FRAMEWORK CONTRACT"]
[{"$nulls":4},"Application Description:","Renovations and refurbishment of ERE Properties"]
[null,"Section",{"$nulls":3},"ESKOM REAL ESTATE"]
[null,"ITEM","DESCRIPTION",null,null,"UNITS","ESKOM","SUPPLIER","ESKOM Comments","SUPPLIER Comments"]
[null,{"v":1,"d":"1.0"},"Electrical Characteristics of LV Reticulation",{"$nulls":3},"Schedule A ","Schedule B "]
[null,{"v":1.1,"d":"1.10"},"Rated operating voltage              (Three phase Ue) ","V ",400,"V",400,"[Fill in] "]
[null,1.11,"Rated operating voltage              (Single phase Ue) ","V ",401,"V","230 (+/- 10%)","[Fill in] "]
[null,1.12,"Rated Insulation voltage              (Ui) ","V ",1000,"V",1000,"[Fill in] "]
[null,{"v":1.1300000000000001,"d":"1.13"},"Rated Frequency ","Hz ",50,"Hz ",50,"[Fill in] "]
[null,{"v":1.1400000000000001,"d":"1.14"},"Short-circuit withstand for  0.5 seconds",null,null,"kA","***","[Fill in] "]
[null,{"v":1.1500000000000001,"d":"1.15"},"Short-circuit withstand for  1.0 seconds","kA ","*** ","kA","***","[Fill in] "]
[null,{"v":1.1600000000000001,"d":"1.16"},"Number of Phases and Neutral",null,null,"Number","1 + N + E","[Fill in] "]
[null,{"v":1.1700000000000002,"d":"1.17"},"Number of Phases and Neutral "," ",null,"Number","3 + N + E","[Fill in] "]
[null,{"v":1.1800000000000002,"d":"1.18"},"System Earthing",null,null,"Type","TN - S","[Fill in] "]
[null,{"v":1.1900000000000002,"d":"1.19"},"Conditional short-circuit current (Peak) ",null,null,"kA @ Ue + 10%","***","[Fill in] "]
[null,{"v":2,"d":"2.0"},"Moulded Case Circuit Breaker/Switchgear",{"$nulls":3},"Schedule A ","Schedule B "]
[null,2.01,"Manufacturer ","Manufacturer ","Manufacturer ","Name","Specify in Schedule B","[Fill in] "]
[null,{"v":2.0199999999999996,"d":"2.02"},"Type ","Type ",null,"type","Specify in Schedule B","[Fill in] "]
[null,{"v":2.0299999999999994,"d":"2.03"},"Number of poles ","number of poles ",null,"Number",3,"[Fill in] "]
[null,{"v":2.039999999999999,"d":"2.04"},"Utilization category (IEC 60947-2) ","utilization category (IEC 60947-2) ",null,null,"A or B","[Fill in] "]
[null,{"v":2.049999999999999,"d":"2.05"},"Rated operating voltage (Ue) ","V ",400,"V",400,"[Fill in] "]
[null,{"v":2.0599999999999987,"d":"2.06"},"Rated insulation voltage (Ui) ","V ",1000,"V",1000,"[Fill in] "]
[null,{"v":2.0699999999999985,"d":"2.07"},"Rated frequency ","Hz ",50,"Hz ",50,"[Fill in] "]
[null,{"v":2.0799999999999983,"d":"2.08"},"Rated current (In)",null,null,"A","Specify in Schedule B","[Fill in] "]
[null,{"v":2.089999999999998,"d":"2.09"},"Rated duty  ",null,null,"Operations","Uninterrupted","[Fill in] "]
[null,{"v":2.099999999999998,"d":"2.10"},"Operating Times ",null,null,"cycles","Specify in Schedule B","[Fill in] "]
[null,{"v":2.1099999999999977,"d":"2.11"},"Manner of closing ",null,null,"Type","Manual or Electrical","[Fill in] "]
[null,{"v":2.1199999999999974,"d":"2.12"},"Manner of releasing energy ",{"$nulls":3},"Electrical","[Fill in] "]
[null,{"v":2.1299999999999972,"d":"2.13"},"Manual – mechanical latch ",null,null,"Yes/No","Yes","[Fill in] "]
[null,{"v":2.139999999999997,"d":"2.14"},"Auxiliary contacts (utilization category AC 14 or DC 13 to IEC 60947-5-1) ",null,null,"Yes/No","Yes","[Fill in] "]
[null,{"v":2.149999999999997,"d":"2.15"},"Overcurrent protection ",null,null,"Yes/No","Yes","[Fill in] "]
[null,{"v":2.1599999999999966,"d":"2.16"},"Earth fault protection ",null,null,"Yes/No","Yes","[Fill in] "]
[null,{"v":2.1699999999999964,"d":"2.17"},"KAIC",null,null,"Yes/No","Yes","[Fill in] "]
[null,{"v":2.179999999999996,"d":"2.18"},"Datasheet with ratings, short circuit ratings",null,null,"Yes/No","Yes","[Fill in] "]
[null,{"v":3,"d":"3.0"},"Small Power And Lighting",{"$nulls":3},"Schedule A ","Schedule B "]
[null,3.1,"Photometric Specifications"]
[null,{"v":3.1,"d":"3.10"},"Colour temperature",null,null,"K","4000 (Neutral White)","[Fill in] "]
[null,3.11,"LED luminous flux",null,null,"lm","Specify in Schedule B","[Fill in] "]
[null,{"v":3.1199999999999997,"d":"3.12"},"Luminaire Efficacy",null,null,"lm/W","≥110","[Fill in] "]
[null,{"v":3.1299999999999994,"d":"3.13"},"Time to full brightness",null,null,"minutes","< 1","[Fill in] "]
[null,{"v":3.1399999999999992,"d":"3.14"},"Light output ratio (LOR)",null,null,"%","Specify in Schedule B","[Fill in] "]
[null,{"v":3.149999999999999,"d":"3.15"},"Colour Rendering Index","Colour Rendering Index",null,"CRI","≥ 85","[Fill in] "]
[null,{"v":3.2,"d":"3.20"},"Electrical Specifications"]
[null,3.21,"Input voltage",null,null,"Vac","230 ±15%","[Fill in] "]
[null,{"v":3.2199999999999998,"d":"3.22"},"Frequency",null,null,"Hz","50 ± 5%","[Fill in] "]
[null,{"v":3.2299999999999995,"d":"3.23"},"Input current (maximum)",null,null,"mA","300-500","[Fill in] "]
[null,{"v":3.2399999999999993,"d":"3.24"},"Efficiency (total LED to total luminaire power consumption)",null,null,"%","≥ 90","[Fill in] "]
[null,{"v":3.249999999999999,"d":"3.25"},"Power factor (PF)",null,null,"%","≥ 0.95","[Fill in] "]
[null,{"v":3.259999999999999,"d":"3.26"},"Total Harmonic distortion",null,null,"%","< 20","[Fill in] "]
[null,{"v":3.2699999999999987,"d":"3.27"},"Electromagnetic Specifications",{"$nulls":3},"As specified","[Fill in] "]
[null,{"v":3.2799999999999985,"d":"3.28"},"Protection type",{"$nulls":4},"[Fill in] "]
[null,{"v":3.3000000000000003,"d":"3.30"},"Mechanical Specifications"]
[null,3.31,"Luminaire design",{"$nulls":3},"As specified","[Fill in] "]
[null,3.32,"Luminaire material and SANS 475 compliance",{"$nulls":3},"As specified","[Fill in] "]
[null,{"v":3.3299999999999996,"d":"3.33"},"Luminaire and accessories",{"$nulls":3},"As specified","[Fill in] "]
[null,{"v":3.3399999999999994,"d":"3.34"},"Reflector material",{"$nulls":3},"High-grade super pure deep anodized aluminium","[Fill in] "]
[null,{"v":3.349999999999999,"d":"3.35"},"Diffuser",{"$nulls":3},"As specified","[Fill in] "]
[null,{"v":3.359999999999999,"d":"3.36"},"LED Drivers capability",{"$nulls":3},"As specified","[Fill in] "]
[null,{"v":3.4000000000000004,"d":"3.40"},"General Specifications, Guarantee, Delivery and Maintenance Strategy"]
[null,3.41,"Operating temperature range",null,null,"°C","-10 to +60","[Fill in] "]
[null,3.42,"Operating humidity range",null,null,"%RH","10% - 70%","[Fill in] "]
[null,{"v":3.4299999999999997,"d":"3.43"},"Luminaire housing (minimum)",null,null,"years",10,"[Fill in] "]
[null,{"v":3.4399999999999995,"d":"3.44"},"Electrical components (minimum)",null,null,"hours",{"v":30000,"d":"30,000"},"[Fill in] "]
[null,{"v":3.4499999999999993,"d":"3.45"},"LED modules (minimum)",null,null,"hours",{"v":30000,"d":"30,000"},"[Fill in] "]
[null,{"v":3.459999999999999,"d":"3.46"},"Luminaire replacement in case of sub-standard performance",{"$nulls":3},"As specified","[Fill in] "]
[null,{"v":3.469999999999999,"d":"3.47"},"Maintenance strategy",{"$nulls":3},"Specify in Schedule B","[Fill in] "]
[null,{"v":3.4799999999999986,"d":"3.48"},"Enclosure Material ",null,null," Type","Mild Steel","[Fill in] "]
[null,{"v":3.4899999999999984,"d":"3.49"},"Dimension (LxWxH)",null,null,"mm/mm/mm","Specify in Schedule B","[Fill in] "]
[null,{"v":3.4999999999999982,"d":"3.50"},"Total weight",null,null,"kg","Specify in Schedule B","[Fill in] "]
[null,{"v":3.509999999999998,"d":"3.51"},"Guarantee (luminaire components, housing)",null,null,"hours, years","≥ 30000, ≥ 10","[Fill in] ","Provide proof of warranty"]
[null,{"v":3.519999999999998,"d":"3.52"},"spare parts list",null,null,"List","Specify in Schedule B","[Fill in] ","Provide spare parts list"]
[null,{"v":3.5299999999999976,"d":"3.53"},"Lead time for delivery from time of order",null,null,"Calender days ",60,"[Fill in] "]
[null,{"v":4,"d":"4.0"},"LV Cables ",{"$nulls":3},"Schedule A ","Schedule B "]
[null,4.01,"Manufacturer",null,null,"Name","Specify in Schedule B","[Fill in] "]
[null,4.02,"Cable type",null,null,"Type","Specify in Schedule B","[Fill in] "]
[null,{"v":4.029999999999999,"d":"4.03"},"Rated operating voltage (Ue) ","V ",400,"V","230/400","[Fill in] "]
[null,{"v":4.039999999999999,"d":"4.04"},"Rated cable voltage  (Uo/U) ","V ",1000,"V","600/1000","[Fill in] "]
[null,{"v":4.049999999999999,"d":"4.05"},"Rated frequency ","Hz ",50,"Hz ",50,"[Fill in] "]
[null,{"v":4.059999999999999,"d":"4.06"},"Number of cores",null,null,"Number","Specify in Schedule B","[Fill in] "]
[null,{"v":4.0699999999999985,"d":"4.07"},"Conductor size",null,null,"mm2","Specify in Schedule B","[Fill in] "]
[null,{"v":4.079999999999998,"d":"4.08"},"Rated current",null,null,"A","Specify in Schedule B","[Fill in] "]
[null,{"v":4.089999999999998,"d":"4.09"},"Short circuit current rating","Provide data sheet ","*** ","kA","Specify in Schedule B","[Fill in] "]
[null,{"v":4.099999999999998,"d":"4.10"},"Conductor material",null,null,"Cu","Specify in Schedule B","[Fill in] "]
[null,{"v":4.109999999999998,"d":"4.11"},"Serving or protection: a) For buried cable cables – Flame retardant PVC sheathed ",{"$nulls":3},"Specify in Schedule B","[Fill in] "]
[null,{"v":4.119999999999997,"d":"4.12"},"Serving or protection: b) For cables in tunnel and trenches – Low halogen PVC sheathed ",{"$nulls":3},"Specify in Schedule B","[Fill in] "]
[null,{"v":4.129999999999997,"d":"4.13"},"Serving or protection: c) For cables in open air – white stripe - PVC sheathed ",{"$nulls":3},"Specify in Schedule B","[Fill in] "]
[null,{"v":4.139999999999997,"d":"4.14"},"Water blocking ",{"$nulls":3},"Specify in Schedule B","[Fill in] "]
[null,{"v":4.149999999999997,"d":"4.15"},"Cable manufactured to Low voltage power cables standard -  (SANS 1507-3) ",null,null,"Yes/No","Yes","[Fill in] "]
[null,{"v":4.159999999999997,"d":"4.16"},"Insulation type ",null,null,"Type","PVC","[Fill in] "]
[null,{"v":4.169999999999996,"d":"4.17"},"Cable finish construction: a) For cables that require protection against mechanical damage  ",null,null,"Type","Screen and Armoured","[Fill in] "]
[null,{"v":4.179999999999996,"d":"4.18"},"Marking of cables sheaths ",null,null,"Colour","Specify in Schedule B","[Fill in] "]
[null,{"v":4.189999999999996,"d":"4.19"},"Cable glands - Armour gripping type ",{"$nulls":3},"Specify in Schedule B","[Fill in] "]
[null,{"v":4.199999999999996,"d":"4.20"},"Tinned copper cable lugs  ",{"$nulls":3},"Specify in Schedule B","[Fill in] "]
[null,{"v":4.2099999999999955,"d":"4.21"},"Type Test Reports and certificates as required in SANS 1507-3 ",null,null,"Yes/No","Yes","[Fill in] ","Provide reference number - 240 -56227443"]
[null,{"v":4.219999999999995,"d":"4.22"},"Routine Test reports and certificates generic copies as required in SANS 1507-3 ",null,null,"Yes/No","Yes","[Fill in] ","Provide reference number - 240 -56227443"]
[null,{"v":4.229999999999995,"d":"4.23"},"Cable datasheet with current ratings, impendance and mechanical parameters.",null,null,"Yes/No","Yes","[Fill in] "]

{"sheet":"Civil Schedule A&B","index":1,"n_rows":2,"n_cols":1,"rows_kept":2,"merged":[[1,0,2,1]],"flags":["formulas_cached_only"]}
[]
["None"]

{"sheet":"Deviation from schedule","index":2,"n_rows":14,"n_cols":3,"rows_kept":14,"merged":[[2,0,2,2],[4,0,4,2],[5,0,5,2],[6,0,6,2],[7,0,7,2],[8,0,8,2],[9,0,9,2],[11,0,11,2],[12,0,12,2]],"flags":["formulas_cached_only"]}
[]
[]
[" EXCLUSIONS, ADDITIONS AND DEVIATIONS"]
[]
[]
["NOTES:"]
[]
["1. Any deviations/modifications/alternatives offered to specification are listed below with reasons for the departure."]
[]
["2. No deviations/modifications/alternatives offered to the specification are recognised unless listed on this Schedule."]
[]
["3. If no deviations/modifications/alternatives are offered, this Schedule are marked N/A"]
[]
["Schedule Item no.","Item Description","Proposed deviation/ Modification/Alternative"]

{"sheet":"Architectural Schedule A&B","index":3,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"C&I Schedule A&B","index":4,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Mechanical Schedule A&B","index":5,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Security Schedule A&B","index":6,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}