| INVITATION TO QUOTE |  |
| --- | --- |
| Description; Supply and Installation of diesel and petrol dispensers for umkondeni Fuel tanks.. Advert Date; 27/06/2024. Closing Date and Time; 03/07/2024 at 15:00 pm. Contents of RFQ; - Invitation to quote - Bidders’ information - Terms and Conditions - Undertaking by Bidder - RFQ specifications - Price Schedule [SBD 3.1] - Authority to Sign - Bidders’ disclosure [SBD 4] - Preference points claim form (SBD 6.1) - Contract Form [SBD 7.1]. Compulsory/Non-Compulsory Briefing Session; N/A. SCM Enquiries; Nokwanda Mboyi Tel: 033 846 1800 Email:Nokwanda.mboyi@umgeni.co.za. Technical Enquiries; Njabulo Kheswa Tel: 033 846 1833 / 083 724 2396 Email: Njabulo.kheswa@umgeni.co.za. |
| Submissions: | Tip-Offs Anonymous Hotline: |
| All completed RFQ to be email to : scmquotes@umgeni.co.za using Quote number as the email subject | Report unethical conduct at Umgeni Water on: Toll Free Number: 0800 864 463 Email: umgeniwater@whistleblowing.co.za Toll Free Fax: 0800 212 689 Postal: Freepost KZN665, Musgrave, 4062 SMS: 33490 Online: www.whistleblowing.co.za Stop theft / fraud / dishonesty / bribery /blackmail / intimidation, and remain anonymous. |

2.BIDDERS INFORMATION

| Name of Bidder |  |
| --- | --- |
| Company Registration number |  |
| VAT registration number |  |
| Contact Person |  |
| Telephone number |  |
| Cell number |  |
| E-mail address |  |
| Postal address |  |
| Physical address |  |
| uMngeni-uThukela Water Vendor Number |  |
| CSD Supplier number |  |

I certify that the information furnished on this form is true and correct.  I further accept that, in addition to cancellation of a contract, action may be taken against me should this declaration prove to be false.

______________________	_____________		____________

Name of Representative	Signature 			Date

(Duly Authorised)

3. TERMS AND CONDITIONS OF REQUEST FOR QUOTATION (RFQ)

- Any alteration made by the bidder must be initialled.

- Use of correcting fluid is prohibited.

- Bidders must be registered on the National Treasury’s Central Suppliers Database.

- Tenderers are required to submit a valid Tax clearance verification PIN or CSD MAAA number.

- This quotation is subject to the Preferential Procurement Policy Framework Act and the Preferential Procurement Regulations, 2022; the General Conditions of Contract (GCC) and if applicable any other Special Conditions of Contract.

- The applicable preference point system for this tender is the 80/20 preference point system, Failure on the part of a tenderer to submit proof or documentation required in terms of this RFQ to claim points for specific goals, will be interpreted to mean that preference points for specific goals are not claimed by the bidder. Kindly refer to SBD 6.1 form for additional information.

- Suppliers must complete the attached SBD 4 – Bidders disclosure, failure to complete these documents may result in the quotation being invalidated.

- Quotations must be in accordance and comply with the terms of reference/specifications provided, unless otherwise stipulated.

- The official uMngeni-uThukela Water quotation form must be used to quote the offered price.  Should the allocated price page be insufficient, the tenderer may supplement the price page with an additional pricing breakdown.

- Price Declaration must be completed, and should the total RFQ prices differ, the one indicated on the price declaration shall be considered the correct price.

- The successful supplier may be required to fill in and sign a written Contract Form. (If applicable)

- This document may contain confidential information that is the property of uMngeni-uThukela Water.

- No part of the contents may be used, copied, disclosed or conveyed in whole or in part to any party in any manner whatsoever other than for preparing a proposal in response to this RFQ, without prior written permission from Umgeni Water and the Bidder.

- All Copyright and Intellectual Property herein vests with uMngeni-uThukela Water and its Bidder.

- Responses to this RFQ must be submitted by email scmquotes@umgeni.co.za or be deposited in tender box situated as indicated on the quotation request form marked appropriated as directed. (The applicable submission method is reflected on the cover page).

- It is the responsibility of the bidder to ensure that its response reaches Umgeni Water on or before the closing date and time of the RFQ. Late and incomplete submissions will not be accepted.

- No services must be rendered or goods delivered before an official uMngeni-uThukela Water Purchase Order form has been received.

- A full copy of General Conditions of Contract (GCC) are available on the National Treasury website (https://www.treasury.gov.za/divisions/ocpo/sc/generalconditions/general%20conditions%20of%20contract.pdf)

4. UNDERTAKING BY BIDDER

1.	I/We hereby quote to supply all or any of the supplies and/or to render all or any of the services described in the attached documents to uMngeni-uThukela Water on the terms and conditions. In accordance with the specifications stipulated in the quotation documents (and which shall be taken as part of and be incorporated into this quote) at the prices and on the terms regarding time for delivery and/or execution inserted therein.

2.	I/we agree that:

(a)	the offer herein shall remain binding upon me and open for acceptance by uMngeni-uThukela Water during the validity period indicated and calculated from the closing time of the quote;

(b)	this quote and its acceptance shall be subject to the Public Finance Management Act, 1999, Umgeni Water’s Supply Chain Management Policy and Procedures, the General and Special Conditions of Contract as may be applicable, with which I/we am fully acquainted;

(c)	if I/we withdraw my quote within the period for which I/we have agreed that the quote shall remain open for acceptance or fail to fulfil the contract when called upon to do so. uMngeni-uThukela Water may, without prejudice to its other rights, agree to the withdrawal of my quote or cancel the contract that may have been entered into between uMngeni-uThukela Water and I/us. I/we will then pay to Umgeni Water any additional expenses incurred for having either to accept any less favourable quote or, if fresh quote have to be invited, the additional expenditure incurred by the invitation of fresh quotes and by the subsequent acceptance of any less favourable quotes.  uMngeni-uThukela Water shall reserve the right to recover such additional expenditure by set-off against monies which may be due to me under this, or any other tender or contract or against any guarantee or deposit that may have been furnished by me or on my behalf for the due fulfilment of this or any other tender or contract. Pending the ascertainment of the amount of such additional expenditure to retain such monies, guarantee or deposit as security for any loss uMngeni-uThukela Water may sustain by reason of my default;

(d)	if my quote is accepted, the acceptance may be communicated to me by electronic mail, to the email address supplied in my quotation document;

(e)	the law of the Republic of South Africa shall govern the contract created by the acceptance of my quote and I choose domicilium citandi et executandi in the Republic at (full physical address):

__________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

3.	I/we furthermore confirm that I/we have satisfied myself as to the correctness and validity of my quote: that the price(s), rate(s) and preference quoted cover all of the work/item(s) and my obligations under a resulting contract, and I accept that any mistakes regarding the price(s) and calculations will be at my risk.

4.	I/we hereby accept full responsibility for the proper execution and fulfilment of all obligations and conditions devolving on me under this agreement, as the Principal(s) liable for the due fulfilment of this contract.

5.	I/we agree that any action arising from this contract may in all respects be instituted against me and I/we hereby undertake to satisfy fully any sentence or judgement which may be pronounced against me as a result of such action.

6.	I/we confirm that I/we have declared all and any interest that I or any persons related to my business has with regard to this quote or any related quotations by completion of the Declaration of Interest Section.

7.	I/WE, THE UNDERSIGNED, WHO WARRANT THAT I AM DULY AUTHORISED TO DO SO ON BEHALF OF THE TENDERER, CERTIFY THAT THE INFORMATION SUPPLIED IN TERMS OF THIS DOCUMENT IS CORRECT AND TRUE, THAT THE SIGNATORY TO THIS DOCUMENT IS DULY AUTHORISED AND ACKNOWLEDGE THAT:

# (1) 	The tenderer will furnish documentary proof regarding any tendering issue to the satisfaction of the uMngeni-uThukela Water, if requested to do so.

# (2) 	If the information supplied is found to be incorrect and/or false then uMngeni-uThukela Water, in addition to any remedies it may have, may: -

- Recover from the contractor all costs, losses or damages incurred or sustained by uMngeni-uThukela Water as a result of the award of the contract, and/or

- Cancel the contract and claim any damages which uMngeni-uThukela Water may suffer by having to make less favourable arrangements after such cancellation.

______________________	_____________		____________

Name of Representative	Signature 			Date

(Duly Authorise

5. SPECIFICATIONS OF GOODS REQUIRED

- Background

uMngeni-uThukela Water requires service providers to supply fuel dispensers, piping and associated electrical work to commission the installed fuel tanks at UMkondeni complex.

- Description of goods/ services required

Tanks shall be fitted with valves, meters,  filters, accumulators, pump, nozzle and any other related mechanical/electrical components that are required for functionality

  - Fitted with retail nozzle

  - Dispensing nozzles to be fitted with venture mechanism for overfill protection

  - Top port for priming of pipes

  - Overfill alarm and protection

  - Anti-syphon foot valve

  - Dipping tubes for tank

  - Venting for tank

  - Pump must be able to pump 150 litres per minute

  - Automatic tank gauges

  - lockable outlet valve

  - remote filler point

  - dip point and vents

- The contractor shall test and handover a fully functioning diesel and petrol storage and dispensing systems specified

  - Fuel management system with data logger with storage capacity of at least 30 gigabytes of flash memory, with USB connector for a laptop connection

- Labelling and signage of facility in accordance to legislation and governing standards for petrochemicals.

Electrical Installation

- The supplier shall provide power for the pumps and  any electronics or controls from the existing 220V AC @ 50Hz main

- Electrical installation with surge protection

- Design of all electrical related equipment including the tank shall be in accordance to SANS 10089-2:2017: The petroleum Industry part 2 or similar.

- The electrical distribution for below 250 V AC shall be in accordance to SANS 13297:2008

- All flow meters shall conform  to “SANS 1697: Verification standard for the verification of volume-measuring instruments, including commercial standards of volume”

- All pressure gauges shall conform to “SANS 1062:Pressure and vacuum gauges”

- Compliance with SANS 10089-1: The Petroleum Industry Part1: Storage and distribution of petroleum products in above –ground bulk installations or equivalent

- Earthing for the new tanks

- Control panels for the level indication and alarm

- New supply breaker in existing generator panels

- Cabling to the control panels, level transmitters, sirens and beacons

- Cable tray/ladder/

- Extent of the services

- Install diesel and petrol dispensing station

- Provision of all labour for installation

- Supply and installation of a smart fuel management system

- Processing pipe installation

- Technical Specifications

Pump and dispenser

Minimum Configuration of the Fuel Dispensers must be as follows:

Main board, power board, LED display board, keypad, control board, Gear pump, EX motor, flow meter, solenoid valve, electromagnetic counter , filter, nozzle, hose, sight glass.

Technical specifications:

| Accuracy for the unit | ±0.25% |
| --- | --- |
| Flow rate | 55L/min |
| Ambient temperature | -25℃~ +55℃; -40℃~ +50℃ |
| Relative humidity | 20% – 95% |
| Unit noise rate | < 70dB (A); |
| Inlet vacuum rate for suction pump | ≧54kPa |
| Communication | With RS 485 port, or current loop |
| Power supply | AC 220V( -15%~+10%),(50/60±1)Hz; AC 380V( -15%~+10%)； (50/60±1)Hz |
| Digit of sale | 7digits (decimal points can be adjusted ) |
| Digit of volume | 6digits (decimal points can be adjusted ) |
| Digit of unit price | 5digits (decimal points can be adjusted ) |
| Totalizer of sale | 0~42949672.95 |
| Totalizer of volume | 0~42949672.95 |

Fuel Management system

Feature / Console

System Capacities

- Universal Probe/Sensor Inputs

- In-Tank Probes

- Output Relays

- External Inputs low voltage

- External Inputs high voltage

Interface

- LCD Colour touch screen

Inventory Control

- Hourly Reconciliation Monitoring (HRM)

- Business Inventory Reconciliation

- TSL Timed Sudden Loss

Tank Calibration

AccuChart™ (Optional)

In-Tank Leak Test

- 0.38 LPH Volumetric Tank Tightness Testing

- 0.76 LPH Volumetric Tank Tightness Testing

- Continuous Statistical Leak Detection (CSLD)

Line Leak Detection

  - Digital Pressurised Line Leak Detection (DPLLD)

Data Communications

- RS-232 / 485 Configurable Ports

- RS-232

- RS-485

- Ethernet TCP/IP

- External USB 2.0

- Optional IFSF Capability

System Capabilities

- 3 Years Minimum Data Storage

- Email Notification on Time or Event

- On Board HELP, Context Sensitive

- Web Enabled (access via web browser)

Process Piping (ASME B31.4 AND SANS 1200L)

Supporting Specifications

For product piping and fittings, all work involving steel shall be carried out in accordance with ASME B31.4 (latest edition) and SABS 1200L. In the event of conflict between ASME B31.4 and SABS 1200L, ASME B31.4 shall take precedence. In the event of conflict of either of the above specifications with this project specification this project specification shall take precedence.

Pipelines

Notwithstanding the provisions of sub-clause 5.2.3 of SABS 1200 L jointing of pipes and specials of all diameters shall be by field welding, except where pipes are fitted to flanged valves and elsewhere as shown on the drawings or instructed by the Engineer.

The Design Pressures (maximum working pressures) of this system are as follows: Product piping   1 000 kPa All pipes, flanges and fittings shall be suitable for these duties.

Flanges

All flanges shall be ASME B16.5 class 150 weld-neck raised face and constructed of ASTM A105 material unless otherwise stated on the drawings.

The Design Temperatures of this system are as follows: Product above ground piping:

- Minimum -5ºC

- Maximum 60ºC

Wall Thickness of pipes and specials shall be as follows:

Product

Pipes and fittings less than or equal to Ø40 shall be schedule 80. Pipes and fittings greater than Ø40 shall be schedule40, in accordance with ANSI B36.10, unless otherwise stated on the drawings.

Manufacture of Steel Pipes and Specials

Product

Piping shall comply with API-5L-B (ASTM A106 B), according to availability as per Clause PSL 2.5 above. All product piping shall be seamless or longitudinally welded, spiral seam welded shall not be acceptable. Specials, e.g. bends, tees, reducers and welding caps shall be carbon steel to ASTM A234 WPB.

Pipe shall have beveled ends in accordance with ANSI B16.25.

Piping shall be delivered in a clean state, together with all relevant test and quality control documentation as required by this specification.

Measurement and Payment

Notwithstanding the various payment items of Clause 8.2 of SABS 1200 L, payment straight pipes of non-standard lengths will not be measured as extra over.

The rates tendered for flanges shall include for nuts, bolts, washers and gaskets and all things necessary.

Isometric Drawings

If the bidder deem it necessary to prepare isometric drawings, the cost thereof shall be included in the tendered rates. Isometric drawings will not be issued for this project by the client.

Protection of Pipes and Specials

Internal Protection of product pipes and specials

No internal protection is required for product pipes and specials.

External Protection of New Above-Ground Piping

Pipes, specials, valves, pumps, filters, equipment items and nuts and bolts shall be protected by preparing and painting as follows:

SURFACE PREPARATION:

Remove all oil and grease by washing with a water emulsifiable solvent degreaser and rinsing with potable water. Dry abrasive blast to near white metal in accordance with SIS SA2½ of the International Standard ISO 8501-1:1988 to obtain a surface profile of 75µ +-20µ. Unless otherwise specified by the paint supplier.

COATING SYSTEM:

| Surface preparation | Blast scouring Sa2.5 -Average roughness G |  |
| --- | --- | --- |
| Primer | Zinc rich epoxy (Sigmazinc 109 HS) | 100µ |
| Intermediate Primer | Polyamide-cured epoxy (Sigmacover 435) | 125µ |
| Finishing coat | Alihatic acrylic polyurethane (Sigmadur 550) | 50µ |

NOTE:

Two coats of Sigmadur 550 or equivalent may be required if applied by brush or roller.

The Sigmacover 435 or equivalent and Sigmadur 550 or equivalent coatings must be carried out after erection; any damage to the primed surface shall be touched up with a zinc rich primer.

The above is read in conjunction with the paint manufacturer’s specification for that particular paint. The manufacturer’s specification shall be used for minimum time between coats.

The colour coat shall be included in the finishing coats mentioned above. The final colour of above ground steel pipes shall be as follows:

The final colour of specials shall be as follows:

| Surface preparation | Blast scouring Sa 2½ - Average roughness G |  |
| --- | --- | --- |
| Primer | Zinc rich epoxy (Sigmazinc 109 HS) | 100µ |
| Intermediate primer | Polyamide-cured epoxy (Sigmacover 435) | 125µ |
| Finishing coat | Aliphatic acrylic polyurethane (Sigmadur 550) | 50µ |

| Product | Pipe Colour | Colour Band | Sans Colour Number |
| --- | --- | --- | --- |
| Diesel 50 ppm | Aluminium / Silver | Straw / Dark Violet / Straw | B33 / F06 / B33 |

Note that repairs to any existing painted surfaces shall be done in accordance with this specification.

Pipe Identification

The painting (stencilling) of the following markings (50mm lettering) to equipment and pipes shall be included in the tendered rates for piping.

Colour bands on all pipelines at bends, road receipt nozzle and flanges.

Flow direction arrows with self-adhesive stickers or lacquer paint at the entrance or exit of each obstacle (tie- in point at the generator; points through walls (both sides), straight section of pipe before connecting to the tank and road receipt nozzle).

Fluid flow direction on the pipe has an isosceles triangle shape (base: 50 mm, height: 150 mm) and    be black in colour.

Note that the repairs to any existing painted structures shall be done in accordance with this specification.

Bolts and Nuts

Product piping: Stud bolts and nuts shall conform to ANSI B16.5 and be suitable for raised face flanges. (A193 B7 studs with A194 Gr 2H nuts)

Gaskets

Gaskets shall be spiral wound low stress type, expanded graphite filler, with internal and external ring. Spiral wound metallic strip and inner reinforcement ring in stainless steel 316L, outer cantering ring in carbon steel protected with epoxy. These gaskets shall be 3mm thick.

Welding Procedures

Prior to the commencement of field welding, welding procedures shall be established and approved by the engineer and thereafter such welding procedure shall be adhered to during subsequent construction and shall not be altered unless specifically authorised by the engineer.

The bidder shall provide a detailed description of all aspects of the welding technique to be employed both in jointing pipes in assemblies above trench level and in executing in-situ welds whether above or below ground level. The information required shall include a drawing of the prepared end for butt welding of flanges and pipes.

Records shall be kept by the bidder to enable each weld to be subsequently identified with the welder concerned.

Procedure Qualification Tests

Before the bidder commences routine field welding the procedures test laid down in API 1104 or ASME Section IX shall be carried out.

The minimum number of root bead welds, the minimum number of second bead welds, and the type of clamp used (internal or external) shall be given in the description of the welding technique.

The bidder shall maintain a record of all welders employed on the works giving particulars of each individual welder’s qualification tests carried out in terms of ASME IX, the cost of which shall be borne by the bidder. Nevertheless, the coding of welders for this project shall be carried out by a recognised independent inspection authority approved by the engineer and the cost of such coding shall be for the account of the bidder.

Before a welder is employed on tack or root welds, he shall carry out a test and root weld on a pipe of the same materials and under conditions as close as possible to those experienced on the actual pipeline.

If icicles are present in the bore of the pipes or the weld metal projects more than 5mm the welder shall not be permitted to undertake tack or root welding. The completed test weld pieces shall be visually examined and then radiographed. The weld appear sound it shall be subjected to approved root and face bend tests. Test pieces shall be retained by the Bidder and marked so that they can be identified with the welding carrying out the test.

Weather

Field welding shall not be performed when the surfaces to be welded are wet or during periods of high wind unless the operator and the work are properly protected and sheltered in an approved manner.

Preparation of Joint

Where scarf cutting of the pipe is required in the field the pipe ends shall be prepared by machining or machine flame cutting. Hand flame cutting shall not be permitted.

When jointing pieces by butt welding the number of tack welds applied shall be kept to a minimum to be effective in holding the pipe end securely and to maintain the required root gap prior to welding, but shall be not less than four.

The same procedure for hot cutting is applicable for welding, but where a joint is to be made with new to existing pipe; it is preferable for safety reasons to flange the joint. In the case where the flange is jointed to the existing pipe, a rubber expandable plug is inserted into the line far enough from the heat affected zone. As gas test is then done before a hot work permit is issued.

Cutting and Welding Work – where applicable

Cold Cutting (pipe cutter or hand sawing)

Before any work is to be done to product pipelines they are to be disconnected from any tankage or other possible product source. Before disconnecting or cutting any pipelines, adequate electrical continuity is to be maintained to prevent sparking due to stray currents in the pipelines. A 50sq.mm (minimum) copper cable be used for this purpose and be suitably clamped.

The line must be drained of all product after isolation from the tank and then flushed with water. As the cutting process is cold, a gas test is not required, but it is to be assumed that there will be flammable vapours present.

Critical Tie-Ins Using the “Clay Plug” Method

Where the downtime on a particular pipeline is critical or where it is impractical to gas free a pipeline, the engineer may order the “clay plug” method to be used to perform the tie-in. The existing lines for the particular product will be drained (not gas freed) by the bidder under the supervision of the engineer. The bidder shall then cold cut the existing lines on either side of the tie-in points and install slip on flanges (unless bolting to an existing flange) on the existing pipe upstream and downstream of the tie-in point using the “clay plug” method. The open ends of the cut existing lines shall be “clay plugged” thus eliminating the need for gas freeing during the tie-in period. Partially prefabricated tie-in spool pieces shall then be installed, tack welded, removed, fully welded, pressure tested and reinstalled after removal of the “clay plugs”.

The Bidder shall allow in his tendered rates for the provision of sufficient cold cutting equipment and “clay plugs” to work simultaneously on all tie-in points for the line and for all extra costs involved in performing the above operations.

The use of plumbers’ plugs as “clay plugs” will be permitted provided that the seal between the plug and the pipe wall is air tight.

All plugs are to be vented to prevent pressure build up behind the plug. Vents are to end a minimum of 10m past all hot work and the vent pipe is to be of a non-flammable material in the vicinity of the welding.

A gas test will be required after installation of the plug before any welding commences.

Cleanliness during pipe fabrication

Due to the consequential damage associated with ‘dirty product’, every effort must be made by the bidder to ensure internal cleanliness of product lines during fabrication.

Plastic, rubber or wood caps are to be utilised to seal the pipes to ensure cleanliness during all transport, storage and handling operations, up to placing the pipe prior to welding.

Inspection

Facilities shall be provided for the engineer so that he may be able to inspect, during the process of welding, any layer of weld metal. The engineer may require any defective welds either to be cut out and re-welded or repaired at his discretion.

The bidder shall clean thoroughly all welds prior to inspection. The Engineer may require a number of completed joints, selected at random, to be cut for mechanical tests or to be selected for visual inspection, micro examination or examination by other means. When the engineer orders the bidder in writing to cut out and test joints the bidder shall be paid for such work at day work rates.

If as a result of inspection and testing, the work of any welder is found to be unsatisfactory, the welder will not be permitted to continue under this Contract.

All inspection shall be in accordance with the conformity assessment as defined in SANS 347. The bidder shall ensure that this is done and submitted to the engineer for acceptance.

Radiographic Examination

The bidder will engage the services of an approved radiographer for examination of approximately 10% of all butt welds in the pipeline. The cost of this testing shall be included in the rates tendered for piping. For every weld that fails the radiographic test, the contract shall be debited with the cost of re-testing the repaired work. Any radiographic testing which the bidder may consider necessary in addition to that specified shall be at his own expense. All faults revealed by the tests shall be repaired to the approval of the engineer.

Other Non-Destructive Tests

The bidder will engage the services of an approved non-destructive testing agency for examination of approximately 10% of all socket/fillet welds in the pipeline by means of dye penetrant or other suitable tests. The costs involved with this testing shall be borne by the bidder.

Standards of Acceptability

The completed welds shall comply with the requirements of ASME IX. Work on which unauthorised repairs have been carried out may be rejected.

Repairs to Minor Faults

Faulty welds shall be rectified in accordance with ASME IX.

All costs relative to the repair of faulty joints, including removal and replacement of the backfill and making good the wrapping and lining shall be borne by the bidder.

Tolerances

Tolerances for the line and level of pipelines shall be as follows:

| Positions of bends: | within 150 mm of the location shown on the drawings or as agreed with the Engineer |
| --- | --- |
| Level of pipe invert | within 25mm of the level shown on the drawings |
| Location of pipe centre in plan | within 25mm of the location shown on the drawing through the sleeves and culverts and elsewhere within 75mm position shown on the drawings or as agreed by the Engineer. |
| Line of the Pipe | The line of a straight pipe shall not vary by more than 15mm from the line of a12m vertical or horizontal line |

Testing

Protective Coatings and Linings

The bidder shall provide all necessary labour and equipment for conducting the tests as described above. All tests are to be carried out in the presence of the engineer at such time and in such manner as he may direct.

Testing of Pipelines

General

All the pipelines shall be tested as directed by the engineer. Blank flanges with necessary air, water and pressure gauge connections shall be provided by the bidder for this purpose. Before testing any pipeline all construction work on the pipeline shall be complete unless otherwise specifically directed by the engineer.

All joints, including welds, are to be left un-wrapped and exposed for examinations during the air tests. Vents, drains and relief valves shall be utilised to prevent damage to the piping system due to expansion of the test fluid during the test period. The maximum operating pressure of each piece of equipment, including instruments, shall be checked against the test pressure of the piping system in which the piece of equipment is incorporated. If the test pressure of the piping system is greater than the maximum operating pressure of the equipment, the equipment shall be blanked off and tested separately.

Water may be used for hydrostatic testing of process lines provided special precautions are taken for draining and drying the lines.

Other testing fluids may be used provided they are approved by the Engineer before testing is started.

All piping, vessels, filters, exchanges, etc. shall be completely drained of all fluid after testing. Special precautions be taken to ensure that all pockets where fluid may be trapped are properly drained.

All piping tested with water, in which water would be detrimental to the process operation, shall be thoroughly dried. The engineer shall determine when the piping is dry.

The Bidder shall supply all necessary water or other fluid if so specified, labour and equipment for conducting the tests as described herein. All tests shall be carried out in the presence of the Engineer or his representative at such times and in such manner as he may direct.

Static Test

The pipeline or equipment shall be filled with water, all scours on the section being opened fully for one minute or until the water emerges clean. If after 48 hours the Engineer is satisfied that there are no major leaks, the pressure test shall be carried out.

Pressure Test

A suitable pump shall be connected to the pipeline at a mutually agreed point.

The pressure in the pipeline under test shall be raised slowly by means of the pump and measured by a pressure gauge connected to the pipeline. The full test pressure shall be maintained for at least 4 hours, or longer if so required by the engineer.

The required test pressure of steel pipelines and fittings shall be 1.5 times the design pressure (See PSL 2.2). In the case of valves, this shall also be the pressure to be used for gate and body leakage and opening and closing torque tests. Ensure all valves are open during pressurization.

No section of a pipeline shall be tested against a closed valve.

The bidder shall be paid under the appropriate item in the Schedule of Quantities for hydraulic tests. Re-testing after repairs required by this clause shall not be paid for.

This pressure test shall also comply with the requirements of SABS 1200 L and ASME B31.3.

Testing and Commissioning

Testing

On completion of hydraulic testing, all new pipelines shall be completely flushed out with clean water for a period of not less than one minute and at a velocity greater than 4m/s to ensure the removal of any remaining debris to the satisfaction of the engineer.

In addition to the above, the following tests shall be performed:

Product Pipework

After pressure testing and flushing of the pipelines, all isolating valves shall be installed and the pipework hydraulically pressurised to the design pressure. Each valve, either new or existing used in new lines, shall then be opened and closed and visually checked for leakage.

Commissioning

Prior to commissioning, all product pipelines that have been hydro tested and flushed shall be thoroughly air dried. Filter cartridges / elements (as applicable) are not to be installed until flushing and air drying are completed and only when instructed in writing by the engineer.

Commissioning shall be directed by the engineer but the bidder and any specialist suppliers, (e.g. for pumps, meters, valves, instrumentation etc) shall attend and assist the engineer as necessary.

Skid/cradle mounted items shall be factory commissioned before dispatch to site.

Protection of Pumps, Valves & Equipment

Internal Protection

Internal protection is not required.

External Protection

External protection of valves shall be as specified for above ground pipes in sub-clause PSL 3.3.

Labelling

All equipment items are to be labelled with the tag number as shown on the P&ID drawing

Where applicable the tag number is to be hard stamped onto the nameplate for that particular piece of equipment. Where the equipment does not have a metal name plate the tag is to be stuck to the equipment with a suitable petrochemical resistant adhesive. In addition, each piece of equipment is to have a loose tag fixed with stainless steel wire to the equipment

All labels shall be engraved in laminated plastic (Traffolite) 10mm high with black lettering on a white background.

Alternative Equipment

Provision is made in the schedule of quantities for the bidder to offer alternative equipment to the make and model specified (rate only), i.e. summation of schedule based on specified equipment only. Where bidders do offer alternative equipment, full technical details of this equipment are to be provided with the bid.

Drawings

Drawings Shop Drawings

The proposed routes of all new or modified piping are shown on the drawings. No further details in the form of isometrics drawings will be issued by the engineer. The bidder shall prepare his own isometric drawings if necessary and shall allow for any costs in his tendered rates. All piping shall be fabricated from measurements taken on site after confirmation of the pipe routes with the engineer or his representative.

Record Drawings

The bidder will be required to mark as-built information on a set of prints, to permit the modification of the original drawings by the engineer. This information is to be provided within 2 weeks of completion.

- Applicable national and international  standards

Although not bound in nor issued with this document, all applicable local legislation and the following standardized specifications shall be adhered to and shall form part of the contract document and, notwithstanding the provisions of Sub clause 2.2 of SANS 1200 A, editions specified below shall apply:

| SANS 10131:2004 | Above-ground Storage Tanks for Petroleum Product |
| --- | --- |
| SANS 1200 HA | Structural steelwork (small works) |
| SANS 1200 HC | Corrosion protection of structural steelwork |
| ASME Section IX | Welding and brazing qualifications |
| SANS 10108:2017 | Classification of Hazardous Locations and the Selection of Suitable Equipment |
| ASME B31.4: 2009 | Process Piping |
| IP Model Code | Area Classification Code for Installations Handling Flammable Liquids |

- Format of communications

Communication will be conducted telephonically and via e-mail.

- Electronic payments

State details required / procedures to obtain electronic payments, as relevant

- Site Information

The contract is applicable to the following site: uMkondeni Workshops Izintaba Region

### Security

The Contractor shall ensure that all tools and materials are kept under lock and key. uMngeni-uThukela Water is not responsible for the loss of the Contractor’s equipment as a result of any cause whatsoever. uMngeni-uThukela Water reserves the right for security guards to search persons or vehicles entering or leaving the premises.

Permits

The Contractor shall not perform work for which the issuing of a permit is required prior to the obtaining of a duly completed and approved permit. The following are included as hazardous tasks and may not be carried out by the Contractor unless uMngeni-uThukela Water has duly authorized a work permit:

•	Cutting or welding in any risk area.

•	Working at a height of more than two meters.

•	Working with hazardous substances (e.g. toxic chemicals and flammable liquids).

•	Working inside confined spaces (e.g. vessels, chambers and pipelines).

•	Working in electrical lockouts installations.

- Breaking in any live water main.

### Housekeeping

After the completion of each day work the Contractor must make good and clean up the site area where work was performed, and also at the completion of the contract. Sites must be kept reasonable tidy during work operations.

### Alcohol or Intoxicating Substances

The Contractor shall ensure that no alcohol or intoxicating substances are on their possession while on site. Anyone suspected to be intoxicated or under influence of alcohol shall not be allowed on site.

## Safety

## uMngeni-uThukela Water has a strict attitude when it comes to personal safety of all on site. Thus a Contractor and sub-contractors have to attend a Compulsory Induction before starting the project. Unsafe activities, equipment and procedures shall not be tolerated. And it should be noted that this work requires people to work in elevated positions and confined areas; therefore compliance to the OHS Act is mandatory. The Contractor will be required to submit together with the quotation a schedule of all his activities and as to how he intends to carry them, to the Umgeni Water Project Manager and Safety Officer for approval.

### Safety Clothing and Equipment

The Contractor shall supply all the Umgeni Water specified safety clothing and equipment for his workmen on site. The Contractor’s workmen on site shall wear hard hats, safety glasses, safety shoes and overalls.

### Accidents

In addition to any statutory obligations, the Contractor shall immediately report to the Project Manager every occurrence causing damage to property or injury to persons.

If required by the Employer, the Contractor shall submit a further report in writing to the Employer within 48 hours of such requirement setting out full details of the occurrence.

The Contractor shall report those injuries that are reportable in terms of Section 24 of the OHS Act (1993) to the Department of Labour.

The Employer shall have the right to make any queries either on the Site or elsewhere as to the cause and results of any such occurrence and the Contractor shall make available to the Employer the necessary facilities for carrying out such enquiries

- Contract term

- We anticipate that the Contract will be as per deliverables

- Quality management

QA\QC Data Book

The Bidder shall build and maintain a quality data book which shall as a minimum have the following sections;

- Final Acceptance, Hand-over forms and Snag Lists

- Quality Control Plans

- Drawings

- General Arrangement Drawings

- Weld Maps

- NDE/NDT reports

- Pressure Test Certificates for pipes, valves, vessels and equipment h)	Welding register

- Radiographic and Surveillance Reports

- Material Certificates (pipes, fittings, valves, gauges, welding consumables, Calibration Certificates (instruments, gauges, meters, etc.)

- Corrosion Protection Inspection Certificates

- Welding Procedure Specification (WPS)

- Welders Coding Certificates

- Pressure test certificates

- Pipe wrapping Holiday Test results

- Equipment catalogues, drawings, instruction and installation manuals as well as suppliers acceptance certificates

- As built drawings

- Electrical certificates of compliance, where applicable

- Paint / galvanising thickness tests

- Commissioning Reports

- The data book shall be compiled in a hard cover file suitably indexed as well as an electronic copy (pdf)on disk

Quality Control Procedures

A detailed Quality Control Plan (QCP) is to be submitted, before any work may commence, for approval of hold, witness, and inspection, points. The quality plan shall be tailored to comply with the Umgeni Waters specific requirements. A sample of the proposed plan is to accompany the bid.

The Quality Control Plan shall as a minimum have the following activities:

- Documentation

- Fabrication Drawing Approval

- Approve QCP

- Material Identification

- Material ID Map

- Welding Procedure Approval

- Welders Certificate Approval

- Weld Map Approval

- Dimensional Check

- Non-destructive Examination (NDE) to check integrity

- Penetrant test Inspection

- Pressure Test

- Corrosion Protection

- Final Inspection

The bidder shall state in his bid the name of the painting sub-bidder that he proposes to use to carry out any corrosion protection work under this contract.

The bidder shall transfer the material trace (heat)

number onto all pieces of the pipeline using permanent markings. No high stress stamps shall be used.

The bidder shall ensure that all his sub-bidders have obtained a copy of this specification.

The bidder shall accept full responsibility for the quality of his work and of materials used, irrespective of any quality surveillance that may be carried out by the engineer or his representative.

The engineer may, at his discretion, require a quality audit of the bidder or any of the sub-bidders to ensure that he has the capabilities, resources and quality control facilities to carry out the work to ensure compliance with this specification.

The bidder shall have available the latest issue of each of the manufacturer’s data sheets for the items / materials to be used, all specifications and Codes of Practice relevant to the work to be carried out, including a copy of this specification, all of which shall be available to the bidder’s Quality Control Manager.

The bidder shall:

- Supply a quality plan and quality program at the time of bidding, both of which are subject to acceptance by the engineer.

- Maintain quality control records in accordance with the quality plan during execution of the contract such records shall be available to the engineer or his representative at each quality surveillance visit.

- Mark or securely label each special component (see drawings) with a unique identification tag, and

- Carry out such tests as are required to ensure compliance with the specification. The cost of quality control shall be inclusive in the bidder’s bid price.

The cost of quality surveillance will be borne by Umgeni Water, except when surveillance results in rejection of the lot or when notice by the bidder results in a fruitless trip, in which case the cost of surveillance shall be debited against the bidder’s account. The engineer may, at his discretion, employ an independent technically qualified organization to carry out quality surveillance of the work on his behalf. In the event of dispute, the engineer’s decision shall be final. For the purpose of carrying out quality surveillance, the engineer or his representative shall be granted access to any part of the bidder’s premises relevant to the work being carried out, at any reasonable time. The bidder shall provide, at his own cost, any equipment or labour necessary to gain access to surfaces which are coated, to be coated or are in the process of being coated.

The bidder shall advise the engineer timeously, in writing, when and where the following processes will be carried out;

1)	Completion of fettling or dressing prior to leaving the fabricator’s works

2)	Blast cleaning and application of the first or primer coat

3)	After completion of all coats to be applied at the bidder’s works

4)	At the commencement of repairs or overcoats of existing equipment to be carried out on site.

Failure of the bidder to advise the engineer of his program may result in rejection of the work. The cost of any such rejection shall be borne by the bidder.

Quality control reports shall be updated regularly and a copy of all relevant reports shall accompany all payment certificates. No payments will be authorized by the engineer unless a copy of an approval report has been received by him. The engineer may withhold payment until a final report has been issued, giving approval to the components after installation on site and repair of damage to coating.

Proper and adequate quality control records shall be maintained by the bidder for all stages of the work. These records shall be available for inspection by the engineer or his representative at the time of quality surveillance. Incomplete, inaccurate or inadequate records shall be regarded as non-compliance with the specification, and the cost of surveillance will be back charged to the bidder.

No variation from specification, or change of sub-bidder or materials to be used from those stated in the bid documents, will be permitted without written approval of the engineer. Products equivalent to those specified may be submitted for approval and adequate information shall be supplied by the bidder to engineer in order to assess the claim of equivalence from the bidder. Approval of alternative equipment shall valid only on a written instruction from the engineer.

- Mandatory documentation

- SBD 4 – Bidders disclosure

- Pricing

- The bidder shall provide the price proposal as detailed in SBD 3.1

- The bidders’s price must be fully inclusive, and each item must be clearly specified.

- All additional costs must be clearly specified and included in the total quotation price, (e.g. transport, labour, etc.).

- All prices must be VAT inclusive.

- The bidder is responsible for all the cost that they shall incur related to the preparation and submission of the quotation.

- Evaluation Process

The RFQ will be evaluated using a two (02)-stage evaluation approach:

  - First stage:

Mandatory Requirements

SBD 4 – Bidders disclosure

Administrative Requirements:

Bidder completed all RFQ Forms

Bidder submitted CIPC document/CSD Report

Valid B-BBEE Certificate/Sworn Affidavit

CIDB 1ME or 1EP/EB

  - Second Stage: Price and Preference goals

- Subsequent to the evaluation of mandatory/ administrative requirements, the second stage of evaluation of the bids will be in respect of price and preferential procurement only.

- Tenderer is tax complaint.

- In compliance with the Preferential Procurement Regulations 2022, the 80/20 preference point system is applicable: points for this bid shall be awarded for:

a) 	Price; and (80) and Preference as defined in SBD 6.1 (20)

- The Preference Goals that have been identified for this bid is stipulated in SBD 6.1

- Preferential goals and applicable points for this tender in terms of Preferential Procurement Regulations 2022, are indicated in the table below:

|  | Description | 80/20 | Evidence to be provided |
| --- | --- | --- | --- |
| HDI | 51% owned by Black people | 10 | Valid B-BBEE Certificate/Sworn Affidavit |
| RDP | The promotion of South African owned enterprises | 10 | CIPC documents/CSD report |
| Total points for preferential goals |  | 20 |  |

- Failure on the part of a bidder to submit proof or documentation required in terms of this RFQ to claim points for specific goals, will be interpreted to mean that preference points for specific goals are not claimed by the bidder.

- UW reserves the right to request a bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim in regard to preferences, in any manner required by UW.

- UW reserves the right to conduct negotiations with the qualifying bidder/s regarding any terms and conditions, including price(s), of a proposed contract where applicable UW reserves the right not to accept the lowest financial offer or any offer.

6. SBD 3.1 PRICING SCHEDULE – FIRM PRICES (PURCHASES)

NOTE:

ONLY FIRM PRICES WILL BE ACCEPTED. NON-FIRM PRICES (INCLUDING PRICES SUBJECT TO RATES OF EXCHANGE VARIATIONS) WILL NOT BE CONSIDERED

IN CASES WHERE DIFFERENT DELIVERY POINTS INFLUENCE THE PRICING, A SEPARATE PRICING SCHEDULE MUST BE SUBMITTED FOR EACH DELIVERY POINT

Name of bidder _______________________ RFQ number______Q24/756NM_______ Closing Time ___________15H00_________ Closing date__________03/07/2024________

OFFER TO BE VALID FOR___________CALENDER DAYS FROM THE CLOSING DATE OF QUOTE.

BASIC GOODS PRICE TABLE

______________________________________________________________________

| #### Item No. | #### Material / Description of item | #### Unit Measure | #### Qty (A) | #### Unit Price | #### Quoted Price(AxB) #### Excl. Vat |
| --- | --- | --- | --- | --- | --- |
| 1 | Supply and installation of fuel dispensers and pumps with minimum 55L/min suction | No. | 2 |  |  |
| 2 | Smart fuel management system for fuelling stations (all software and instrumentation works) | No. | 3 |  |  |
| 3 | Supply and Install automatic shutoff valve to the generators | No. | 2 |  |  |
| 4 | Installation of pipework for diesel tank installation including meters | sum | 1 |  |  |
| 5 | Installation of pipework for petrol tank installation including meters | sum | 1 |  |  |
| 6 | Electrical installations for both diesel and petrol system | sum | 1 |  |  |
| 7 | Installation of safety signs | Sum | 1 |  |  |
| 8 | Installation of fire protection systems | sum | 1 |  |  |
| 9 | As-built drawings (pipe work, and electrical) | sum | 1 |  |  |
| SUB TOTAL |  |  |  |  |  |
| VAT @ 15% |  |  |  |  |  |
| GRAND TOTAL (price SA Rands with all applicable taxes included) |  |  |  |  |  |
| I (full name)__________________________________________, in my capacity as ___________________________, the duly authorized representative of ________________________________________________(business name) hereby declares that the offer is in accordance with the attached specification, notes to suppliers & accepts all conditions/clauses contained in the said documents. |  |  |  |  |  |
| Signature of duly authorized representative |  |  | _______________ | DATE: __________________ |  |

Required by					_____________________

Delivered to:					_____________________

_____________________

Product brand/make				_____________________

Country of origin				_____________________.

Does the offer comply with the specification(s)?	YES/NO

If not to specification, indicate deviation(s)		_____________________.

Period required for delivery				_____________________.

Delivery: 						Firm/not firm

Delivery basis 						_____________________.

Note:

All delivery costs must be included in the bid price, for delivery at the prescribed destination.

All applicable taxes” includes value added tax, pay as you earn, income tax, unemployment insurance fund contributions and skills development levies.

*Delete if not applicable

7. AUTHORITY TO SIGN

RFQ NO: ______________________________

Description: ______________________________________________________________

Close Corporation / Company / Partnership / Trust /Sole proprietor or sole trader

Name: _______________________________________________________________________

Registration Number: _______________________________________________________ RESOLUTION OF THE DIRECTORS OF THE COMPANY etc. RESOLVED that _____________________, in his/her capacity as _______________________________, is authorized to make applications on behalf of the  Close Corporation / Company / Partnership / Trust /Sole proprietor or sole trader for:

Any documentation relating to the business (which is not necessarily a change of ownership). The nominated person will also have access to webpage for the business. Signature(s) for Close Corporation / Company / Partnership / Trust/ Sole proprietor or sole trader.

(Sole member still must sign this resolution)

Signature of members:

Name 						Signature 				Date

1. _______________________            ________________________               ____________________

2. _______________________            ________________________ 	     ____________________

3. _______________________            ________________________               ____________________

4. _______________________            ________________________	     ____________________

5. _______________________            ________________________	     ____________________

6. _______________________            ________________________	     ____________________

8. SBD 4 - BIDDER’S DISCLOSURE

- PURPOSE OF THE FORM

Any person (natural or juristic) may make an offer or offers in terms of this invitation to bid. In line with the principles of transparency, accountability, impartiality, and ethics as enshrined in the Constitution of the Republic of South Africa and further expressed in various pieces of legislation, it is required for the bidder to make this declaration in respect of the details required hereunder.

Where a person/s are listed in the Register for Tender Defaulters and / or the List of Restricted Suppliers, that person will automatically be disqualified from the bid process.

- Bidder’s declaration

2.1 	Is the bidder, or any of its directors / trustees / shareholders / members / partners or any person having a controlling interest in the enterprise, employed by the state YES/NO

2.1.1	If so, furnish particulars of the names, individual identity numbers, and, if applicable, state employee numbers of sole proprietor/ directors / trustees / shareholders / members/ partners or any person having a controlling interest in the enterprise, in table below.

| Full Name | Identity Number | Name of State institution |
| --- | --- | --- |

2.2	Do you, or any person connected with the bidder, have a relationship with any person who is employed by the procuring institution? YES/NO

2.2.1    If so, furnish particulars:

______________________________________________________________________________________________________________________________________

2.3 	Does the bidder or any of its directors / trustees / shareholders / members / partners or any person having a controlling interest in the enterprise have any interest in any other related enterprise whether or not they are bidding for this contract?	YES/NO

    - If so, furnish particulars:

____________________________________________________________________________________________________________________________________________

- DECLARATION

I, the undersigned, (name)______________________________ in submitting the accompanying bid, do hereby make the following statements that I certify to be true and complete in every respect:

3.1 	I have read and I understand the contents of this disclosure;

3.2	I understand that the accompanying bid will be disqualified if this disclosure is found not to be true and complete in every respect;

3.3 	The bidder has arrived at the accompanying bid independently from, and without consultation, communication, agreement or arrangement with any competitor. However, communication between partners in a joint venture or consortium will not be construed as collusive bidding.

3.4 	In addition, there have been no consultations, communications, agreements or arrangements with any competitor regarding the quality, quantity, specifications, prices, including methods, factors or formulas used to calculate prices, market allocation, the intention or decision to submit or not to submit the bid, bidding with the intention not to win the bid and conditions or delivery particulars of the products or services to which this bid invitation relates.

3.4	The terms of the accompanying bid have not been, and will not be, disclosed by the bidder, directly or indirectly, to any competitor, prior to the date and time of the official bid opening or of the awarding of the contract.

  - There have been no consultations, communications, agreements or arrangements made by the bidder with any official of the procuring institution in relation to this procurement process prior to and during the bidding process except to provide clarification on the bid submitted where so required by the institution; and the bidder was not involved in the drafting of the specifications or terms of reference for this bid.

  - I am aware that, in addition and without prejudice to any other remedy provided to combat any restrictive practices related to bids and contracts, bids that are suspicious will be reported to the Competition Commission for investigation and possible imposition of administrative penalties in terms of section 59 of the Competition Act No 89 of 1998 and or may be reported to the National Prosecuting Authority (NPA) for criminal investigation and or may be restricted from conducting business with the public sector for a period not exceeding ten (10) years in terms of the Prevention and Combating of Corrupt Activities Act No 12 of 2004 or any other applicable legislation.

I CERTIFY THAT THE INFORMATION FURNISHED IN PARAGRAPHS 1, 2 and 3 ABOVE IS CORRECT.

I ACCEPT THAT THE STATE MAY REJECT THE BID OR ACT AGAINST ME IN TERMS OF PARAGRAPH 6 OF PFMA SCM INSTRUCTION 03 OF 2021/22 ON PREVENTING AND COMBATING ABUSE IN THE SUPPLY CHAIN MANAGEMENT SYSTEM SHOULD THIS DECLARATION PROVE TO BE FALSE.

_________________________	         _________________

Signature	   Date

_________________________	_________________

Position                                                    Name of bidder

9. SBD 6.1 PREFERENCE POINTS CLAIM FORM IN TERMS OF THE PREFERENTIAL PROCUREMENT REGULATIONS 2022

This preference form must form part of all tenders invited.  It contains general information and serves as a claim form for preference points for specific goals.

NB:	BEFORE COMPLETING THIS FORM, TENDERERS MUST STUDY THE GENERAL CONDITIONS, DEFINITIONS AND DIRECTIVES APPLICABLE IN RESPECT OF THE TENDER AND PREFERENTIAL PROCUREMENT REGULATIONS, 2022

- GENERAL CONDITIONS

  - The following preference point systems are applicable to invitations to tender:

the 80/20 system for requirements with a Rand value of up to R50 000 000 (all applicable taxes included); and

the 90/10 system for requirements with a Rand value above R50 000 000 (all applicable taxes included).

  - To be completed by the organ of state

The applicable preference point system for this tender is the 80/20 preference point system.

  - Points for this tender (even in the case of a tender for income-generating contracts) shall be awarded for:

- Price; and

- Specific Goals.

  - To be completed by the organ of state:

The maximum points for this tender are allocated as follows:

|  | POINTS |
| --- | --- |
| PRICE | 80 |
| SPECIFIC GOALS | 20 |
| TOTAL POINTS FOR PRICE AND SPECIFIC GOALS | 100 |

  - Failure on the part of a tenderer to submit proof or documentation required in terms of this tender to claim points for specific goals with the tender, will be interpreted to mean that preference points for specific goals are not claimed.

  - The organ of state reserves the right to require of a tenderer, either before a tender is adjudicated or at any time subsequently, to substantiate any claim in regard to preferences, in any manner required by the organ of state.

- DEFINITIONS

- “tender” means a written offer in the form determined by an organ of state in response to an invitation to provide goods or services through price quotations, competitive tendering process or any other method envisaged in legislation;

- “price” means an amount of money tendered for goods or services, and includes all applicable taxes less all unconditional discounts;

- “rand value” means the total estimated value of a contract in Rand, calculated at the time of bid invitation, and includes all applicable taxes;

- “tender for income-generating contracts” means a written offer in the form determined by an organ of state in response to an invitation for the origination of income-generating contracts through any method envisaged in legislation that will result in a legal agreement between the organ of state and a third party that produces revenue for the organ of state, and includes, but is not limited to, leasing and disposal of assets and concession contracts, excluding direct sales and disposal of assets through public auctions; and

- “the Act” means the Preferential Procurement Policy Framework Act, 2000 (Act No. 5 of 2000).

- FORMULAE FOR PROCUREMENT OF GOODS AND SERVICES

  - POINTS AWARDED FOR PRICE

3.1.1   THE 80/20 OR 90/10 PREFERENCE POINT SYSTEMS

A maximum of 80 or 90 points is allocated for price on the following basis:

# 80/20	or	90/10

Ps=801-Pt-PminPmin	or	Ps=901-Pt-PminPmin

Where

Ps	=	Points scored for price of tender under consideration

Pt	=	Price of tender under consideration

Pmin	=	Price of lowest acceptable tender

  - FORMULAE FOR DISPOSAL OR LEASING OF STATE ASSETS AND INCOME GENERATING PROCUREMENT

    - POINTS AWARDED FOR PRICE

A maximum of 80 or 90 points is allocated for price on the following basis:

# 80/20	               or	            90/10

Ps=801+Pt-PmaxPmax	or	Ps=901+Pt-PmaxPmax

Where

Ps	=	Points scored for price of tender under consideration

Pt	=	Price of tender under consideration

Pmax	=	Price of highest acceptable tender

- POINTS AWARDED FOR SPECIFIC GOALS

  - In terms of Regulation 4(2); 5(2); 6(2) and 7(2) of the Preferential Procurement Regulations, preference points must be awarded for specific goals stated in the tender. For the purposes of this tender the tenderer will be allocated points based on the goals stated in table 1 below as may be supported by proof/ documentation stated in the conditions of this tender:

  - In cases where organs of state intend to use Regulation 3(2) of the Regulations, which states that, if it is unclear whether the 80/20 or 90/10 preference point system applies, an organ of state must, in the tender documents, stipulate in the case of—

- an invitation for tender for income-generating contracts, that either the 80/20 or 90/10 preference point system will apply and that the highest acceptable tender will be used to determine the applicable preference point system; or

- any other invitation for tender, that either the 80/20 or 90/10 preference point system will apply and that the lowest acceptable tender will be used to determine the applicable preference point system,

then the organ of state must indicate the points allocated for specific goals for both the 90/10 and 80/20 preference point system.

Table 1: Specific goals for the tender and points claimed are indicated per the table below.

(Note to organs of state: Where either the 90/10 or 80/20 preference point system is applicable, corresponding points must also be indicated as such.

Note to tenderers: The tenderer must indicate how they claim points for each preference point system.)

| The specific goals allocated points in terms of this tender [select where applicable to this bid] | Number of points allocated (80/20 system) (To be completed by the organ of state) | Number of points claimed (80/20 system) (To be completed by the tenderer) |
| --- | --- | --- |
| 51 % owned by Black people | 10 |  |
| The promotion of South African owned enterprises | 10 |  |

DECLARATION WITH REGARD TO COMPANY/FIRM

  - Name of company/firm	____________________________________________

  - Company registration number: …………………………………………………………...

  - TYPE OF COMPANY/ FIRM

Partnership/Joint Venture / Consortium

One-person business/sole propriety

Close corporation

Public Company

Personal Liability Company

(Pty) Limited

Non-Profit Company

State Owned Company

[Tick applicable box]

  - I, the undersigned, who is duly authorised to do so on behalf of the company/firm, certify that the points claimed, based on the specific goals as advised in the tender, qualifies the company/ firm for the preference(s) shown and I acknowledge that:

- The information furnished is true and correct;

- The preference points claimed are in accordance with the General Conditions as indicated in paragraph 1 of this form;

- In the event of a contract being awarded as a result of points claimed as shown in paragraphs 1.4 and 4.2, the contractor may be required to furnish documentary proof to the satisfaction of the organ of state that the claims are correct;

- If the specific goals have been claimed or obtained on a fraudulent basis or any of the conditions of contract have not been fulfilled, the organ of state may, in addition to any other remedy it may have –

  - disqualify the person from the tendering process;

  - recover costs, losses or damages it has incurred or suffered as a result of that person’s conduct;

  - cancel the contract and claim any damages which it has suffered as a result of having to make less favourable arrangements due to such cancellation;

  - recommend that the tenderer or contractor, its shareholders and directors, or only the shareholders and directors who acted on a fraudulent basis, be restricted from obtaining business from any organ of state for a period not exceeding 10 years, after the audi alteram partem (hear the other side) rule has been applied; and

forward the matter for criminal prosecution, if deemed necessary

SIGNATURE(S) OF TENDERER(S)  ________________________________

SURNAME AND NAME:		   ________________________________

DATE: 				   ________________________________

ADDRESS:			   ________________________________

________________________________

________________________________

________________________________

# SBD 7.2 CONTRACT FORM - RENDERING OF SERVICES

THIS FORM MUST BE FILLED IN DUPLICATE BY BOTH THE SERVICE PROVIDER (PART 1) AND THE PURCHASER (PART 2).  BOTH FORMS MUST BE SIGNED IN THE ORIGINAL SO THAT THE SERVICE PROVIDER AND THE PURCHASER WOULD BE IN POSSESSION OF ORIGINALLY SIGNED CONTRACTS FOR THEIR RESPECTIVE RECORDS.

# PART 1 (TO BE FILLED IN BY THE SERVICE PROVIDER)

- I hereby undertake to render services described in the attached bidding documents to uMngeni-uThukela Water in accordance with the requirements and task directives / proposals specifications stipulated in above mentioned RFQ Number at the price/s quoted.  My offer/s remain binding upon me and open for acceptance by the Purchaser during the validity period indicated and calculated from the closing date of the bid.

- The following documents shall be deemed to form and be read and construed as part of this agreement:

  - Bidding documents, viz

- Invitation to bid;

- Proof of tax compliance status;

- Pricing schedule(s);

- Filled in task directive/proposal;

- Preference claim form for Preferential Procurement in terms of the Preferential Procurement Regulations;

- Bidder’s Disclosure form;

- Special Conditions of Contract;

  - General Conditions of Contract; and

  - Other (specify)

- I confirm that I have satisfied myself as to the correctness and validity of my bid; that the price(s) and rate(s) quoted cover all the services specified in the bidding documents; that the price(s) and rate(s) cover all my obligations and I accept that any mistakes regarding price(s) and rate(s) and calculations will be at my own risk.

- I accept full responsibility for the proper execution and fulfilment of all obligations and conditions devolving on me under this agreement as the principal liable for the due fulfillment of this contract.

- I declare that I have no participation in any collusive practices with any bidder or any other person regarding this or any other bid.

- I confirm that I am duly authorised to sign this contract.

WITNESSES

- ______________

- ______________

DATE:	______________

NAME (PRINT)		________________________________

CAPACITY		________________________________

SIGNATURE		________________________________

NAME OF TENDERER	________________________________

DATE			_______________________________

CONTRACT FORM - RENDERING OF SERVICES (SBD 7.2)

# PART 2 (TO BE FILLED IN BY THE PURCHASER)

- I __________________________________ in my capacity as __________________________ accept your quotation under reference number _____________ dated _______________for the rendering of services indicated hereunder and/or further specified in the annexure(s).

- An official order indicating service delivery instructions is forthcoming.

- I undertake to make payment for the services rendered in accordance with the terms and conditions of the contract, within 30 (thirty) days after receipt of an invoice.

| ## DESCRIPTION OF SERVICE |  |
| --- | --- |
| PRICE (ALL APPLICABLE TAXES INCLUDED) |  |
| CONTRACT TERM / COMPLETION DATE |  |
| TOTAL PREFERENCE POINTS CLAIMED |  |
| 51 % owned by Black people |  |
| The promotion of enterprises located in KwaZulu-Natal |  |

- I confirm that I am duly authorised to sign this contract.

SIGNED AT _______________________________________ 		ON:_____________________

NAME (PRINT):___________________________________	SIGNATURE:_____________________

WITNESSES

- ______________________

- ______________________

DATE:	______________________

OFFICIAL STAMP

the power, by one person or a group of persons holding the majority of the equity of an enterprise, alternatively, the person/s having the deciding vote or power to influence or to direct the course and decisions of the enterprise.

Joint venture or Consortium means an association of persons for the purpose of combining their expertise, property, capital, efforts, skill and knowledge in an activity for the execution of a contract.