8 ton BOILER PB 450 AND MAIN STEAM LINE INSPECTION, CERTIFICATION & ANNUAL SERVICE of 2026 SPECIFICATIONS INCLUDING IDENTIFIED ADDITIONAL WORKS at 100 Old Soutpan Road TAD facility

| # | Description | Comply Yes or No | Amount to be inserted at the last row per section. |
| --- | --- | --- | --- |
|  | Prepare 8 ton coal fired boiler for 12 monthly external inspection. (1) |  |  |
|  | Isolate and drain boiler with main Steam line. (2 main and crown, drainage, 4 manholes) |  |  |
|  | Open smoke box cover doors on boiler. (2 front 2 rear) |  |  |
|  | Clean fire tubes, tube plates and combustion chamber. (all) |  |  |
|  | Open manhole and mud-hole cover doors. (4) |  |  |
|  | Cover water pumps motors with water protection materials against water spillages. (2) |  |  |
|  | Cover main control electric panel with water protection materials. (1) |  |  |
|  | Cover boiler operating water level sensors at the sight gauge glass area. (1) |  |  |
|  | Wash out outer part of the tubes to remove scaling. (only all visible from manhole) |  |  |
|  | Carry out annual inspection on boiler and main steam line by approved inspection authority (AIA) as specified in OHS act. AIA supplied by the appointed contractor. (2) |  |  |
|  | Replace smoke box door seals and box up boiler. (2 front 2 rear) |  |  |
|  | Supply and install new manhole and mud gaskets. (4) |  |  |
|  | Supply and install new gauge glass and gauge glass rubbers. (2 glasses and 4 rubbers) |  |  |
|  | Repack valve glands. (8) |  |  |
|  | Paint rear and front end of boiler with high temperature resistant paint. (2) |  |  |
|  | Wash out and clean outer lagging body sheet to best capabilities. (1) |  |  |
|  | Take/clean out all ash within the boiler fire area and de-ashing area. (1) |  |  |
|  | Service and loosen both Mowbray’s manual drain valves in position and clean pipes of Mowbray’s (without removing the Mowbray’s). (2) |  |  |
|  | Replace stoker side sealants (seals) against the boiler body shell. (2 sides) |  |  |
|  | Warm the recast cement in the combustion chamber to operational temperature. (1) |  |  |
|  | Ensure the guillotine door is aligned in position accordingly. (1) |  |  |
|  | Test guillotine door for level and correct heights. (1) |  |  |
|  | Reset main safety valve to correct set operating pressures (800 KPA to 900 KPA). (1) |  |  |
|  | Complete all service documentation certificates and reports and hand over to ARC representative. (all) |  |  |
|  | Boiler service total |  |  |
|  | Boiler House Essential Additional Repairs Scope |  |  |
| 1. | Guillotine door recast. (1) |  |  |
| 2. | Main pressure gauge recalibrate and provide certificate. (1) |  |  |
| 3. | Soot blower valves service with repairs (X2) and provide certification. (2) |  |  |
| 4. | Blow down valve service with repairs (1) |  |  |
|  | Totals |  |  |
|  | Boiler Water Hotwel Tank |  |  |
|  | Replace inlet ball (float) valve. (1) |  |  |
|  | Service and repair water level indicator. (1) |  |  |
|  | Drain and clean the tank. (1) |  |  |
|  | Paint the tank with anti-corrosion coating (1) |  |  |
|  | Totals |  |  |
|  | Main Water Reservoir Tank |  |  |
|  | Replace inlet ball (float) valve. (1) |  |  |
|  | Service and repair water level indicator. (1) |  |  |
|  | Repaint the water level indicator wall (1) |  |  |
|  | Totals |  |  |
|  | Water Treatment Plant Repairs |  |  |
| 1. | Water Treatment Plant Service and Repairs. (1) |  |  |
| 2. | Supply boiler wood (200 packs) :Sample to be shown on site (as stated) |  |  |
|  | Totals |  |  |
|  | # Main 6 inch steam line test and certification |  |  |
| # | Description | Comply Yes or No | Amount |
| 1. | Blank off main steam pipeline at appropriate areas. (1) |  |  |
| 2. | Isolate steam traps and plug in pressure pump. (2) |  |  |
| 3. | Flood the line with water for hydraulic test/operating pressure testing (supplied by the appointed contractor). (1) |  |  |
| 4. | Pressure test main steam line with AIA in attendance as specified in OHS act. (1) |  |  |
| 5. | Carry out thickness test on main steam line and compile a report. (randomly, anywhere likely to wear out) |  |  |
| 6. | Remove all blanks and plugs. (3) |  |  |
| 7. | Replace gaskets and reconnect the main steam line to the boiler. (3) |  |  |
| 8. | Complete all documentation and submit to ARC representative. (all) |  |  |
| 9. | Ignore the fact that the steam line is old type and not schedule 40. (for info) |  |  |
|  | Steam line totals |  |  |

N.B.: The numbering does not constitute sequence except to guide the process and essential work inputs & outputs by the appointed contractor.

Amount to be inserted at the last row per section

Only minimum of level 2 ME grading or above CIDB registered suppliers qualify to submit a quote.

GRAND TOTAL = _________________________________

Bidder Name:_______________________________________________________

Bidder Representative sign:_______________________________________________