Addendum on the Fire Protection System Spares tender
Date – 10 July 2025
1.
Supplier question
We kindly requesting extension of the closing date for the above tender.
Eskom answer
The second closing date extension request has been granted and the new closing date is now 21 July 2025 at 14h00.
2.
Supplier question
We are requesting for additional info regarding specifications for accurate Quote. 
Eskom answer
The requested additional information has been uploaded to the Eskom Tender Bulletin and National Treasury portal or website.
3.
Supplier question
	CMG cage induction, motor
	MOTOR, CAGE INDUCTION
	CMG, 6.6 kV, cage induction, 355 kW, HTE 400-4 induction motor
	CMG
	 
	EA
	1
	 


Kindly advise if the motor below is a 4 pole or foot mounted? 

[bookmark: _Hlk203037493]Eskom Answer
Kindly note that the motor is foot mounted.
4.
Supplier question
Please note that the OEM for the below has requested the following:

“In order for us to make you an offer, please kindly provide a photo of the nameplate of the product or more information.
They, unfortunately, cannot prepare an offer without the above-mentioned information”
 
Please can you assist?
 
	114
	COUPLING
	COUPLING
	SGA20/21 AP001/SGA23/24 AP001
	TYRE COUPING FOR PUMP SHAFT
	FENNER
	
	618646



Eskom Answer
Kindly see the description below, the coupling does not have serial no however the information below will assist

COUPLING, SHAFT FLEXIBLE: TYPE: FENAFLEX TYRE; BORE DIAMETER: 140 X 75 MM; TORQUE: 9.339 KNM; MATERIAL: CHLOROPRENE COMPOUND; SPEED: 1600 RPM; SUPPL P/N: 033L0068; REFERENCE NO: F160; APPLICATION: CLOSED LOOP CW 1-6 PUMP 1-3 COUPLING; TYRE COUPLING MATERIAL TO BE FIRE RESISTANT AND ANTI-STATIC; GAP BETWEEN ENDS; 5 MM; MAXIMUM ANGULAR MISALIGNMENT CAPACITY: 4 DEGREE; MAXIMUM PARALLEL MISALIGNMENT: 4.2 MM; OD 402 MM; DISTANCE FLANGES: 30 MM; WEIGHT: 3.4 KG

5.
Supplier question
In our efforts to prepare and submit a comprehensive and value-adding tender for Eskom’s Medupi Power Station, we kindly request that you furnish us with the equipment serial numbers for the items listed in the Bill of Quantities, specifically those relating to pumps and electronic equipment.
We are currently engaging with the respective OEM suppliers, and the consistent feedback received is that the equipment in question is manufactured to order. As such, the provision of accurate serial numbers is essential for us to ensure technical alignment and supplier lead-time commitments.
The affected brand names as per the BoQ include the following:
1. Endress & Hauser – Pressure transmitters
1. Sulzer – Pumps, pump sets, and service kits
1. Bermad – Valves
1. Grundfos – Pump repair kits
1. Whale Gusher Urchin – Pump repair kits
1. Fenner – Pumps
We would appreciate your assistance in providing the requested information at your earliest convenience.

Eskom Answer
Kindly receive attached feedback as below

1. Endress & Hauser – Pressure transmitters : Material No 609484 :Serial No F40B020109C
1. Endress & Hauser – Pressure transmitters Material No  609483: Serial No F40AED019C
1. Endress & Hauser – Pressure transmitters Material No  609482: Serial No F40AEF0109C
1. Endress & Hauser – Pressure transmitters Material No  609432:  Description (TRANSMITTER, LEVEL: RANGE: 0-40 M; OUTPUT: 4-20 MA; SUPPLY: 16-36 VDC 0.8 W; CONNECTION: FLANGE; WORKING PRESSURE: 16 BAR; TYPE: NON CONTACT RADAR; BODY MATERIAL: ALUMINIUM; APPLICATION: MAIN FIRE WATER TANKS; MOUNT: HEAD; SUPPL P/N: FMR245-ACCQKAA2A1; COUNTER FLANGE DETAILS: N/B SANS 1123 1600/3; CERTIFIED: EN1092-1/05 DN100; MEASURED LEVEL: 1750M3 CAPACITY)
1. 
1. Sulzer pump APP 32- 80 – Pumps, pump sets, and service kits:(Pump Serial no:100286797)
1. Sulzer pump APP 31-125- Pumps, pump sets, and service kits(Pump Serial no:100090922)
1. Bermad – Valves(Material no 665863)serial no :(22822180016)
1. Grundfos – pump serial no:402 597548
1. Whale Gusher Urchin – Pump repair kits, description: KIT, PUMP REPAIR: TYPE: DIAPHRAGM PUMP; APPLICATION: WHALE GUSHER URCHIN BILGE DIAPHRAGM PUMP; COMPRISING: ONE DIAPHRAGM; ONE INLET VALVE; ONE OUTLET VALVE; TWO CIRCLIP SMALL; TWO CIRCLIP LARGE; ON DECK WITH FIXED HANDLE, DUAL SIZE NOZZLES FOR 25MM (1 INCH) MOUNTING MODEL THRUC DECK MODELS; MATERIAL NITRILE; MANUF P/N: AK9011

1. Fenner – Pumps tyre coupling ( COUPLING, SHAFT FLEXIBLE: TYPE: FENAFLEX TYRE; BORE DIAMETER: 140 X 75 MM; TORQUE: 9.339 KNM; MATERIAL: CHLOROPRENE COMPOUND; SPEED: 1600 RPM; SUPPL P/N: 033L0068; REFERENCE NO: F160; APPLICATION: CLOSED LOOP CW 1-6 PUMP 1-3 COUPLING; TYRE COUPLING MATERIAL TO BE FIRE RESISTANT AND ANTI-STATIC; GAP BETWEEN ENDS; 5 MM; MAXIMUM ANGULAR MISALIGNMENT CAPACITY: 4 DEGREE; MAXIMUM PARALLEL MISALIGNMENT: 4.2 MM; OD 402 MM; DISTANCE FLANGES: 30 MM; WEIGHT: 3.4 KG)

6.
Supplier question
We are currently quoting items that are in the pricing schedule attached to the NEC of the fire system spares Tender. 
 
Can you please assist us by providing more information of the following items so we may be able to price them:
1. Motors: We need information about the mounting of the motors
Material numbers for these motors are: 665861, 663348, 665863. 
Kindly send us information for the mounting of these motors so we can proceed with quoting them.
 
1. Coupling: Please give us a more detailed description of tyre coupling for the pump shaft. 
Material number: 618646
 
1. Paste: More detailed description of the paste
Material number: 728862
 
1. Pressure gauge; More information needed
Material number: 671904
 
1. Flow meter: More information is needed for the FSD

Eskom response
Kindly see information below: 
1. Motors – Mounting of all motors, Hold Down Bolts are utilized.

1. Coupling -COUPLING, SHAFT FLEXIBLE: TYPE: FENAFLEX TYRE; BORE DIAMETER: 140 X 75 MM; TORQUE: 9.339 KNM; MATERIAL: CHLOROPRENE COMPOUND; SPEED: 1600 RPM; SUPPL P/N: 033L0068; REFERENCE NO: F160; ; TYRE COUPLING MATERIAL TO BE FIRE RESISTANT AND ANTI-STATIC; GAP BETWEEN ENDS; 5 MM; MAXIMUM ANGULAR MISALIGNMENT CAPACITY: 4 DEGREE; MAXIMUM PARALLEL MISALIGNMENT: 4.2 MM; OD 402 MM; DISTANCE FLANGES: 30 MM; WEIGHT: 3.4 KG

1. PASTE: TYPE: DENSO SUPERLIGHT PROFILING MASTIC; CONTAINER: BOX; PACKAGE WEIGHT: 20 KG; APPLICATION TEMPERATURE 0 DEGREE CELSIUS TO +45 DEGREE CELSIUS. COLOUR DULL CREAM WITH WHITE SPHERES


1. GAUGE- PRESSURE: RANGE: 0-1600 KPA; DIAL SIZE: 100 MM; CONNECTION TYPE: THD; CONNECTION SIZE: 15NB; CASE MATERIAL: STAINLESS STEEL; TUBE MATERIAL: STAINLESS STEEL; CONNECTION MATERIAL: COPPER ALLOY; CONNECTION LOCATION: BOTTOM; MOUNT: SCREW; FILLED: GLYCERINE 99.7PCT; SPECIFICATION: EN 837-1; TYPE: BOURDON TUBE; MODEL NO: 213.53; PROTECTION CLASS: IP65 AS PER EN 60-529 / IEC 529; POINTER COLOUR AND MATERIAL: BLACK ALUMINUM

1. Flow Meter – Information provided in the NEC( that is the information available)

Date – 26 June 2025
1.
Supplier question
We kindly requesting extension of the closing date for the above tender, we are still waiting for prices from the suppliers.
Eskom answer
The closing date extension request has been granted until 10 July 2025 at 14h00.
