{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["OHTE Condutcors Scope"],"read":"whole","date_system":"1900"}

{"sheet":"OHTE Condutcors Scope","index":0,"n_rows":51,"n_cols":10,"rows_kept":51,"merged":[[1,0,1,9],[6,0,6,9],[14,0,14,9],[19,0,19,9],[27,0,27,9],[32,0,32,9],[44,0,44,9]]}
["#","Item Number","SAP Description","Long description","Standard/Specification","Unit of measure","Bidder/OEM Drawing/Spec/technical datasheet Returned?\nYES/NO","Tests to be conducted on the conductor","Qauntity ","Unit Price"]
["Category A (Phase and earth wires)"]
[1,54032718,"WIRE ELECTRICAL;PHASE WIRE,DIA 50 MM2,\nLENGTH 1KM, ALUMINIUM, RABBIT","WIRE, ELECTRICAL; TYPE: PHASE, CONDUCTOR DIAMETER: 50 MM2, INSULATION COLOR: NONE, DIMENSIONS: 1 KM, CONDUCTOR MATERIAL: ALUMINIUM, INSULATION MATERIAL: NONE, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS 182 PART 3, LA; USED ON OHTE; STEEL REINFORCED; CODE NAME: RABBIT; STRAND 6/1/3.35 MM"," SANS182 PART3","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[2,54039916,"WIRE ELECTRICAL;EARTH,DIA 160 MM2,\nLENGTH 2KM, ALUMINIUM, CODE HORNET","WIRE, ELECTRICAL; TYPE: EARTH, CONDUCTOR DIAMETER: 160 MM2, INSULATION COLOR: NONE, CONDUCTOR MATERIAL: ALUMINIUM HARD DRAWN, PACKAGE TYPE: WOOD DRUM 2 KM; SPECIFICATION: SANS182 PART2, 0; SABS182 PART2; USED ON OHTE; CODE NAME: HORNET; STRAND 19/3.25 MM","SANS 182-2","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length",1]
[3,54032706,"WIRE ELECTRICAL;EARTH,DIA 160 MM2,\nLENGTH 1KM, ALUMINIUM, CODE HORNET","WIRE, ELECTRICAL; TYPE: EARTH, CONDUCTOR DIAMETER: 160 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 1000 MM, CONDUCTOR MATERIAL: ALUMINIUM HARD DRAWN, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART2, LA; CODE NAME: HORNET; STRAND 19/3.25 MM","SANS182 PART2","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length",1]
[4,54012945,"WIRE ELECTRICAL;PHASE,DIA 50 MM2,\nLENGTH 2KM,ALUMINIUM,CODE RABBIT","WIRE, ELECTRICAL; TYPE: PHASE, CONDUCTOR DIAMETER: 50 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 2 KM, CONDUCTOR MATERIAL: ALUMINIUM, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART3, LA; MATERIAL NUMBER 054012945; USED ON OHTE; STEEL REINFORCED; CODE NAME: RABBIT"," SANS182 PART3","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
["Category B (Bonding and XPLE wires)"]
[1,54019365,"WIRE ELECTRICAL;BONDING,DIA 97 MM2,\nINSULATION BLACK,LENGTH 500M, STEEL","WIRE, ELECTRICAL; TYPE: BONDING, CONDUCTOR DIAMETER: 97 MM2, INSULATION COLOR: BLACK, POTENTIAL RATING: 25 KV, OVERALL DIAMETER: 13 MM, CONDUCTOR MATERIAL: STEEL, CONDUCTOR FINISH: GALVANIZED, SPECIAL FEATURES: INSULATION POLYVINYL CHLORIDE/SHEATHED, PACKAGE TYPE: REEL; SPECIFICATION: SANS182 PART 5, LASANS1507 PART 3, LA; MATERIAL NUMBER 54019365, STRANDED GALVANIZED STEEL WIRE STRANDING 49/1.6MM","SANS 182-5/SANS 1507-3","M",null,"1) Resistance per km test\n 2) Insulation to be tested according to the mentioned specification\n3) Physical size\n4) Galvanized according to specification (Test certificate required)\n",1]
[2,54033089,"CABLE ELECTRICAL;CNDTR QTY 3,ALUMINIUM\nDIA 50MM2,LENGTH 500M,ABC,11KV ","CABLE, ELECTRICAL; CONDUCTOR QUANTITY: 3, CONDUCTOR DIAMETER: 50 MM2, POTENTIAL: 11 KV, CONDUCTOR MATERIAL: ALUMINIUM, CONDUCTOR ARRANGEMENT: BUNDLE, PACKAGE TYPE: WOOD DRUM 500; SPECIFICATION: BBC 7613, LASANS1339(ADAPTED), 0SANS1713, 0; USED ON OHTE;; 50MM2 G.S.W CATENARY XLPE INSULATED ; USERS INTEREST:RETICULATION UNDER BRIDGES ETC","BBC7613 Version 2\nSANS1339(ADAPTED), SANS1713","M",null,"1) Resistance per km test\n 2) Insulation to be tested according to the mentioned specification\n3) Physical size\n4) Partial discharge test if required in specification\n5) Catenary wire tested to specification\n",1]
[3,54033117,"CABLE ELECTRICAL;CNDTR QTY 3,DIA 70 MM2\nLENGTH 500M,ALUMINIUM","CABLE, ELECTRICAL; TYPE: CANTENARY, CONDUCTOR QUANTITY: 3, CONDUCTOR DIAMETER: 50 MM2, POTENTIAL: 11 KV, CURRENT: 30 A, CONDUCTOR MATERIAL: ALUMINIUM, CONDUCTOR INSULATION: CROSS LINKED POLYETHYLENE, CONDUCTOR ARRANGEMENT: BUNDLE, LENGTH: 500 M, COVERING: NONE, PACKAGE TYPE: WOODEN DRUM; SPECIFICATION: SANS1713, 0SANS1339(ADAPTED), 0; TYPE A BBC7613 VERSION 1; USED ON OHTE; USERS INTEREST:RETICULATION UNDER BRIDGES ETC","BBC7613 Version 2\nSANS1339(ADAPTED), SANS1713","M",null,"1) Resistance per km test\n 2) Insulation to be tested according to the mentioned specification\n3) Physical size\n4) Partial discharge test if required in specification\n5) Catenary wire tested to specification\n",1]
[4,54033053,"CABLE ELECTRICAL,CNDTR QTY 3,ALUMINIUM\nLENGTH 500M,35 MM2, ABC, 11KV","CABLE, ELECTRICAL; TYPE: MEDIUM VOLTAGE, CONDUCTOR QUANTITY: 3, CONDUCTOR DIAMETER: 35 MM2, POTENTIAL: 11 KV, CURRENT: 210 A, CONDUCTOR MATERIAL: ALUMINIUM, CONDUCTOR ARRANGEMENT: BUNDLE, LENGTH: 500 M, COVERING: POLYVINYL CHLORIDE, APPLICATION: CANTENARY, PACKAGE TYPE: DRUM; SPECIFICATION: SANS1339(ADAPTED), 0BBC 7613, LA; USED ON OHTE; 50MM2 G.S.W., CANTENARY INSULATION: XLPE; USERS INTEREST: RETICULATION UNDER BRIDGES ETC","BBC7613 Version 2\nSANS1339(ADAPTED), SANS1713","M",null,"1) Resistance per km test\n 2) Insulation to be tested according to the mentioned specification\n3) Physical size\n4) Partial discharge test if required in specification\n5) Catenary wire tested to specification\n",1]
[5,54040342,"WIRE ELECTRICAL;BONDING,DIA 160 MM2\nLENGTH 300M, COPPER","WIRE, ELECTRICAL; TYPE: BONDING, CONDUCTOR DIAMETER: 160 MM2, INSULATION COLOR: BLACK, CONDUCTOR MATERIAL: COPPER ANNEALED, INSULATION MATERIAL: POLYVINYL CHLORIDE, PACKAGE TYPE: REEL; SPECIFICATION: SANS 1507-PART 3, LA; SANS 1411-PART 2, LA; EQUIPMENT USED ON OHTE","SANS1411/ SANS 1507-3","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Insulation to be tested according to the mentioned specification\n",1]
[6,54033191,"WIRE ELECTRICAL;BONDING,DIA 150 MM2\nLENGTH 300M,TINNED COPPER/GALVANIZED STEEL,","WIRE, ELECTRICAL; TYPE: BONDING, CONDUCTOR DIAMETER: 150 MM2, INSULATION COLOR: BLACK, DIMENSIONS: LG 300 M, CONDUCTOR MATERIAL: TINNED COPPER/GALVANIZED STEEL, INSULATION MATERIAL: POLYVINYL CHLORIDE, CONDUCTOR FINISH: POLYVINAL CHLORIDE, PACKAGE TYPE: DRUM; RESISTANCE; TO BE EQUAL TO 50 MM2 TINNED COPPER WIRE; STRANDING 6 BUNCHES 7/1 MM COPPER AROUND 19/1 MM COPPER CENTRE; EACH OF THE 6 BUNCHES IS COVERED BY 12 STRANDS OF 1 MM STEEL WIRE; SPECIFICATION: SANS 1507-PART 3","SANS 1507-3","M",null,"1)Resistance/km test\n2) Physical size\n3) Insulation to be tested according to the mentioned specification\n4) Make up of cable\n5) Galvanized according to specification (Test certificate required)\n",1]
[7,54001596,"WIRE,ELECTRICAL; TYPE BONDING, DIA 160MM2 ALL ALUMINIUM","WIRE, ELECTRICAL; TYPE: BONDING, CONDUCTOR DIAMETER: 160 MM2, INSULATION COLOR: BLACK, CONDUCTOR MATERIAL: ALL ALUMINIUM CONDUCTOR, INSULATION MATERIAL: POLYVINYL CHLORIDE, SPECIAL FEATURES: LG 500 M, PACKAGE TYPE: REEL; SPECIFICATION: SANS 182 PART 2, LASANS 1507 PART 3, LASANS 1411 PART 2, LA; EQUIPMENT USED ON OHTE","SANS 182 PART 2, SANS 1507 PART 3, SANS 1411 PART 2","M",null,"1) Resistance per km test\n 2) Insulation to be tested according to the mentioned specification\n3) Physical size\n4) Galvanized according to specification (Test certificate required)\n",1]
["CATEGORY C (DROPPERS WIRE & STAY WIRES)"]
[1,54039888,"WIRE ELECTRICAL;DROPPER,DIA 4 MM,\nSUPPLIED IN 50KG COIL","WIRE; TYPE: DROPPER, DIAMETER: 4 MM, MATERIAL: STAINLESS STEEL, STRUCTURE: SOLID; SPECIFICATION: AISI GRADE 304 SOFT, LA; PACKAGE TYPE:COIL 50 KG, THE WIRE COIL MUST HAVE A DIAMETER OF 500 MM\nUSED ON OHTE","AISI GRADE 304","KG",null,"1) Physical size\n2) Elongation test\n3) Tensile strength\n\n",1]
[2,54011357,"WIRE ELECTRICAL;DROPPER,DIA 4 MM2,\nSUPPLIED IN SIZE OF 50KG COIL","WIRE; TYPE: DROPPER, DIAMETER: 4 MM, MATERIAL: COPPER; SPECIFICATION: SANS 182 PART 1, LA; INSULATION MATERIAL, NONE, SPECIAL FEATURES, PACKAGE TYPE: COIL 50 KG THE WIRE COIL MUST HAVE A DIAMETER OF 500 MM; SPECIFICATION: SANS 182 PART 1","SANS 182 PART 1","KG",null,"1) Physical size\n2) Elongation test\n3) Tensile strength\n4) Resistance test\n",1]
[3,54012868,"WIRE ELECTRICAL;STAY,DIA 12.2 MM2,\nLENGTH OF 300M, MATERIAL STEEL.","WIRE, ELECTRICAL; TYPE: STAY, CONDUCTOR DIAMETER: 12.2 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 300 M, CONDUCTOR MATERIAL: STEEL, CONDUCTOR FINISH: GALVANIZED, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART5, 0; USED ON OHTE; QUALITY: 700MPA; TENSILE STRENGTH: 61.57KN ,CONDUCTOR SIZE 12-12.2 MM2","SANS182 PART5","M",null,"1) Tensile test\n2) Elongation test\n3) Physical size\n4) Galvanized according to specification (Test certificate required)\n",1]
[4,54012881,"WIRE ELECTRICAL;STAY,DIA 20.4 MM2,\nLENGTH OF 500M, STEEL.","WIRE, ELECTRICAL; TYPE: STAY, CONDUCTOR DIAMETER: 20.4 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 500 M, CONDUCTOR MATERIAL: STEEL, INSULATION MATERIAL: NON INSULATED, CONDUCTOR FINISH: GALVANIZED, PACKAGE TYPE: REEL, WOOD; USED ON OHTE; SPECIFICATION: SANS182 PART5",{"$f":"E18","v":"SANS182 PART5"},"M",null,"1) Tensile test\n2) Elongation test\n3) Physical size\n4) Galvanized according to specification (Test certificate required)\n",1]
["Category D (Jumper and return wires)"]
[1,54010894,"WIRE ELECTRICAL;JUMPER,DIAMETER 96 MM2,\nLENGTH 500M,COPPER ANNEALED","WIRE, ELECTRICAL; TYPE: JUMPER, CONDUCTOR DIAMETER: 96 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 500 M, CONDUCTOR MATERIAL: COPPER ANNEALED, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART1, STRAND 37/7/0.686 MM","SANS 182 Part 1","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[2,54011458,"WIRE ELECTRICAL;JUMPER,DIAMETER 160 MM2,\nLENGTH 500M,COPPER ANNEALED","WIRE, ELECTRICAL; TYPE: JUMPER, CONDUCTOR DIAMETER: 160 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 500 M, CONDUCTOR MATERIAL: COPPER ANNEALED, INSULATION MATERIAL: NON INSULATED, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182-PART 1, LA, SANS1411 PART1, LA; USED ON OHTE , STRAND 61/1.8 MM","SANS 1411-1/SANS182-2","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[3,54032731,"WIRE ELECTRICAL;FEEDER,DIA 500 MM2,\nLENGTH 500M,ALUMINIUM,SCORPION","WIRE, ELECTRICAL; TYPE: FEEDER, CONDUCTOR DIAMETER: 500 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 500 M, CONDUCTOR MATERIAL: ALUMINIUM, INSULATION MATERIAL: NONE, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS 182 PART 2, LA; ITEM CODE NAME SCORPION.","SANS 182-2","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[4,54013016,"WIRE ELECTRICAL;FEEDER,DIA 800 MM2,\nLENGTH 1KM, CODE NAME BULL,ALUMINIUM","WIRE, ELECTRICAL; TYPE: FEEDER, CONDUCTOR DIAMETER: 800 MM2, INSULATION COLOR: NONE, DIMENSIONS: 1 KM, CONDUCTOR MATERIAL: ALUMINIUM HARD DRAWN, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART2, 0; USED ON OHTE; CODE NAME:  BULL; STRAND 61/4.25 MM","SANS 182-2","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[5,54032630,"WIRE ELECTRICAL;JUMPER,DIA 160 MM2,\nLENGTH 300M, COPPER ANNEALED","WIRE, ELECTRICAL; TYPE: JUMPER, CONDUCTOR DIAMETER: 160 MM2, INSULATION COLOR: NONE, POTENTIAL RATING: 25 KV, DIMENSIONS: LG 300 M, CONDUCTOR MATERIAL: COPPER ANNEALED, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS1411 PART1, 1; ITEM USED ON OHTE; STRAND 61/1.8MM","SANS1411 PART1","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[6,54011434,"WIRE ELECTRICAL;JUMPER,DIA 50 MM2,\nLENGTH 300M, COPPER ANNEALED","WIRE, ELECTRICAL; TYPE: JUMPER, CONDUCTOR DIAMETER: 50 MM2, INSULATION COLOR: NONE, CONDUCTOR MATERIAL: COPPER ANNEALED, PACKAGE TYPE: WOOD DRUM 300 M; SPECIFICATION: SANS182 PART1, 0; USED ON OHTE; PIGTAIL; STRAND 19/1.8 MM"," SANS182 PART1","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[7,54039459,"WIRE ELECTRICAL;RETURN CONDUCTOR,DIA 250MM\nLENGTH 2KM,ALUMINIUM, CODE NAME: COCKROACH","WIRE, ELECTRICAL; TYPE: RETURN CONDUCTOR, CONDUCTOR DIAMETER: 250 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 2 KM, CONDUCTOR MATERIAL: ALUMINIUM HARD DRAWN, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART2, 0; ITEM USED ON OHTE; CODE NAME: COCKROACH; STRAND 19/4.22 MM","SANS182 PART2","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
["Category E (Feeder wires)"]
[1,54033307,"WIRE ELECTRICAL;FEEDER,DIA 800 MM2,\nLENGTH 1KM, CODE LAPWING,ALUMINIUM","WIRE, ELECTRICAL; TYPE: FEEDER, CONDUCTOR DIAMETER: 800 MM2, INSULATION COLOR: NONE, POTENTIAL RATING: 25 KV, DIMENSIONS: LG 1 KM, CONDUCTOR MATERIAL: ALUMINIUM HARD DRAWN, INSULATION MATERIAL: NONE, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART 3, LA; ACSR; USED ON OHTE; STEELREINFORCED; CODE NAME; LAPWING; STRAND 45/4.77 MM ALUMINIUM + 7/3.18 MM STEEL","SANS 182-3","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[2,54013004,"WIRE ELECTRICAL;FEEDER,DIA 500 MM2,\nLENGTH 1KM, ALUMINIUM, COPE SCORPION","WIRE, ELECTRICAL; TYPE: FEEDER, CONDUCTOR DIAMETER: 500 MM2, INSULATION COLOR: NONE, DIMENSIONS: 1 KM, CONDUCTOR MATERIAL: ALUMINIUM, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS 182 PART2, LA; ITEM NAME CODE NAME: SCORPION; STRANDS OF 37 X 4.27MM","SABS182 PART2","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length",1]
[3,54032743,"WIRE ELECTRICAL;FEEDER,DIA 800 MM2,\nLENGTH 500M, ALUMINIUM,CODE BULL","WIRE, ELECTRICAL; TYPE: FEEDER, CONDUCTOR DIAMETER: 800 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 500 M, CONDUCTOR MATERIAL: ALUMINIUM HARD DRAWN, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART2, 0; USED ON OHTE; CODE NAME: BULL; STRAND 61/4.25 MM","SANS182 PART2","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length",1]
[4,54112442,"WIRE ELECTRICAL;JUMPER,AAC,DIA:160 MM2","WIRE, ELECTRICAL; TYPE: JUMPER, ALL ALUMINUM CONDUCTOR, CONDUCTOR DIAMETER: 160 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 500 M, CONDUCTOR MATERIAL: ALUMINIUM, INSULATION MATERIAL: NONE, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: BBH 2161, LA","BBH 2161","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
["Category F (Catenary wires)"]
[1,54011471,"WIRE ELECTRICAL;CATENARY,DIA 80 MM2,\nLENTGH 2KM,HARD DRAWN,25 KV","WIRE, ELECTRICAL; TYPE: CATENARY, CONDUCTOR DIAMETER: 80 MM2, INSULATION COLOR: NONE, POTENTIAL RATING: 25 KV, DIMENSIONS: LG 2 KM, CONDUCTOR MATERIAL: COPPER HARD DRAWN, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART1, 1; USED ON OHTE; STRAND 7/3.75MM","SANS 182-1","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[2,54011483,"WIRE ELECTRICAL;CATENARY,DIA 100 MM2\nLENGTH 2KM, HARD DRAWN COPPER","WIRE, ELECTRICAL; TYPE: CATENARY, CONDUCTOR DIAMETER: 100 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 2 KM, CONDUCTOR MATERIAL: COPPER HARD DRAWN, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART1, 0; STRAND 19/2.65MM","SANS 182-1","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[3,54011511,"WIRE ELECTRICAL;CATENARY,DIA 250 MM2\nLENGTH 500M, HARD DRAWN COPPER","WIRE, ELECTRICAL; TYPE: CATENARY, CONDUCTOR DIAMETER: 250 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 500 M, CONDUCTOR MATERIAL: COPPER HARD DRAWN, INSULATION MATERIAL: NON INSULATED, PACKAGE TYPE: REEL, WOOD; EQUIPMENT USED ON OHTE; SPECIFICATION: SANS 182 PART 1","SANS 182-1","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[4,54019567,"WIRE ELECTRICAL;CATENARY,DIA 160 MM2\nLENGTH 2KM,ALUMINIUM, CODE NAME TIGER","WIRE, ELECTRICAL; TYPE: CATENARY, CONDUCTOR DIAMETER: 160 MM2, INSULATION COLOR: NONE, POTENTIAL RATING: 25 KV, DIMENSIONS: LG 2 KM, CONDUCTOR MATERIAL: ALUMINIUM HARD DRAWN, PACKAGE TYPE: REEL, WOOD; ACSR; USED ON OHTE; STEEL REINFORCED; CODE NAME: TIGER; STRAND 30/7/2.36MM","SANS 182-3","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length",1]
[5,54019580,"WIRE ELECTRICAL;CATENARY,DIA 530 MM2\nLENGTH 1KM,ALUMINIUM,CODE NAME DEER","WIRE, ELECTRICAL; TYPE: CATENARY, CONDUCTOR DIAMETER: 530 MM2, INSULATION COLOR: NONE, DIMENSIONS: 1 KM, CONDUCTOR MATERIAL: ALUMINIUM HARD DRAWN, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART3 2003, 0; ACSR; USED ON: OHTE, STEEL REINFORCED; CODE NAME: DEER ; STRAND 30/7/4.27","SANS 182-3","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length",1]
[6,54032642,"WIRE ELECTRICAL;CATENARY,DIA 80 MM2,\nLENGTH 1KM,COPPER,","WIRE, ELECTRICAL; TYPE: CATENARY, CONDUCTOR DIAMETER: 80 MM2, INSULATION COLOR: NONE, POTENTIAL RATING: 25 KV, DIMENSIONS: 1 KM, CONDUCTOR MATERIAL: COPPER HARD DRAWN, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART1, 1; ITEM USED ON OHTE; STRAND 7/3.75MM","SANS 182-1","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length",1]
[7,54032654,"WIRE ELECTRICAL;CATENARY,DIA 160 MM2\nLENGTH 500M, COPPER","WIRE, ELECTRICAL; TYPE: CATENARY, CONDUCTOR DIAMETER: 160 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 500 M, CONDUCTOR MATERIAL: COPPER HARD DRAWN, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART1, 0; USED ON OHTE; STRAND 37/2.36 MM","SANS 182-1","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[8,54032767,"WIRE ELECTRICAL;CATENARY,DIA 160 MM2\nLENGTH 1KM,ALUMINIUM, CODE TIGER","WIRE, ELECTRICAL; TYPE: CATENARY, CONDUCTOR DIAMETER: 160 MM2, INSULATION COLOR: NONE, DIMENSIONS: 1 KM, CONDUCTOR MATERIAL: ALUMINIUM HARD DRAWN, PACKAGE TYPE: REEL, WOOD; USED ON OHTE; STEEL REINFORCED; CODE NAME: TIGER; STRAND 30/7/2.36 MM","SANS182 PART3 2003","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[9,54000040,"CABLE ELEC;CANTENARY,GREASED,DIA:160 MM2","CABLE, ELECTRICAL; TYPE: CATENARY, GREASED, CONDUCTOR QUANTITY: MULTI STRAND, CONDUCTOR DIAMETER: 160 MM2, POTENTIAL: 3 TO 50 KVAC, CURRENT: 1.004 KA, CONDUCTOR MATERIAL: ALUMINIUM, STEEL REINFORCED, LENGTH: 2 KM, COVERING: NOT INSULATED, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART3, LA; ALL THE CONDUCTORS MUST BE GREASED EXCEPT THE OUTER SURFACE OF THE OUTER LAYER ACCORDING TO SANS 61089 FIGURE C.5 AND TYPE 20A150 ACCORDING TO BS EN 61394","SANS182 PART3 2003,\nBS EN 61394\nSANS61089","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length",1]
[10,54032755,"WIRE ELECTRICAL;CATENARY,DIA 530 MM2\nLENGTH 500M,ALUMIMIUM,CODE DEER","WIRE, ELECTRICAL; TYPE: CATENARY, CONDUCTOR DIAMETER: 530 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 500 M, CONDUCTOR MATERIAL: ALUMINIUM HARD DRAWN, INSULATION MATERIAL: NON INSULATED, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART3 , LA; ITEM USED ON: OHTE; STEEL REINFORCED; CODE NAME: DEER; STRAND 30/7/4.27","SANS182 PART3","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
[11,54920900,"CABLE ELEC;CANTENARY,GREASED,DIA:160 MM2","CABLE, ELECTRICAL; TYPE: CATENARY, GREASED, CONDUCTOR QUANTITY: MULTI STRAND, CONDUCTOR DIAMETER: 160 MM2, POTENTIAL: 3 TO 50 KVAC, CURRENT: 1.004 KA, CONDUCTOR MATERIAL: ALUMINIUM, STEEL REINFORCED, LENGTH: 1 KM, COVERING: NOT INSULATED, PACKAGE TYPE: REEL, WOOD; SPECIFICATION: SANS182 PART3, LA; ALL THE CONDUCTORS MUST BE GREASED EXCEPT THE OUTER SURFACE OF THE OUTER LAYER ACCORDING TO SANS 61089 FIGURE C.5 AND TYPE 20A150 ACCORDING TO BS EN 61394","SANS182 PART3 2003,\nBS EN 61394\nSANS61089","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n",1]
["Category G (Contact wires)"]
[1,54013041,"WIRE ELECTRICAL;CONTACT WIRE,DIA 161 MM2\nLENGTH 1830M,COPPER,","WIRE, ELECTRICAL; TYPE: CONTACT, CONDUCTOR DIAMETER: 161 MM2, INSULATION COLOR: NONE, POTENTIAL RATING: 3 KV, DIMENSIONS: LG 1.83 KM, CONDUCTOR MATERIAL: COPPER, INSULATION MATERIAL: NON INSULATED, SPECIAL FEATURES: GROOVED, PACKAGE TYPE: DRUM WOOD; SPECIFICATION: CEE.0241.2009, LA; MATERIAL NUMBER; 54013041; FOR SPOORNET USE ONLY; USED ON OHTE","CEE 0241-2009","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Twist test\n6) Bend test\n7) Hardness test\n",1]
[2,54039839,"WIRE ELECTRICAL;CONTACT WIRE,DIA 107 MM2\nLENGTH 1620M, COPPER","WIRE, ELECTRICAL; TYPE: CONTACT WIRE, CONDUCTOR DIAMETER: 107 MM2, INSULATION COLOR: NONE, POTENTIAL RATING: 25 KVAC, CONDUCTOR MATERIAL: COPPER, SPECIAL FEATURES: GROOVED, PACKAGE TYPE: WOODEN DRUM 1620 M; SPECIFICATION: CEE.0241.2009, LA; USED ON OHTE","CEE 0241-2009","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Lay length\n6) Twist test\n7) Bend test\n8) Hardness test",1]
[3,54032666,"WIRE ELECTRICAL;CONTACT WIRE,DIA 107 MM2\nLENGTH 810M, COPPER","WIRE, ELECTRICAL; TYPE: CONTACT WIRE, CONDUCTOR DIAMETER: 107 MM2, INSULATION COLOR: NONE, POTENTIAL RATING: 25 KV, DIMENSIONS: LG 810 M, CONDUCTOR MATERIAL: COPPER, SPECIAL FEATURES: GROOVED, PACKAGE TYPE: WOOD DRUM; SPECIFICATION: CEE-0241, LA; EQUIPMENT USED ON OHTE","CEE.0241","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Twist test\n6) Bend test\n7) Hardness test",1]
[4,54032678,"WIRE ELECTRICAL;CONTACT,DIA 161 MM2,\nLENGTH 915M, COPPER","WIRE, ELECTRICAL; TYPE: CONTACT, CONDUCTOR DIAMETER: 161 MM2, INSULATION COLOR: NONE, POTENTIAL RATING: 3 KV, DIMENSIONS: 915 M, CONDUCTOR MATERIAL: COPPER, SPECIAL FEATURES: GROOVED, PACKAGE TYPE: DRUM 915 M; SPECIFICATION: CEE.0241, LA","CEE.0241","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Twist test\n6) Bend test\n7) Hardness test",1]
[5,54034135,"WIRE ELECTRICAL;CONTACT,DIA:107 MM2,\nLENGTH 1620M,COPPER MAGNESIUM","WIRE, ELECTRICAL; TYPE: CONTACT, CONDUCTOR DIAMETER: 107 MM2, INSULATION COLOR: NONE, DIMENSIONS: LG 1620 M, CONDUCTOR MATERIAL: COPPER MAGNESIUM, CONDUCTOR FINISH: MARKING THREE IDENTIFICATION GROOVES ON UPPER LOBE, PACKAGE TYPE: DRUM WOOD; SPECIFICATION: BBD 7267, LA","BBD 7267","M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Twist test\n6) Bend test\n7) Hardness test",1]
[6,54034147,"WIRE ELECTRICAL;CONTACT,DIA:161 \nLENGTH 1830M, COPPER MAGANESIUM","WIRE, ELECTRICAL; TYPE: CONTACT, CONDUCTOR DIAMETER: 161 MM2, INSULATION COLOR: NONE,DIMENSIONS: LG 1830 M CONDUCTOR MATERIAL: COPPER MAGNESIUM, INSULATION MATERIAL: NON INSULATED, CONDUCTOR FINISH: MARKING THREE IDENTIFICATION GROOVES ON UPPER LOBE, PACKAGE TYPE: WOODEN DRUM; SPECIFICATION: BBD 7267, LA",{"$f":"E50","v":"BBD 7267"},"M",null,"1)Resistance/km test\n2) Physical size\n3) Profile\n4) Elongation test/Tensile strength\n5) Twist test\n6) Bend test\n7) Hardness test",1]