
SCOPE OF WORK / TERMS OF REFERENCE

1. [bookmark: _GoBack]Background

Description of scope: Removal, Supply, Installation and Commissioning of Dust Filtration Units at Midmar System.

2. Description of goods/ services required
Manufacturing specifications 

5 reverse pulse dust collector units manufactured from 304 stainless steel & electrostatically powder coated after manufacture for durability, the unit includes the fan capable of producing 3000 m3/h @ 300 pa through the washable cartridge type filters, the pulsing through the valves is controlled through a specially designed timer card that is easy to program to the customers’ requirements. 

Technical specifications 
Dimensions: 
500 x 500 x 1390 
Weight: 
105 kgs 

Construction: 
These units should be constructed from 304 stainless steel, then electrostatically powder coated, it should be manufactured with at least 1 inlet of 250/315 diameter. 

Cartridge type: 
Standard cartridges should be manufactured from a non-woven filter media rated at 99.8% efficiency for 0.5 micron size particulate. The filter should be designed to withstand temperatures up to 95°c. 

Controller: 
The solenoid valves utilized for reverse pulse cleaning and are operated by a 220 v pulse card controller by electronic adjustable presets, the reverse pulse cleaning is scheduled to clean at pre-desired time intervals. This solid state controller is pre-wired and housed within a waterproof enclosure, the reverse pulse controller offers the option of both on-line and off-line cleaning. 

Reverse pulse system: 
Cartridge cleaning is accomplished by the use of 1" x 220v asco valves and sonic nozzles positioned behind the cartridge filters, the specially designed sonic nozzles precision ally direct and increase the air velocity into the cartridge filter to reverse pulse the contaminants from the filters. 


3. Guarantee
a) 2 year from date of installation


4. Other information 
b) We estimate the quantity to be delivered is 5 bound copies of each business plan together with electronic copies in pdf and also in editable formats. 
c) We require the business plans to be delivered at uMngeni uThukela Water Mkondeni Regional Offices in Pietermaritzburg. 
d) Payment will be on successful delivery of milestones as detailed in section 3 / at the end of the Contract. 
e) New Intellectual Property arising as a result of the Contract will be the property of uMgeni uThukela Water.   

5. Other documents
In addition to this Bid document, the documents listed below form part of this Bid:
a) Nil
6. Special conditions
Nil

7. Pricing
a) The bidder shall provide the price proposal as detailed in SBD 3.1 
b) The bidders’s price must be fully inclusive, and each item must be clearly specified. 
c) All additional costs must be clearly specified and included in the total quotation price, (e.g. transport, labour, etc.). 
d) All prices must be VAT inclusive. 
e) The bidder is responsible for all the cost that they shall incur related to the preparation and submission of the quotation.

8. Evaluation Process
The RFQ will be evaluated using a two (02) stage evaluation approach:

8.1 First stage: 

	Mandatory
	SBD 4 – Bidders disclosure 

	Administrative Requirements
	 Bidder completed all RFQ Forms 
	 Bidder registered on National Treasury CSD/CIPC registration cert.
	 Bidder attended compulsory briefing session
                   BBBEE Certificate/ Sworn Affidavit  
	
8.2 [bookmark: Key_Personnel_Assigned_to_the_Work] Second Stage: Price and Preference goals
1. Subsequent to the evaluation of mandatory/ administrative requirements, the second stage of evaluation of the bids will be in respect of price and preferential procurement only.
2. Tenderer is tax complaint 
3. In compliance with the Preferential Procurement Regulations 2022, the 80/20 preference point system is applicable: points for this bid shall be awarded for: 
a) 	Price; and (80) and Preference as defined in SBD 6.1 (20)
4. 	The Preference Goals that have been identified for this bid is stipulated in SBD 6.1
5. Preferential goals and applicable points for this tender in terms of Preferential Procurement Regulations 2022, are indicated in the table below:







	6. 
	Description 
	80/20 
	Evidence to be provided

	RDP
	South African Owned Enterprise
	20
	CIPC  company registration/CSD 

	Total points for preferential goals
	20 
	



7. Failure on the part of a bidder to submit proof or documentation required in terms of this RFQ to claim points for specific goals, will be interpreted to mean that preference points for specific goals are not claimed by the bidder.

8. UUW reserves the right to require of a bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim in regard to preferences, in any manner required by UUW.

9. UUW reserves the right to conduct negotiations with the qualifying bidder/s regarding any terms and conditions, including price(s), of a proposed contract where applicable UUW reserves the right not to accept the lowest financial offer or any offer.


SBD 3.1 – PRICING SCHEDULE (BOQ) – FIRM PRICES 

NOTE:	

a) Only firm prices will be accepted. Non-Firm prices (including prices subject to rates of exchange variations) will not be considered

b) In cases where different delivery points influence the pricing, a separate pricing schedule must be submitted for each delivery point 

	
Name of bidder _______________________	        RFQ number_____Q25/268NM_______________

Closing Time  ________15H00_______________       Closing date______25/10/2024_____________




OFFER TO BE VALID FOR___________CALENDER DAYS FROM THE CLOSING DATE OF QUOTE.


	Item no. 
	QUANTIY
	DESCRIPTION
	UNIT PRICE
	TOTAL 

	1.
	5
	Custom Filtration unit 5 units 

	
	

	2.
	Sum
	Labour 

	
	

	3.
	1
	OHS 

	
	

	4.

	sum
	Travel
	
	

	
SUB TOTAL
		

	
VAT @ 15%
	

	GRAND TOTAL (price SA Rands with all applicable taxes included)
	

	
I (full name)__________________________________________, in my capacity as ___________________________, the duly authorized representative of ________________________________________________(business name) hereby declares that the offer is in accordance with the attached specification, notes to suppliers & accepts all conditions/clauses contained in the said documents.

	Signature of duly authorized representative
	
________________________
	DATE: 
__________________



